BPVIN-661498-2016 | BPV-436204-2016 | 9/8/2016 9:07:25 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | There is no records of when the safety valve was last replaced or serviced on a air receiver machine mount with a maximum working pressure of 200 psig. If left in this condition, the safety valve could malfunction resulting in a critical situation. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Support_arrangement.png | file://x:/photopub/docs/0000000485/62e68b53-919a-4035-96cd-daffe3f968a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6328355_28d6_467b_a8a7_7f4e4dcfd30b
BPVIN-661498-2016 | BPV-436204-2016 | 9/8/2016 9:07:25 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | There is no records of when the safety valve was last replaced or serviced on a air receiver machine mount with a maximum working pressure of 200 psig. If left in this condition, the safety valve could malfunction resulting in a critical situation. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve.png | file://x:/photopub/docs/0000000485/965dc76b-dd7c-4eb8-b4b8-2ac06d58c228.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6328355_28d6_467b_a8a7_7f4e4dcfd30b
GAIN-645902-2016 | GA-305238-2015 | 9/13/2016 9:41:24 AM | ASSESS: GA: Final | png | #asFound | GA039 | Painting of exterior piping | 1 | 1 | Corrugated strain less steel tubing not installed as per installation instructions. Where outer coating of tubing has been removed the stainless steel tubing must be wrapped in waterproof tape. | 1 | Painting of exterior piping | Exposed_corugated_stainless_steel_tubing_unprotected.png | file://x:/photopub/docs/0000000485/f0282a08-b5ac-42bb-993d-ee17d61c62e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f61f43d_3147_42a3_b02c_2def5dbf03dd
GAIN-661835-2016 | GA-053157-2013 | 9/14/2016 12:11:46 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Clearance to combustible material not met. Combustible material too close to a gas appliance could catch fire. | 3 | Clearance to combustible not met | Non_combustible_drywall_inside_clearance_to_combustible_area.png | file://x:/photopub/docs/0000000485/6a43308c-d662-48bc-b1fa-4bb4dba9bb64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0f00370_68a8_427e_b15e_522fd744a260
ELIN-612678-2016 | EL-391824-2016 | 7/15/2016 1:18:07 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Site left in hazardous condition, imminent and immediate shock hazards present throughout site. Energized conductors exposed to public and workers. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Main_red_tag.png | file://x:/photopub/docs/0000000456/86c7057e-5b68-4118-be14-d8b9268a2481.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc5c0295_ba03_4df1_90e1_ec93c9fdaee1
ELIN-612678-2016 | EL-391824-2016 | 7/15/2016 1:18:07 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Site left in hazardous condition, imminent and immediate shock hazards present throughout site. Energized conductors exposed to public and workers. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Heater_rec.png | file://x:/photopub/docs/0000000456/fa443af3-3109-4d91-9d5b-df969e1173fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc5c0295_ba03_4df1_90e1_ec93c9fdaee1
ELIN-612678-2016 | EL-391824-2016 | 7/15/2016 1:18:07 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Site left in hazardous condition, imminent and immediate shock hazards present throughout site. Energized conductors exposed to public and workers. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Altered_cord_end.png | file://x:/photopub/docs/0000000456/c66a3b21-85f3-4628-bbe4-1d8d79f18053.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc5c0295_ba03_4df1_90e1_ec93c9fdaee1
ELIN-612678-2016 | EL-391824-2016 | 7/15/2016 1:18:07 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Site left in hazardous condition, imminent and immediate shock hazards present throughout site. Energized conductors exposed to public and workers. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Energized_exposed.png | file://x:/photopub/docs/0000000456/3aa03341-ae46-4a99-85d6-567f31271316.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc5c0295_ba03_4df1_90e1_ec93c9fdaee1
ELIN-612678-2016 | EL-391824-2016 | 7/15/2016 1:18:07 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Site left in hazardous condition, imminent and immediate shock hazards present throughout site. Energized conductors exposed to public and workers. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Energized_subpanel2.png | file://x:/photopub/docs/0000000456/1697e4e5-01ac-42ed-9917-c83a4df44458.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc5c0295_ba03_4df1_90e1_ec93c9fdaee1
ELIN-612678-2016 | EL-391824-2016 | 7/15/2016 1:18:07 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Site left in hazardous condition, imminent and immediate shock hazards present throughout site. Energized conductors exposed to public and workers. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Energized_subpanel.png | file://x:/photopub/docs/0000000456/7173d8ec-ebd8-455c-8695-2fbbd1d5cacb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc5c0295_ba03_4df1_90e1_ec93c9fdaee1
ELIN-612678-2016 | EL-391824-2016 | 7/15/2016 1:18:07 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Site left in hazardous condition, imminent and immediate shock hazards present throughout site. Energized conductors exposed to public and workers. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Energized_conductors.png | file://x:/photopub/docs/0000000456/9be23874-41aa-4bd7-9951-d8b2f8022f48.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc5c0295_ba03_4df1_90e1_ec93c9fdaee1
ELIN-612678-2016 | EL-391824-2016 | 7/15/2016 1:18:07 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Site left in hazardous condition, imminent and immediate shock hazards present throughout site. Energized conductors exposed to public and workers. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Breakers_all_on_at_arrival.png | file://x:/photopub/docs/0000000456/d921e123-8515-445a-af25-2e249335beb6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc5c0295_ba03_4df1_90e1_ec93c9fdaee1
GAIN-599531-2016 | GA-401614-2016 | 6/29/2016 2:36:00 PM | ASSESS: GA: Rough-In | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Found Flexible gas piping in walls, installed too close to face of studs. This could easily allow screws/nails to penetrate gas line when drywall is installed resulting in a gas leak. | 2 | Physical protection of piping and tubing absent. | Gas_tite.png | file://x:/photopub/docs/0000000450/394bba95-3165-4fa7-ab19-69c78e5829af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__86fb8738_a783_4566_93a2_5aeea0cd340e
ELIN-620302-2016 | EL-416076-2016 | 8/2/2016 9:06:34 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 2 | In an existing commercial office space, numerous 15 & 20amp 120/208 branch circuit wires were found throughout the T-bar space bundled and strapped together. This can lead to a thermal effect. Pic attached. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Bundled_cabling_in_ceiling.png | file://x:/photopub/docs/0000000466/31dad027-956a-4d30-a5af-8d8cbcbd0ad7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cd8abe1_02ee_430c_b825_9b6071449e40
ELIN-659065-2016 | EL-433258-2016 | 9/13/2016 9:13:43 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 2 | NMD 90 not supported could be put in harms way by being pinched or pulled out of JB. This could cause a thermal effect an possible fire. | 3 | Conductors, No expansion joint or not installed correctly. | Non_supported_NMD.png | file://x:/photopub/docs/0000000484/984ea00a-6e5c-4223-841b-182534bb1585.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15d472ff_5b5b_49f9_aaf1_d399ca80a100
ELIN-659065-2016 | EL-433258-2016 | 9/13/2016 9:13:43 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 2 | NMD 90 not supported could be put in harms way by being pinched or pulled out of JB. This could cause a thermal effect an possible fire. | 3 | Conductors, No expansion joint or not installed correctly. | Box_not_supported_on_2_sides_.png | file://x:/photopub/docs/0000000484/c5bc808b-68f9-48f8-9918-5819fd1ccdd8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15d472ff_5b5b_49f9_aaf1_d399ca80a100
ELIN-659065-2016 | EL-433258-2016 | 9/13/2016 9:13:43 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 2 | NMD 90 not supported could be put in harms way by being pinched or pulled out of JB. This could cause a thermal effect an possible fire. | 3 | Conductors, No expansion joint or not installed correctly. | receptacle_exposed_to_weather_.png | file://x:/photopub/docs/0000000484/81284631-1f02-4f2e-9977-6f4d1708727b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15d472ff_5b5b_49f9_aaf1_d399ca80a100
ELHE-649527-2016 | HE-434931-2016 | 9/14/2016 11:02:07 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Circuits approved for dry location areas are installed in wet locations and exposed to weather. Potential for electric shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Lighting_circuit_on_a_tree.png | file://x:/photopub/docs/0000000485/c0e52846-aa00-4194-a6c6-8895f5e92faf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43ef65bd_a1d4_4bab_b856_bdd09e245781
ELHE-649527-2016 | HE-434931-2016 | 9/14/2016 11:02:07 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Circuits approved for dry location areas are installed in wet locations and exposed to weather. Potential for electric shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_cables_at_service_panel_accessible_to_public.png | file://x:/photopub/docs/0000000485/7e1f2958-e268-41c4-8690-bd4f2eddf335.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43ef65bd_a1d4_4bab_b856_bdd09e245781
EDRI-637706-2016 | ED-388215-2016 | 8/24/2016 1:20:11 PM | ASSESS: ED RI: Initial | png | #asFound | ED057 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 2 | 2 | No handrail on side of landing leaves a trip hazard. | 2 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | Landing_4.png | file://x:/photopub/docs/0000000475/c7ed0195-b316-49fb-bdb0-d35fd7f1778d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46c5e607_a221_450d_965e_d545153f8faf
BPVOP-604231-2016 | 2293290 | 8/24/2016 11:21:24 AM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | This high temperature glycol boiler safety relief valves are below the required relieving capacity as marked on the boiler nameplate which may lead to an incident in an overpressure situation. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | PRD_min_capacity.png | file://x:/photopub/docs/0000000476/1eae94fb-d21f-4de4-938c-4410dde76fe5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__F597FE25_5E74_4E79_BA53_3EA94FDB448F
GAUP-616207-2016 | UW-414745-2016 | 7/27/2016 11:30:03 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 5 | The furnace vent system was not secured or sealed to the furnace. When the furnace is in operation the vent will leak exhaust into the occupied area of the home. The products of combustion could contain carbon monoxide creating a high risk to the occupants. | 5 | Special venting system not glued or connected as per certified instructions | Furnace_vent_not_secured_or_sealed_.png | file://x:/photopub/docs/0000000462/bc448b5e-497e-489d-bbf4-ee4f67707caf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6968ecbf_bd9d_4bd0_a03d_9f7a0ee43b10
ELIN-659282-2016 | EL-435368-2016 | 9/12/2016 5:26:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL056 | Protection and control Overcurrent protection for transformer has not been provided, or is not properly rated | 3 | 3 | Arrangement of the 60A Main Breaker does not properly protected the Service Panel as the breaker does not properly disconnect the service feed. The rating of the feed from this service panel exceeds the rating of the Loadcenter fed from this Service panel. Both items pose a shock risk and potential damage to the panels. | 3 | Protection and control Overcurrent protection for transformer has not been provided, or is not properly rated | Panel_Rating.png | file://x:/photopub/docs/0000000484/74c6f7d6-58bb-475f-ba5b-418ffed91410.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f69f826_ace7_46d3_85c0_477f2f88faf2
ELIN-621865-2016 | EL-400220-2016 | 8/4/2016 2:08:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | The energized 15 amp 120 volt receptacles installed do not include cover plates or other means to protect energized terminals from coming into contact with public, this is a shock hazard | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_receptacle.png | file://x:/photopub/docs/0000000466/ba132594-d2bc-4796-b544-1195fc7dbe49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c49500a9_777c_47ac_b8cd_3ef4fc76dfd8
ELOP-637015-2016 | 1086 | 8/31/2016 2:32:55 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 | The bag house cyclone has filter bags inside a brick room right beside the cyclone motor and a light. With incorrect connectors the dust in the area will migrate into the equipment and could cause a fire. | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Baghouse.png | file://x:/photopub/docs/0000000479/a3b9fe6d-d7c0-469f-bd70-7fe35248df61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__954fb177_0110_4c68_aaef_8250db9a3fed
ELIN-639213-2016 | EL-415843-2016 | 8/30/2016 2:22:42 PM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Service equipment installed outdoors is not permitted to be installed using plywood mounted to service poles. This is because over time the wood will deteriorate and rot with exposure to weather. This installation has 30A 120V RV service equipment installed on plywood that is mounted to a service pole outdoors. Left uncorrected over time the wood will deteriorate and the service equipment will become disconnected from the wood and will no longer be mounted firmly in place. This may cause equipment damage and may allow water to enter cabinet mounting openings in the panel and meter base causing corrosion and rust to internal equipment and terminations. This is a potential fire hazard if equipment or terminations are damaged and fail. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Plywood_use_to_mount_service_equipment_to_a_service_pole_outdoors.png | file://x:/photopub/docs/0000000477/d480304c-6b4b-413c-ae68-0ac0cc0e2f8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0dea3f53_bbe6_492c_b98f_bbec05b7eed0
ELIN-639213-2016 | EL-415843-2016 | 8/30/2016 2:22:42 PM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Service equipment installed outdoors is not permitted to be installed using plywood mounted to service poles. This is because over time the wood will deteriorate and rot with exposure to weather. This installation has 30A 120V RV service equipment installed on plywood that is mounted to a service pole outdoors. Left uncorrected over time the wood will deteriorate and the service equipment will become disconnected from the wood and will no longer be mounted firmly in place. This may cause equipment damage and may allow water to enter cabinet mounting openings in the panel and meter base causing corrosion and rust to internal equipment and terminations. This is a potential fire hazard if equipment or terminations are damaged and fail. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | RV_service_pole_.png | file://x:/photopub/docs/0000000477/822482e1-67e6-4595-9fc2-5a1969a12ec6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0dea3f53_bbe6_492c_b98f_bbec05b7eed0
ELIN-663012-2016 | EL-436880-2016 | 9/14/2016 11:49:55 AM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | At an existing single family dwelling, a new 200amp 120/240volt service is installed with the main feeder not attached to panel, but laying open in the yard. This can lead to a shock hazard. Pic attached. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Main_feeder.png | file://x:/photopub/docs/0000000485/15c40c84-72aa-42ff-a5f7-c929d7ca900b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca243379_b08b_46d4_91b0_a1106bd1b9f6
ELIN-663012-2016 | EL-436880-2016 | 9/14/2016 11:49:55 AM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | At an existing single family dwelling, a new 200amp 120/240volt service is installed with the main feeder not attached to panel, but laying open in the yard. This can lead to a shock hazard. Pic attached. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | No_support_on_main_feeder.png | file://x:/photopub/docs/0000000485/5c908c31-49a5-45e0-80ef-5a609fed1862.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca243379_b08b_46d4_91b0_a1106bd1b9f6
BPVOP-603108-2016 | 2271384 | 6/29/2016 11:07:40 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP140 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | 1 | 1 |  | 1 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | Pressure_gauge_range_not_to_code.png | file://x:/photopub/docs/0000000450/55d788d8-9390-4d21-803a-9974c8c61b63.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0940ca29_442d_4a02_9fae_edcd7bffd89b
GAIN-632744-2016 | GA-388416-2016 | 8/22/2016 11:19:54 AM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Permanently installed heater was connected using type one holes, during the life of Installation hose will prematurely failed causing gas leak and possible fire | 3 | Non-compliant material/fittings installed | Typed_1_hose.png | file://x:/photopub/docs/0000000473/41a4bef7-fb05-47e3-a437-acd1afeeb964.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa6cb460_08fc_47fb_9e7f_dc729caf8e05
ELIN-664272-2016 | EL-428526-2016 | 9/16/2016 10:24:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | The system ground conductor is not terminated in the correct location of the service box | 4 | Installation Grounding; conductor is not continuous. | Grounding_cnductor_in_service_box.png | file://x:/photopub/docs/0000000486/95831c85-0149-45e5-9bd0-60cc90a9d554.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be6756b3_b4b2_4c6e_a5a8_e3a6e046664a
EDOP-661921-2016 | 2052575 | 8/30/2016 2:36:27 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 |  | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Missing_pick_up_roller.png | file://x:/photopub/docs/0000000484/34ecd2be-e7d1-4d78-9231-a493bea35c5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dab62aa3_71d8_4071_8d86_613156c66f36
BPVOP-612835-2016 | 2779314 | 7/15/2016 2:01:40 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | The person in charge of the plant must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that supervision was not provided at the time when the plant was in steaming operation on a 75m2 low pressure steam boiler/hot water boiler. Potential exists for an incident to occur due to lack qualified personnel. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Boiler_name_plate.png | file://x:/photopub/docs/0000000461/89eb930a-5b7b-4e72-a1df-113d5fd0c538.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ed5f2c0_9a30_4be2_bff3_f9e169d200bd
BPVOP-612835-2016 | 2779314 | 7/15/2016 2:01:40 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | The person in charge of the plant must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that supervision was not provided at the time when the plant was in steaming operation on a 75m2 low pressure steam boiler/hot water boiler. Potential exists for an incident to occur due to lack qualified personnel. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Low_press_steam_hw_boiler.png | file://x:/photopub/docs/0000000461/07269a01-bc76-494b-acfe-5fc0f517bf74.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ed5f2c0_9a30_4be2_bff3_f9e169d200bd
GAIN-603586-2016 | GA-404404-2016 | 7/6/2016 11:10:56 AM | ASSESS: GA: Final | png | #asFound | GA045 | Gas connector passes through wall, floor, ceiling, partition or into appliance | 2 | 2 | Gas hose passes through a partition wall. A gas hose may be damaged at the point in which it passes through a partition wall causing a gas leak. | 2 | Gas connector passes through wall, floor, ceiling, partition or into appliance | Gas_hose_passing_through_partition.png | file://x:/photopub/docs/0000000452/d4e8a97f-3280-45ec-aff4-369d066791f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b15857d5_9f42_4fcc_be29_a257e52a4b55
ELHE-629823-2016 | HE-423591-2016 | 8/15/2016 2:12:24 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | The flexible cord was used to feed a branch circuit in the basement that did not work. The conductors were too small for the breaker size and could overheat creating a fire hazard. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord.png | file://x:/photopub/docs/0000000470/c2794677-eba9-4ae3-853d-ee1067757013.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f20ac97_33e6_42d1_8c4b_59e27196c5d9
BPVOP-644813-2016 | 2277662 | 9/7/2016 8:23:56 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 | During the inspection of a HP Steam Boiler with MAWP of 150 psig was found on the waterside heavy soft scale. This insulates the tubes and can cause overheating of the tubes. | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Leak.png | file://x:/photopub/docs/0000000481/3a1a764a-c59c-4867-b31a-dbc7243efac8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d784d547_09b7_4683_8139_1243d08ca56a
BPVOP-644813-2016 | 2277662 | 9/7/2016 8:23:56 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 | During the inspection of a HP Steam Boiler with MAWP of 150 psig was found on the waterside heavy soft scale. This insulates the tubes and can cause overheating of the tubes. | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Scale_on_handhold_covers.png | file://x:/photopub/docs/0000000481/0af6c665-b497-4df6-bf9c-4bd9e71bdb51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d784d547_09b7_4683_8139_1243d08ca56a
ELIN-626959-2016 | UW-421734-2016 | 8/9/2016 1:22:51 PM | ASSESS: EL IN: Unsafe Condition | jpg | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Branch circuit does not have identified conductor. Possibility for energizing incorrect voltage resulting in shock. | 3 | Conductors Equipment is not approved for the specific use. | buried JB.jpg | file://x:/photopub/docs/0000000468/6c59bcf6-25b3-4085-8b05-f25415f2c925.jpg | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a4ce624c_522a_4208_b273_e0ceabf6da90
EDIN-606538-2016 | ED-346816-2016 | 7/22/2016 1:21:40 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED003 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 3 | 3 | Hoist way is constructed of hollow concrete block, the blocks are to filled with concrete to provide the strength needed to attach structural components to. In this case the brackets that hold the rails for the elevator. The blocks were not filled properly, and the bolts used are for filled block. No attempt to use proper alternate attachment method was used. | 3 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | Rail_bracket.png | file://x:/photopub/docs/0000000460/3d7327a2-6649-4e88-bd01-a3e70297e1ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8441cd1a_ee6f_46dc_8610_fb7ed31d0389
EDIN-606538-2016 | ED-346816-2016 | 7/22/2016 1:21:40 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED003 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 3 | 3 | Hoist way is constructed of hollow concrete block, the blocks are to filled with concrete to provide the strength needed to attach structural components to. In this case the brackets that hold the rails for the elevator. The blocks were not filled properly, and the bolts used are for filled block. No attempt to use proper alternate attachment method was used. | 3 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | Back_side_of_bolt.png | file://x:/photopub/docs/0000000460/241811b2-dcbb-4ee3-aa7a-468259636015.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8441cd1a_ee6f_46dc_8610_fb7ed31d0389
EDIN-606538-2016 | ED-346816-2016 | 7/22/2016 1:21:40 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED003 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 3 | 3 | Hoist way is constructed of hollow concrete block, the blocks are to filled with concrete to provide the strength needed to attach structural components to. In this case the brackets that hold the rails for the elevator. The blocks were not filled properly, and the bolts used are for filled block. No attempt to use proper alternate attachment method was used. | 3 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | Rail_bracket_1.png | file://x:/photopub/docs/0000000460/99abb0e9-bad5-4ae6-a69c-ff2eebc45f39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8441cd1a_ee6f_46dc_8610_fb7ed31d0389
ELIN-645654-2016 | EL-431328-2016 | 9/14/2016 1:38:26 PM | ASSESS: EL: Final | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The 15 amp 120 volt GFCI breaker labelled as the heat trace for the mobile home is not connected and no other GFCI was found as required by the used mobile home inspection report. No GFCI protection for the heat trace circuit can lead to a shock hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use | GFCI_breaker_wiring.png | file://x:/photopub/docs/0000000485/bd194a72-b631-42f2-b9a0-5ad28602f774.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a54066d_14f8_446f_a3bc_c4734edae446
ELIN-645654-2016 | EL-431328-2016 | 9/14/2016 1:38:26 PM | ASSESS: EL: Final | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The 15 amp 120 volt GFCI breaker labelled as the heat trace for the mobile home is not connected and no other GFCI was found as required by the used mobile home inspection report. No GFCI protection for the heat trace circuit can lead to a shock hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Heat_trace_gfci_breaker.png | file://x:/photopub/docs/0000000485/b1837062-4315-48c1-ac8b-4d6dc93f4626.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a54066d_14f8_446f_a3bc_c4734edae446
GAIN-606066-2016 | GA-350438-2016 | 9/6/2016 4:01:02 PM | ASSESS: GA: Final | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 2 |  | 2 | Non compliant Type B Vent Clearance | Laurier1.png | file://x:/photopub/docs/0000000481/b045686b-5507-4cc2-9968-fb59410ae07e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f09d881a_de63_4a1b_b2d9_d4ac7f795650
GAIN-606066-2016 | GA-350438-2016 | 9/6/2016 4:01:02 PM | ASSESS: GA: Final | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 2 |  | 2 | Non compliant Type B Vent Clearance | Laurier3.png | file://x:/photopub/docs/0000000481/97d6f3b6-38e5-4750-a6b8-b11c47afd195.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f09d881a_de63_4a1b_b2d9_d4ac7f795650
GAIN-606066-2016 | GA-350438-2016 | 9/6/2016 4:01:02 PM | ASSESS: GA: Final | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 2 |  | 2 | Non compliant Type B Vent Clearance | Laurier2.png | file://x:/photopub/docs/0000000481/c57805d0-d506-4ed5-aee3-4400eda73006.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f09d881a_de63_4a1b_b2d9_d4ac7f795650
ELIN-616988-2016 | EL-351059-2016 | 7/25/2016 2:49:10 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The electrical code requires that equipment that is installed be specific for its use. This is required to protect persons from energized equipment and to contain the thermal energy if there is a fault in the equipment. In a new residential single family home under construction, 240 volt receptacles where installed that did not fit correctly on the box that the receptacle was mounted to. Cover plates would not be able to be installed over these receptacles and would leave openings around the receptacles. The opening around the receptacle could lead to accidental contact with live energized parts and could create a shock or fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Dryer_receptacle_location.png | file://x:/photopub/docs/0000000461/7ee743b9-fefa-40da-9b10-8e71c52315e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0985e1ab_ae91_4763_a1b6_e84367e8f3e4
GAUP-623211-2016 | UW-419961-2016 | 9/16/2016 10:19:49 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA124 | Blocked combustion air supply | 4 | 4 | Combustion air opening for furnace was blocked off indoors. Insufficient combustion air may lead to incomplete combustion and the production of excessive amounts of carbon monoxide. | 4 | Blocked combustion air supply | Blocked_combustion_air_opening.png | file://x:/photopub/docs/0000000486/17eff8df-3b84-40ec-8182-229783ce2aac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a271de31_2681_4fb6_8083_7f7b578a3fab
ELIN-658738-2016 | EL-434888-2016 | 9/13/2016 12:21:18 PM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Two 20A 120V receptacles have been installed in a temporary construction service for temp power but they are not GFCI protected, this poses a shock hazard to persons and potential to damage equipment if used in wet conditions or with improperly grounded equipment. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | GFCI_Protection_not_provided.png | file://x:/photopub/docs/0000000484/84f9e235-8afa-401e-bf50-be5a9799a539.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab7e827c_4ce1_441e_a4f7_56c4961b7080
BPVOP-662032-2016 | BPV-0000290863-2015 | 9/13/2016 9:34:38 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP196 | 5.1.0 In service proc/process - Scale and deposit build up on fireside (fire tubes or furnace tubes) | 3 | 3 | During the inspection of a HP Steam Boiler with MAWP of 150 psig was found that the fireside had heavy red/white deposits(up to 50% blockage) likely from refractory. | 3 | 5.1.0 In service proc/process - Scale and deposit build up on fireside (fire tubes or furnace tubes) | Fireside_deposits.png | file://x:/photopub/docs/0000000484/a286289a-d1b1-4f61-a167-1b6e5f17af85.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f926157_0303_44c1_83ec_f2a1351e9757
ELIN-665284-2016 | UW-438765-2016 | 9/16/2016 11:52:54 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL232 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | 4 | 4 | Wood processing facilities are a combustible dust hazard. Accumulations of combustible dust is a fire and explosion hazard. As a guide line greater than 1/8th of an inch of dust accumulated on great than 5% of the surface area is a hazard. As per safety order SO-EL/GA 2013-02 these facilities are to have a hazardous location assessments completed and a mitigation plan documented, implemented and audited. | 4 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | A.png | file://x:/photopub/docs/0000000486/86052758-833d-4edc-b352-d30b9a63e3ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__715d8968_c277_4d5a_84dc_c797e3e16306
ELIN-631927-2016 | EL-330949-2016 | 8/19/2016 2:18:40 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Un-bonded metal gas pipe can have a hazardous standing voltage if becomes in contact with a faulty power circuit. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_bond.png | file://x:/photopub/docs/0000000473/b55693b4-9494-4a48-b5e2-cb82ada58d02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c436626c_814a_4537_a78b_c9fb5b216574
ELIN-616988-2016 | EL-351059-2016 | 7/25/2016 2:49:10 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The electrical code requires that equipment that is installed be specific for its use. This is required to protect persons from energized equipment and to contain the thermal energy if there is a fault in the equipment. In a new residential single family home under construction, 240 volt receptacles where installed that did not fit correctly on the box that the receptacle was mounted to. Cover plates would not be able to be installed over these receptacles and would leave openings around the receptacles. The opening around the receptacle could lead to accidental contact with live energized parts and could create a shock or fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Range_receptacle_location.png | file://x:/photopub/docs/0000000461/c98b877d-bd63-4b9f-9a17-b975ecf8b6cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0985e1ab_ae91_4763_a1b6_e84367e8f3e4
BPVOP-664486-2016 | 2303228 | 9/15/2016 10:13:53 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety valves and pressure relief devices require periodic service or replacement. I found no record of testing\service\replacement for safety valve(s) for 13 years for on a 30psi hot water boiler. Potential exists for a safety valve not to function properly and relieve the pressure in critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve_data_tag.png | file://x:/photopub/docs/0000000485/560a273c-55dc-4fbc-8016-d9b0cfbafec0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cc90a0f_6ee5_44eb_aeec_19317b33d107
BPVOP-664486-2016 | 2303228 | 9/15/2016 10:13:53 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety valves and pressure relief devices require periodic service or replacement. I found no record of testing\service\replacement for safety valve(s) for 13 years for on a 30psi hot water boiler. Potential exists for a safety valve not to function properly and relieve the pressure in critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Expired_Safety_releif_valves_.png | file://x:/photopub/docs/0000000485/fa67e0fa-82b1-4ec5-ad82-9a02f5d82294.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cc90a0f_6ee5_44eb_aeec_19317b33d107
ELIN-630852-2016 | EL-391226-2016 | 8/16/2016 10:28:16 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | 200A 120/240V Service is not properly grounded, the #6 copper ground conductor has been terminated at a bonding point instead of the neutral point. This could result in equipment damage and a shock hazard as the breakers may not operate as designed and undesirable current may be present on metal devices that could be contacted by persons. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_Wire.png | file://x:/photopub/docs/0000000471/7b0d043a-ad41-4608-8054-f34816e949dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ddd7e8c_eef7_4d0e_871f_0ec4d5418db5
ELIN-630430-2016 | EL-417450-2016 | 8/16/2016 11:35:11 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 |  | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | ACWU_fitting.png | file://x:/photopub/docs/0000000471/aa87fa67-f8c2-400f-89d8-14dff562efde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00403cd1_1d70_4490_bc1a_1c251370189a
ELHE-620766-2016 | HE-417719-2016 | 7/29/2016 9:38:41 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found altered unapproved 120 volt use portable flexible cord which has a male cord attachment plug installed on each end of flexible cord. When flexible cord is unapproved and altered to have a male cord attachment device on each end of cord, the cord will have exposed and energized cord end blades which is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | Cord_with_male_end_back_feeding_to_structure_receptacle_outlet3.png | file://x:/photopub/docs/0000000463/1449f37d-19a5-448e-b2aa-e4429d247190.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4387fc7_3702_4d21_a727_c54556d74831
ELIN-662191-2016 | EL-436003-2016 | 9/14/2016 9:54:38 AM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Main service grounding conductor terminated to enclosure, neutral grounded services require grounding connection at the neutral conductor. Terminating the ground at the neutral point provides a path for a fault to get to ground and have overcurrent devices act to clear the fault. Terminating the ground conductor at the enclosure may have overcurrent devices not act as required and may pose a risk of shock or damage to persons or property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Ground_terminated_to_enclosure_not_nuetral__.png | file://x:/photopub/docs/0000000485/cd4cc84b-73b8-485e-ad27-be604ad418fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__729e03bf_eda1_47f5_b8b0_0609385f4951
ELIN-623273-2016 | EL-381745-2016 | 8/4/2016 1:28:22 PM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Lark_3.png | file://x:/photopub/docs/0000000465/e60506b6-aae7-47ce-bd5c-3f957c2c1250.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1334d721_9da9_42c2_ad75_78e4c1f93a4f
ELIN-623273-2016 | EL-381745-2016 | 8/4/2016 1:28:22 PM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Lark_5.png | file://x:/photopub/docs/0000000465/1f3a1104-cb2a-42b5-aac4-440d37a7eb8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1334d721_9da9_42c2_ad75_78e4c1f93a4f
ELIN-623273-2016 | EL-381745-2016 | 8/4/2016 1:28:22 PM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Lark_4.png | file://x:/photopub/docs/0000000465/9c49a086-e1e0-4960-bc48-ed8f9e3711ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1334d721_9da9_42c2_ad75_78e4c1f93a4f
ELIN-623273-2016 | EL-381745-2016 | 8/4/2016 1:28:22 PM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Lark_2.png | file://x:/photopub/docs/0000000465/18dce224-72cf-495d-b0db-6df0fe62b3e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1334d721_9da9_42c2_ad75_78e4c1f93a4f
ELIN-623273-2016 | EL-381745-2016 | 8/4/2016 1:28:22 PM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Lark_1.png | file://x:/photopub/docs/0000000465/a808572c-6ade-4772-b718-a6f38ebf27be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1334d721_9da9_42c2_ad75_78e4c1f93a4f
ELIN-605738-2016 | EL-400912-2016 | 7/7/2016 2:36:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Overhead_service_cable_not_installed_.png | file://x:/photopub/docs/0000000453/b1486f21-1ff1-46d1-a9f5-247f0bccc2ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__980515bf_e248_41dd_b50d_10a62762ff07
ELIN-567144-2016 | UW-380781-2016 | 7/27/2016 11:56:40 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed energized electrical. Possibility for shock or fire | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Smoke_detector_not_installed_exposed_junction_box.png | file://x:/photopub/docs/0000000462/a04d183a-9932-4e55-ba97-0f2309601297.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__430fba7e_6ef1_49f8_823c_11088526d2be
ELIN-567144-2016 | UW-380781-2016 | 7/27/2016 11:56:40 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed energized electrical. Possibility for shock or fire | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_junction_box_at_jet_tub.png | file://x:/photopub/docs/0000000462/41792722-8e34-4794-99e3-52aee2ab9473.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__430fba7e_6ef1_49f8_823c_11088526d2be
ELIN-567144-2016 | UW-380781-2016 | 7/27/2016 11:56:40 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed energized electrical. Possibility for shock or fire | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Base_board_not_mounted.png | file://x:/photopub/docs/0000000462/e67e1f4e-9d88-427b-b18c-f3f3967d9cca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__430fba7e_6ef1_49f8_823c_11088526d2be
ELIN-617646-2016 | EL-411782-2016 | 7/27/2016 12:49:38 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | The 15 amp 120 volt energized receptacles do not include covers or GFCI protection leaving exposed terminals to accidental contact, this is a shock hazard | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exterior_outlet.png | file://x:/photopub/docs/0000000462/1fb50fc5-e947-46ac-a237-14c5a7559148.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91b7bce5_e4b3_4b2e_a79e_c10d64d96f9b
ELIN-617646-2016 | EL-411782-2016 | 7/27/2016 12:49:38 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | The 15 amp 120 volt energized receptacles do not include covers or GFCI protection leaving exposed terminals to accidental contact, this is a shock hazard | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Interior_outlet.png | file://x:/photopub/docs/0000000462/a65e852d-6428-4640-894e-d4547051c64a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91b7bce5_e4b3_4b2e_a79e_c10d64d96f9b
ELHE-620766-2016 | HE-417719-2016 | 7/29/2016 9:38:41 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found altered unapproved 120 volt use portable flexible cord which has a male cord attachment plug installed on each end of flexible cord. When flexible cord is unapproved and altered to have a male cord attachment device on each end of cord, the cord will have exposed and energized cord end blades which is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | One_flexible_cord_rewired_with_a_male_cord_attachment_plug_on_each_end_of_same_cord3.png | file://x:/photopub/docs/0000000463/2d7a9af2-9699-42c3-ad61-b7fda57c4513.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4387fc7_3702_4d21_a727_c54556d74831
ELHE-620766-2016 | HE-417719-2016 | 7/29/2016 9:38:41 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found altered unapproved 120 volt use portable flexible cord which has a male cord attachment plug installed on each end of flexible cord. When flexible cord is unapproved and altered to have a male cord attachment device on each end of cord, the cord will have exposed and energized cord end blades which is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | One_flexible_cord_rewired_with_a_male_cord_attachment_plug_on_each_end_of_same_cord4.png | file://x:/photopub/docs/0000000463/58ed3f26-6fdb-4ffd-a124-319662c2849d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4387fc7_3702_4d21_a727_c54556d74831
ELHE-620766-2016 | HE-417719-2016 | 7/29/2016 9:38:41 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found altered unapproved 120 volt use portable flexible cord which has a male cord attachment plug installed on each end of flexible cord. When flexible cord is unapproved and altered to have a male cord attachment device on each end of cord, the cord will have exposed and energized cord end blades which is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | Cord_with_male_end_back_feeding_to_structure_receptacle_outlet.png | file://x:/photopub/docs/0000000463/d23f9cb0-8d96-4ad4-b1fc-4c73a3ecacac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4387fc7_3702_4d21_a727_c54556d74831
ELHE-620766-2016 | HE-417719-2016 | 7/29/2016 9:38:41 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found altered unapproved 120 volt use portable flexible cord which has a male cord attachment plug installed on each end of flexible cord. When flexible cord is unapproved and altered to have a male cord attachment device on each end of cord, the cord will have exposed and energized cord end blades which is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | Cord_with_male_end_back_feeding_to_structure_receptacle_outlet4.png | file://x:/photopub/docs/0000000463/739ed082-08d0-44cf-b0d5-89c77727d1d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4387fc7_3702_4d21_a727_c54556d74831
ELHE-620766-2016 | HE-417719-2016 | 7/29/2016 9:38:41 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found altered unapproved 120 volt use portable flexible cord which has a male cord attachment plug installed on each end of flexible cord. When flexible cord is unapproved and altered to have a male cord attachment device on each end of cord, the cord will have exposed and energized cord end blades which is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | Cord_with_male_end_back_feeding_to_structure_receptacle_outlet2.png | file://x:/photopub/docs/0000000463/551065fa-0440-41aa-82dd-0c42ebcd7a88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4387fc7_3702_4d21_a727_c54556d74831
ELHE-620766-2016 | HE-417719-2016 | 7/29/2016 9:38:41 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found altered unapproved 120 volt use portable flexible cord which has a male cord attachment plug installed on each end of flexible cord. When flexible cord is unapproved and altered to have a male cord attachment device on each end of cord, the cord will have exposed and energized cord end blades which is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | One_flexible_cord_rewired_with_a_male_cord_attachment_plug_on_each_end_of_same_cord.png | file://x:/photopub/docs/0000000463/2803a0fc-751c-4c84-8ddf-d8847a6215f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4387fc7_3702_4d21_a727_c54556d74831
ELHE-620766-2016 | HE-417719-2016 | 7/29/2016 9:38:41 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found altered unapproved 120 volt use portable flexible cord which has a male cord attachment plug installed on each end of flexible cord. When flexible cord is unapproved and altered to have a male cord attachment device on each end of cord, the cord will have exposed and energized cord end blades which is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | One_flexible_cord_rewired_with_a_male_cord_attachment_plug_on_each_end_of_same_cord2.png | file://x:/photopub/docs/0000000463/f4aef970-cef1-4050-8b0a-975cc27dfe3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4387fc7_3702_4d21_a727_c54556d74831
ELHE-620766-2016 | HE-417719-2016 | 7/29/2016 9:38:41 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found altered unapproved 120 volt use portable flexible cord which has a male cord attachment plug installed on each end of flexible cord. When flexible cord is unapproved and altered to have a male cord attachment device on each end of cord, the cord will have exposed and energized cord end blades which is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | Cord_with_male_end_back_feeding_to_structure_receptacle_outlet5.png | file://x:/photopub/docs/0000000463/dd2108ec-f1c3-4421-bf7c-e5d6f40e7e5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4387fc7_3702_4d21_a727_c54556d74831
ELIN-622078-2016 | EL-418749-2016 | 8/3/2016 10:08:52 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Electrical contractor had installed armoured cable within a concrete slab, ac 90 cable is not approved for such use. The calcium in concrete will actually deteriate the exterior aluminum jacket of the cable and significantly increase the risk of electric shock. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Ac90_located_in_concrete_floor.png | file://x:/photopub/docs/0000000465/5522fff8-5806-4b2b-997d-a0b8b45af747.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ccab3a03_e5fe_472a_8780_961d171357f2
ELIN-618702-2016 | EL-408685-2016 | 7/27/2016 3:11:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 2 | 400 a meter main breaker serving as disconnect for house and shop: disconnect required inside buildings served for safety of persons and property as per directive. | 3 | General Equipment is not approved for the specific use | Lc.png | file://x:/photopub/docs/0000000462/c1e8fdfd-0b06-41b6-bf3a-0abbda5bea88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45ccf98b_2f85_4427_be1a_60c783e9d87b
EDIN-665315-2016 | ED-379341-2016 | 9/16/2016 3:29:23 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | A safe pathway across the roof to access the control room without fall hazard is essential for the safety of the elevator worker. During an acceptance inspection there was found to be a moderate fall hazard during access of the control room across the roof. The pathway is approximately 50 feet from the edge of the building, which is a considerable distance from the path. The fall hazard will put the safety of the elevator worker or anyone accessing the control room to be at a risk of injury or death. It was found the general contractor failed to recognize the need for the pathway to be provided with railing. This 15 stop MRL traction elevator is located In a newly constructed residential building. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Path_to_control_room_across_roof.png | file://x:/photopub/docs/0000000486/b635ff7f-5c29-4c08-82cc-74d9ab921530.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba0d0199_a73e_4b58_8cff_d996ae451f3b
ELIN-665060-2016 | EL-427103-2016 | 9/16/2016 11:41:13 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | NMD90 used for service conductors. And is not rated | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | NMD90_used_for_service_conductor_to_panel.png | file://x:/photopub/docs/0000000486/90fa634c-d42a-44eb-912d-5c280bffea73.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f7c0e79_f178_4a11_bf7c_b9c9f605a931
ELIN-665060-2016 | EL-427103-2016 | 9/16/2016 11:41:13 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | NMD90 used for service conductors. And is not rated | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | NMD90_used_for_service_conductor.png | file://x:/photopub/docs/0000000486/88ac116b-c177-43f9-a546-f5e6a195578b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f7c0e79_f178_4a11_bf7c_b9c9f605a931
ELHE-641363-2016 | HE-430474-2016 | 8/8/2016 11:29:16 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | This assessment found an underground cable that is buried too shallow. The cable crosses under a roadway and is exposed at the roads edge. This is in a beach area where there is public access. There is a shock hazard if the cable becomes exposed and damaged from vehicles. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Cable_under_road.png | file://x:/photopub/docs/0000000477/7b9eea91-7a9b-45c4-a09a-e0902e9bc9be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cbf5ed6_5dbb_468a_add8_1c3967d27f59
ELHE-641363-2016 | HE-430474-2016 | 8/8/2016 11:29:16 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | This assessment found an underground cable that is buried too shallow. The cable crosses under a roadway and is exposed at the roads edge. This is in a beach area where there is public access. There is a shock hazard if the cable becomes exposed and damaged from vehicles. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Cable_under_road_2.png | file://x:/photopub/docs/0000000477/13087339-4f12-459c-9755-fec370c31679.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cbf5ed6_5dbb_468a_add8_1c3967d27f59
ELHE-641363-2016 | HE-430474-2016 | 8/8/2016 11:29:16 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | This assessment found an underground cable that is buried too shallow. The cable crosses under a roadway and is exposed at the roads edge. This is in a beach area where there is public access. There is a shock hazard if the cable becomes exposed and damaged from vehicles. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | PVC_along_fence.png | file://x:/photopub/docs/0000000477/5fc29ba6-006a-40b5-bfd3-1e9797f99b38.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cbf5ed6_5dbb_468a_add8_1c3967d27f59
BPVIN-607846-2016 | BPV-307369-2015 | 7/8/2016 10:52:39 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Refrigeration_relief_line_termination.png | file://x:/photopub/docs/0000000462/3c277392-26c1-4cac-992c-776c47c4bfff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6457f17f_689c_4c79_b361_ad9dfabb2c99
BPVIN-619773-2016 | BPV-358234-2016 | 7/27/2016 1:53:20 PM | ASSESS: BPV IN: Piping | png | #asFound | BP025 | 1.0.2 Clearances/Maintenance - Failed visual welding inspection. | 3 | 3 | Upon the assessment of a Ammonia Condenser with MAWP of 250 psig, the visual welding inspection failed as per ASME B 31.5. | 3 | 1.0.2 Clearances/Maintenance - Failed visual welding inspection. | Weld_void.png | file://x:/photopub/docs/0000000462/a6a0e325-9aa2-4948-b34a-cd7727596d19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a85db52b_1483_44ee_8c11_e93d3eecc6c9
GAIN-512585-2016 | GA-320203-2015 | 8/2/2016 2:45:15 PM | ASSESS: GA: Final | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | Clearance between propane relief valve and mechanical air intake not maintained. In the event of a relieving valve, propane could be drawn into the combustion air intake of the appliance causing a fire or explosion. | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Cylinder_clearances_not_met_.png | file://x:/photopub/docs/0000000464/3bfac68a-d630-4d7a-aec2-a2965920b43e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3be39630_5a43_4fb9_b795_747b563522fb
GAIN-553859-2016 | GA-367640-2016 | 8/2/2016 11:46:11 AM | ASSESS: GA: Final | png | #asFound | GA055 | Bonding for Corrugated Stainless Steel Tubing missing | 3 | 3 | Corrugated stainless steel tubing not bonded. Corrugated stainless steel tubing can be damaged by electrical faults causing uncontrolled release of gas. | 3 | Bonding for Corrugated Stainless Steel Tubing missing | Corrugated_stainless_steel_tubing_not_bonded_.png | file://x:/photopub/docs/0000000464/83306a4c-d6ee-4242-b251-e6cc21eaeb6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__088027be_08db_4fe5_85d7_bdec88d2c13c
ELIN-621824-2016 | EL-413825-2016 | 8/17/2016 3:45:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | A pump controller for a 5 horsepower 240 volt water utility did not have a nameplate indicating capacity, make model or evidence of certification. Electrical equipment that does not bear this information can be utilized unsafely and where lacking certification can present a hazard for damage to property or injury to persons | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Telemetry_pump_controller_does_not_bear_evidence_of_approval_and_no_nameplate.png | file://x:/photopub/docs/0000000472/1120ea52-9a72-43ac-b5b9-9e0d79c77489.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__364da5b8_55f8_43b4_8f56_276816dcfdf7
ELIN-629281-2016 | EL-346001-2016 | 8/17/2016 2:44:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | A new 200 amp 240 volt 1 phase residential service was authorized for connection to the utility. The service panel was not locked to prevent unauthorized access, or use. Electrical equipment that is accessible to u authorized operation can present a safety hazard to persons | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_accessible_to_unauthorized_operation_temp_to_perm.png | file://x:/photopub/docs/0000000472/20923861-7ed5-4590-a56b-9d547199a228.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a67dfe92_c66f_4c4c_8898_f437624c25b1
ELIN-603909-2016 | EL-402331-2016 | 7/5/2016 2:37:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | The new service panel has been installed in a unfinished garage wall with no protection from the rain. The service panels main breaker has been wetted. This may prevent the breaker from functioning or short the breaker out causing a shock hazard or fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 1_.png | file://x:/photopub/docs/0000000452/e5e418d6-856b-440c-b848-180110bf7675.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__751c2a6c_d96b_477f_824f_82008c4775b5
ELIN-603909-2016 | EL-402331-2016 | 7/5/2016 2:37:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | The new service panel has been installed in a unfinished garage wall with no protection from the rain. The service panels main breaker has been wetted. This may prevent the breaker from functioning or short the breaker out causing a shock hazard or fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 2.png | file://x:/photopub/docs/0000000452/f7e2be62-7823-423b-8529-cf7cac4c1496.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__751c2a6c_d96b_477f_824f_82008c4775b5
ELIN-603909-2016 | EL-402331-2016 | 7/5/2016 2:37:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | The new service panel has been installed in a unfinished garage wall with no protection from the rain. The service panels main breaker has been wetted. This may prevent the breaker from functioning or short the breaker out causing a shock hazard or fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 1.png | file://x:/photopub/docs/0000000452/f7c27ee3-29c8-4463-99f4-3d6efa4ca4d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__751c2a6c_d96b_477f_824f_82008c4775b5
ELIN-603909-2016 | EL-402331-2016 | 7/5/2016 2:37:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | The new service panel has been installed in a unfinished garage wall with no protection from the rain. The service panels main breaker has been wetted. This may prevent the breaker from functioning or short the breaker out causing a shock hazard or fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 2_.png | file://x:/photopub/docs/0000000452/7ded5428-3a9d-42c0-a72b-b8a36c2aeb6f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__751c2a6c_d96b_477f_824f_82008c4775b5
GAIN-605766-2016 | GA-388104-2016 | 7/8/2016 11:19:11 AM | ASSESS: GA: Final | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 2 |  | 2 | Non compliant Type B Vent Clearance | Oak_street.png | file://x:/photopub/docs/0000000454/52b709d9-e767-4e9a-89d4-cc58c8921b52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54296731_dd61_4f16_9751_2929e33d2974
GAIN-613207-2016 | GA-409938-2016 | 8/2/2016 8:51:01 AM | ASSESS: GA: Final | png | #asFound | GA093 | Under sized system regulator for multiple appliances = < 10% | 3 | 3 | 2 psi to inches regulator undersized for total connected load, this could cause appliances to be under fired as not adequate gas can be supplied. | 3 | Under sized system regulator for multiple appliances = < 10% | Wes1.png | file://x:/photopub/docs/0000000464/32532fb1-5fd3-488b-8718-d10aafa51412.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d22f3b17_2816_4619_b4f3_e7ec8970201d
ELIN-664796-2016 | EL-344694-2016 | 9/16/2016 1:24:01 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL191 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | 3 | 3 | Energized circuit | 3 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | Energized_circuit.png | file://x:/photopub/docs/0000000486/b57877ee-98fe-460c-82bb-d59610a3819a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e69c41c_9fb3_4f7e_87ca_61459087029f
ELIN-619168-2016 | EL-416682-2016 | 8/18/2016 1:33:42 PM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Exposed energized conductors and connections for hallway lights in direct contact with combustible ceiling finish Exposed energized conductors in contact with with combustible material may present a thermal or shock hazard | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Bent_service_mast.png | file://x:/photopub/docs/0000000472/24c803f8-960b-4d78-96cd-f24273a21d26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e793f585_4a14_449b_bb6b_6e413c4e6bd8
ELIN-619168-2016 | EL-416682-2016 | 8/18/2016 1:33:42 PM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Exposed energized conductors and connections for hallway lights in direct contact with combustible ceiling finish Exposed energized conductors in contact with with combustible material may present a thermal or shock hazard | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Shed_wiring.png | file://x:/photopub/docs/0000000472/8507ca5d-2537-41dc-ae14-63461de4bd67.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e793f585_4a14_449b_bb6b_6e413c4e6bd8
ELIN-619168-2016 | EL-416682-2016 | 8/18/2016 1:33:42 PM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Exposed energized conductors and connections for hallway lights in direct contact with combustible ceiling finish Exposed energized conductors in contact with with combustible material may present a thermal or shock hazard | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Conductors_not_in_box.png | file://x:/photopub/docs/0000000472/cd5e71b1-57c3-420f-95b8-ac64ad209a55.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e793f585_4a14_449b_bb6b_6e413c4e6bd8
ELIN-619168-2016 | EL-416682-2016 | 8/18/2016 1:33:42 PM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Exposed energized conductors and connections for hallway lights in direct contact with combustible ceiling finish Exposed energized conductors in contact with with combustible material may present a thermal or shock hazard | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | kit_Fluor_light.png | file://x:/photopub/docs/0000000472/5df2807a-c60c-445e-940f-f7110413515b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e793f585_4a14_449b_bb6b_6e413c4e6bd8
ELIN-619168-2016 | EL-416682-2016 | 8/18/2016 1:33:42 PM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Exposed energized conductors and connections for hallway lights in direct contact with combustible ceiling finish Exposed energized conductors in contact with with combustible material may present a thermal or shock hazard | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Single_conductors_addition.png | file://x:/photopub/docs/0000000472/9c4f03e7-a194-4cc7-8ca8-a6eebb83a1fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e793f585_4a14_449b_bb6b_6e413c4e6bd8
ELOP-627672-2016 | 2168170 | 8/25/2016 8:39:28 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Transformer.png | file://x:/photopub/docs/0000000475/8cd8ef98-cd2a-456d-b26b-4151652a627c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__930a5024_927d_4b44_8091_3ae789173ff6
ELIN-607044-2016 | EL-343832-2016 | 7/14/2016 11:58:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Exterior_meter_base.png | file://x:/photopub/docs/0000000456/e50ad0a9-05a6-46d2-b874-9f0285e985e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f785285e_18a9_4764_b6df_10b4306e37be
ELIN-607044-2016 | EL-343832-2016 | 7/14/2016 11:58:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Ground_exists_here.png | file://x:/photopub/docs/0000000456/dd60094c-0d43-4f25-a8d3-d90a7f033741.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f785285e_18a9_4764_b6df_10b4306e37be
GAIN-610851-2016 | GA-354200-2016 | 7/14/2016 8:20:22 AM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | Draft hood not installed at minimum height required in the manufacturers installation instructions. Incorrect draft hood height may cause improper venting. | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Pressure_washer_venting.png | file://x:/photopub/docs/0000000456/08b7c3b1-cdff-4602-a662-5963773b6d3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27ed8df2_0141_43c2_83b6_8cf1d4c2da50
ELIN-645018-2016 | EL-368828-2016 | 9/7/2016 2:01:32 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non metallic sheathed cable installed on upper faces of ceiling joists with greater than 1m clearance to the roof. This is considered walkable space and is a shock and fire hazard as the cables can become damaged if someone should step on them and damage the cables. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C.png | file://x:/photopub/docs/0000000482/3e1a2c3c-90ac-47da-86a5-4a6333434440.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7739977a_c4d7_4f3f_a5ea_cfa8bd5c206c
ELIN-645018-2016 | EL-368828-2016 | 9/7/2016 2:01:32 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non metallic sheathed cable installed on upper faces of ceiling joists with greater than 1m clearance to the roof. This is considered walkable space and is a shock and fire hazard as the cables can become damaged if someone should step on them and damage the cables. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | E.png | file://x:/photopub/docs/0000000482/d76bdd73-c0b4-4200-822a-5784165a4148.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7739977a_c4d7_4f3f_a5ea_cfa8bd5c206c
ELIN-645018-2016 | EL-368828-2016 | 9/7/2016 2:01:32 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non metallic sheathed cable installed on upper faces of ceiling joists with greater than 1m clearance to the roof. This is considered walkable space and is a shock and fire hazard as the cables can become damaged if someone should step on them and damage the cables. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | F.png | file://x:/photopub/docs/0000000482/47554715-ab3f-4c44-a8c3-3a7acdf97101.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7739977a_c4d7_4f3f_a5ea_cfa8bd5c206c
ELIN-645018-2016 | EL-368828-2016 | 9/7/2016 2:01:32 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non metallic sheathed cable installed on upper faces of ceiling joists with greater than 1m clearance to the roof. This is considered walkable space and is a shock and fire hazard as the cables can become damaged if someone should step on them and damage the cables. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000482/67673084-9d17-488b-8a22-f36a34b19260.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7739977a_c4d7_4f3f_a5ea_cfa8bd5c206c
ELIN-645018-2016 | EL-368828-2016 | 9/7/2016 2:01:32 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non metallic sheathed cable installed on upper faces of ceiling joists with greater than 1m clearance to the roof. This is considered walkable space and is a shock and fire hazard as the cables can become damaged if someone should step on them and damage the cables. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | D.png | file://x:/photopub/docs/0000000482/ec877ba3-48a9-4b56-ab28-309100abe344.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7739977a_c4d7_4f3f_a5ea_cfa8bd5c206c
ELIN-645018-2016 | EL-368828-2016 | 9/7/2016 2:01:32 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non metallic sheathed cable installed on upper faces of ceiling joists with greater than 1m clearance to the roof. This is considered walkable space and is a shock and fire hazard as the cables can become damaged if someone should step on them and damage the cables. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | B.png | file://x:/photopub/docs/0000000482/d817fe69-e0d1-4628-aa08-1b3284093c32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7739977a_c4d7_4f3f_a5ea_cfa8bd5c206c
BPVOP-664510-2016 | 2277840 | 9/15/2016 11:19:23 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety valves and pressure relief devices require periodic service or replacement. I found no record of testing\service\replacement for safety valve(s) for 16 years on a 30psi hot water boiler. Potential exists for a safety valve not to function properly and relieve the pressure in critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve_data_tag.png | file://x:/photopub/docs/0000000485/5abd276c-fa72-4eaa-a58d-e8a5c45a0462.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3e5d4c6_6ecc_4cbe_a862_7e8032844021
BPVOP-664510-2016 | 2277840 | 9/15/2016 11:19:23 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety valves and pressure relief devices require periodic service or replacement. I found no record of testing\service\replacement for safety valve(s) for 16 years on a 30psi hot water boiler. Potential exists for a safety valve not to function properly and relieve the pressure in critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valves_2000.png | file://x:/photopub/docs/0000000485/a0ef564d-8062-4ec1-a687-2c28185c5a3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3e5d4c6_6ecc_4cbe_a862_7e8032844021
ELIN-661269-2016 | EL-436160-2016 | 9/14/2016 2:46:28 PM | ASSESS: EL: Service Connection | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #14 Size wire terminated on 20A breakers. This is a thermal heating condition. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | _14_AWG_size_conductor_terminated_on_20A_breakers_.png | file://x:/photopub/docs/0000000485/21314f00-c034-4ccb-80a7-22b92cc26eff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed2ae737_7d54_4ba7_9f28_7c599c76b4ec
ELIN-606680-2016 | EL-383990-2016 | 7/7/2016 1:58:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | Enclosure not of weather proof construction | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Enclosure.png | file://x:/photopub/docs/0000000453/f065907c-15d8-4a46-87b7-430a130d4144.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba7243e1_b0d4_4dfb_b1e2_b81ff6a5e4c8
BPVOP-610128-2016 | 2273705 | 7/12/2016 10:13:31 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | While inspecting replacement safety valves on this hot water boiler it was observed that the set pressure of one of the valves was set to 65 PSI but the Maximum Allowable Working Pressure (MAWP) of the boiler is 60 PSI. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | SAFETY_VALVE.png | file://x:/photopub/docs/0000000455/286d15aa-5fc0-45f7-b3f8-fda7d4c5299d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a939e109_ad21_4d64_8eb4_5c97a360ad8d
EDIN-634775-2016 | ED-371729-2016 | 8/19/2016 4:45:23 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | The door for the control space only opens 100deg's, when open and personal are working on equipment, it traps them in the space, and restricts access to the fire extinguisher if needed. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Control_space_door.png | file://x:/photopub/docs/0000000473/e07a375e-6a96-410d-8e36-defd3f4ebcbe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee148de7_227a_4e47_abb8_2396afba6c34
GAIN-374034-2015 | GA-247675-2015 | 8/24/2016 11:29:34 AM | ASSESS: GA: Final | png | #asFound | GA045 | Gas connector passes through wall, floor, ceiling, partition or into appliance | 2 | 2 |  | 2 | Gas connector passes through wall, floor, ceiling, partition or into appliance | 1600.png | file://x:/photopub/docs/0000000475/b9162fc4-192a-45fa-a53f-348edc0d9b6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__679a76bd_ed95_486f_a233_38d8085738f6
ELIN-663372-2016 | EL-423488-2016 | 9/16/2016 10:11:59 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | The cable which connects the neutral in the electrical panel is attached at the wrong point. This could lead to the white wires and the bare wires in the house being at different voltages which could present a shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Ground_connection.png | file://x:/photopub/docs/0000000486/54deec06-9d42-45e1-a577-4c5af3261edc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8edaf76f_52e9_4163_bbbe_95190da50c37
ELIN-643258-2016 | EL-433040-2016 | 9/6/2016 11:11:18 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 2 | 15A construction receptacle fed with a 20A breaker. This is a potential fire hazard as the 15A receptacle could over heat. | 3 | Conductors Equipment is not approved for the specific use. | B.png | file://x:/photopub/docs/0000000480/0808246d-747c-4f45-b156-be1ae90ee642.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40fb3f64_8a0f_413f_82d0_dd9cf31ffe75
ELIN-643258-2016 | EL-433040-2016 | 9/6/2016 11:11:18 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 2 | 15A construction receptacle fed with a 20A breaker. This is a potential fire hazard as the 15A receptacle could over heat. | 3 | Conductors Equipment is not approved for the specific use. | A.png | file://x:/photopub/docs/0000000480/a88c35e5-e0e7-41e9-9ba7-939d2fcac788.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40fb3f64_8a0f_413f_82d0_dd9cf31ffe75
BPVOP-631650-2016 | 2268224 | 8/16/2016 9:16:35 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Upon assessment of low pressure steam heating boiler with 60 square meters heating surface it is determined that capacity of safety valve is less than theoretical minimum capacity required. In the event of over-pressure built up in the boiler (due to failure of control and other safety devices) there is possibility of permanent damage or even rupture of pressure boundary of boiler which can lead to incident. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Burner_nameplate.png | file://x:/photopub/docs/0000000471/52e5295b-400a-4af6-98b2-17ea150bdc18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d72258c_8cc7_4c08_ae38_1a71ff74aaeb
ELIN-659253-2016 | EL-434358-2016 | 9/15/2016 12:37:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | A new residential service 200 amps and 240 volts is installed. The meter combination service entrance equipment is secured to the pole by wood screws at an angle int the service pole. This can allow water into the electrical equipment and cause property damage or injury to persons | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Screws_will_allow_water_into_meter_enclosure.png | file://x:/photopub/docs/0000000486/8022b05b-b9b8-4449-a0a3-809da1a74df6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aecd3c6a_f1a9_4061_bad2_ee6538e71099
BPVIN-662785-2016 | UW-437266-2016 | 9/13/2016 3:53:36 PM | ASSESS: BPV IN: Installation REF/PV | png | #asFound | BP210 | 5.1.1 Work done: unqualified ind - Maintenance done by unlicensed contractor or unqualified individual | 2 | 2 | A person must hold a contractors license in order to perform regulated work. I found work was done by a contractor, who did not hold a refrigeration licence for work carried out on refrigeration equipment greater than 5kw. This can result in an incident, because the unlicensed contractor is unfamiliar of the code requirements for the scope of work performed. | 2 | 5.1.1 Work done: unqualified ind - Maintenance done by unlicensed contractor or unqualified individual | Contractor_invoice.png | file://x:/photopub/docs/0000000485/73392675-5b58-4667-8516-46f9b9115254.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de44b3b4_b217_4052_835e_7b30a059c134
BPVOP-661860-2016 | 2253269 | 9/13/2016 8:43:27 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety valves and pressure relief devices require periodic service or replacement. I found no record of testing\service\replacement for safety valves for 14 years on a 160psi hot water boiler. Potential exists for a safety valve not to function properly/ relieve pressure in critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_releif_Valve_2002.png | file://x:/photopub/docs/0000000484/daa90f29-8f14-4a7b-b0b8-a3eb4d43b1fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__546b14bd_f2b1_408a_8e1a_3d53f20503f0
BPVOP-661860-2016 | 2253269 | 9/13/2016 8:43:27 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety valves and pressure relief devices require periodic service or replacement. I found no record of testing\service\replacement for safety valves for 14 years on a 160psi hot water boiler. Potential exists for a safety valve not to function properly/ relieve pressure in critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Expired_Safety_relief_valves_.png | file://x:/photopub/docs/0000000484/faf06f4c-0b8d-4701-b288-df03f6fcbd03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__546b14bd_f2b1_408a_8e1a_3d53f20503f0
ELOP-623390-2016 | 5400100 | 8/4/2016 10:32:21 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | Fire alarm systems are required to be in safe working conditions. This is required to ensure the fire alarm system will function in the event of a fire and provide early warning to protect persons and structures. An annual electrical inspection of a grocery store showed a trouble condition ( ground fault)on the fire alarm panel. A fire alam panel with a trouble condition may not function correctly in the event of a fire. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Inspection_Tag.png | file://x:/photopub/docs/0000000466/a8163321-c411-4905-870d-122608f3bbb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0552493f_5950_4f55_ac73_4c278b805c65
AMOP-606852-2016 | AM-397058-2016 | 7/7/2016 11:29:21 AM | ASSESS: AM OP: Periodic | png | #asFound | AM002 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | 3 | 3 | It was observed that this device was being operated under a non-self supporting tarp in rain conditions. There is no evidence that the tarp meets 2 second flameout standard. One of 2 blowers was being operated under the tarp. Manufacturer has indicated that this unit is not designed to support a cover (i.e. Tarp). There could be significant challenges in evacuating participant from the device in event of power failure. There is a fire hazard as the tarp does probably does not have a fire rating and the fact that one of the blowers was operating under the tarp there would be a risk that the blower could over heat and provide a source of ignition. | 3 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | Device_operating_under_tarp_in_light_rain.png | file://x:/photopub/docs/0000000453/843cb5fa-e71c-4f90-a32e-fca33e888dce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c31d1da_07da_4904_94dc_d0188ede7b42
AMOP-606852-2016 | AM-397058-2016 | 7/7/2016 11:29:21 AM | ASSESS: AM OP: Periodic | png | #asFound | AM002 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | 3 | 3 | It was observed that this device was being operated under a non-self supporting tarp in rain conditions. There is no evidence that the tarp meets 2 second flameout standard. One of 2 blowers was being operated under the tarp. Manufacturer has indicated that this unit is not designed to support a cover (i.e. Tarp). There could be significant challenges in evacuating participant from the device in event of power failure. There is a fire hazard as the tarp does probably does not have a fire rating and the fact that one of the blowers was operating under the tarp there would be a risk that the blower could over heat and provide a source of ignition. | 3 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | Device_operating_in_rain_under_tarp.png | file://x:/photopub/docs/0000000453/5f3671a6-1a61-4209-ac7a-65a31ba18beb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c31d1da_07da_4904_94dc_d0188ede7b42
EDIN-645086-2016 | ED-389708-2016 | 9/7/2016 11:11:29 AM | ASSESS: ED IN: Acceptance | png | #asFound | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | The lift call station at the top landing was installed in a medium traffic area (underground parking). No Audio/Visual was present to warn drivers in vehicles to watch for users the are operating the lift. There were no Yellow marking to also warn drivers to avoid refuge area where users of the lift would be in front of the Hall Station. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Top_hall_station2.png | file://x:/photopub/docs/0000000481/605680f6-69e5-42a3-911a-718282b4d6cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2cff53fa_8b33_4ce8_9db8_e93b316194c0
EDIN-645086-2016 | ED-389708-2016 | 9/7/2016 11:11:29 AM | ASSESS: ED IN: Acceptance | png | #asFound | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | The lift call station at the top landing was installed in a medium traffic area (underground parking). No Audio/Visual was present to warn drivers in vehicles to watch for users the are operating the lift. There were no Yellow marking to also warn drivers to avoid refuge area where users of the lift would be in front of the Hall Station. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Top_Hall_Station1.png | file://x:/photopub/docs/0000000481/7864e25a-66c9-4037-8de4-7c11f8e13fab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2cff53fa_8b33_4ce8_9db8_e93b316194c0
GAUP-662389-2016 | UW-436919-2016 | 9/13/2016 9:58:33 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA163 | Use of appliance/accessories that creates a immediate hazard (Risk Registry Item GA-04) | 5 | 5 | A Hot Water Tank (HWT) is installed in a bedroom. Any issues with HWT venting or gas piping (Spillage of Combustion Gases or Leaking Gas) could cause injury or death to occupant of bedroom. | 5 | Use of appliance/accessories that creates a immediate hazard (Risk Registry Item GA-04) | HWT_located_in_bedroom.png | file://x:/photopub/docs/0000000484/198ec706-1b51-497c-b0ff-66472cd26ebb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e65dc29e_d657_43d9_831b_18d5742fb72a
ELIN-644906-2016 | EL-419757-2016 | 9/9/2016 10:45:10 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Multiple locations in workshop/shed where non metallic sheathed cable has been installed to ground level receptacles. mechanical protection is required for this type of cable if used below 1.5 meters, if cable was struck the soft jacket would not provide mechanical protection and may expose energized conductors, thus a shock and fire risk to persons and property would be present. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Non_metallic_sheathed_cable_not_mechanically_protected.png | file://x:/photopub/docs/0000000482/09e11c52-c364-4982-92c2-8b120703c0de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__027003bd_5957_41b3_a199_2f09f23fd1c0
ELIN-649745-2016 | EL-434162-2016 | 9/9/2016 12:40:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL202 | Energized work by qualified persons High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | 3 | 3 | New 200 amp service panel found energized, existing hydro meter is installed and clip in place. Service feeder conductors were installed in an energized state, accidental contact with energized conductors by persons or conductive material would cause shock and fire to persons and property. | 3 | Energized work by qualified persons High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | Rigid_conduit_and_service_conductors_installed_in_new_panel.png | file://x:/photopub/docs/0000000482/72984ca9-1d0b-4f62-8949-4afe3fcd39b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__88126a98_0949_41a7_a9d6_07df1742fd5e
ELOP-190506-2014 | 1865 | 8/5/2016 9:57:47 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | Private outdoor high voltage transformer installations must include a metal fence which is bonded to ground in a particular fashion. In this chipper mill installation a fence had been installed around a transformer but the bonding had not been completed. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Unbounded_fence.png | file://x:/photopub/docs/0000000466/d72abb4b-30d2-4bfb-99b8-44f06059653a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2341de33_1e0b_4c4d_b167_a6b1d3f65877
AMOP-630517-2016 | 2044502 | 8/15/2016 2:33:28 PM | ASSESS: AM OP: Operational | png | #asFound | AM000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Pic3.png | file://x:/photopub/docs/0000000470/e565eaab-e417-4605-aaca-5d5820ac3d25.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3e2abd5_a74a_4b41_a370_c0d2a4685cd3
AMOP-630517-2016 | 2044502 | 8/15/2016 2:33:28 PM | ASSESS: AM OP: Operational | png | #asFound | AM000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Pic2.png | file://x:/photopub/docs/0000000470/775ebe56-f569-49a9-839a-3d229558932a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3e2abd5_a74a_4b41_a370_c0d2a4685cd3
ELIN-608352-2016 | EL-267094-2015 | 7/11/2016 4:28:04 PM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 400 amp 600 volt service equipment is energized and exposed to weather conditions. Structure was not completed and requires lockable enclosure. This can be both an equipment damage and shock hazard | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Missing_roof_flashing.png | file://x:/photopub/docs/0000000454/d6c5e3d4-8820-4599-9595-9fcf41bb0b82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be2d30ee_cb16_45ff_af0b_f8f8343777de
ELIN-608352-2016 | EL-267094-2015 | 7/11/2016 4:28:04 PM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 400 amp 600 volt service equipment is energized and exposed to weather conditions. Structure was not completed and requires lockable enclosure. This can be both an equipment damage and shock hazard | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Open_structure.png | file://x:/photopub/docs/0000000454/0aa1b4c4-6885-42a0-b698-6fda361da961.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be2d30ee_cb16_45ff_af0b_f8f8343777de
ELIN-607991-2016 | EL-408759-2016 | 7/11/2016 11:54:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 200 amp 120/240 volt panel enclosure is not built of approved materials and may allow moisture (rain) into enclosure with non-weather proof equipment. This can lead to both an equipment damage issue and a shock hazard | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Front_view_top.png | file://x:/photopub/docs/0000000454/ff29bde1-be9a-4492-8af5-fc2cf62b518e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c74ff26_0c1e_42a5_afdc_4583442eef37
ELIN-607991-2016 | EL-408759-2016 | 7/11/2016 11:54:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 200 amp 120/240 volt panel enclosure is not built of approved materials and may allow moisture (rain) into enclosure with non-weather proof equipment. This can lead to both an equipment damage issue and a shock hazard | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | No_overhang_or_wp.png | file://x:/photopub/docs/0000000454/7e812e21-9b67-4c78-a621-33b9089830d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c74ff26_0c1e_42a5_afdc_4583442eef37
ELIN-607991-2016 | EL-408759-2016 | 7/11/2016 11:54:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 200 amp 120/240 volt panel enclosure is not built of approved materials and may allow moisture (rain) into enclosure with non-weather proof equipment. This can lead to both an equipment damage issue and a shock hazard | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Front_view.png | file://x:/photopub/docs/0000000454/4cc9a5c2-3d22-4056-ba52-1354a3c919cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c74ff26_0c1e_42a5_afdc_4583442eef37
ELIN-607991-2016 | EL-408759-2016 | 7/11/2016 11:54:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 200 amp 120/240 volt panel enclosure is not built of approved materials and may allow moisture (rain) into enclosure with non-weather proof equipment. This can lead to both an equipment damage issue and a shock hazard | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | No_overhang.png | file://x:/photopub/docs/0000000454/78b13f8c-b6af-421b-96a0-cfde6092eee8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c74ff26_0c1e_42a5_afdc_4583442eef37
ELIN-607991-2016 | EL-408759-2016 | 7/11/2016 11:54:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 200 amp 120/240 volt panel enclosure is not built of approved materials and may allow moisture (rain) into enclosure with non-weather proof equipment. This can lead to both an equipment damage issue and a shock hazard | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Door_not_closing.png | file://x:/photopub/docs/0000000454/fc28e34c-a55c-40b3-87cd-272d9a05f466.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c74ff26_0c1e_42a5_afdc_4583442eef37
ELIN-607991-2016 | EL-408759-2016 | 7/11/2016 11:54:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 200 amp 120/240 volt panel enclosure is not built of approved materials and may allow moisture (rain) into enclosure with non-weather proof equipment. This can lead to both an equipment damage issue and a shock hazard | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Door_not_closing_when_receptacle_lid_is_open.png | file://x:/photopub/docs/0000000454/293a65a6-0509-410c-be08-8b7c19428acd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c74ff26_0c1e_42a5_afdc_4583442eef37
ELIN-607989-2016 | EL-406932-2016 | 7/11/2016 10:06:56 AM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | The 15 amp 120 volt temporary GFCI receptacles do not include any protection in form of cover plate or approved alternative, the openings are greater than 6.75mm and this is a shock hazard | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | No_covers_on_receptacles.png | file://x:/photopub/docs/0000000454/fdc9b737-fa5e-4e52-94f9-3df4ea2114f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43173c13_58a8_45e0_8f85_2ce05c0fc6d5
BPVOP-601133-2016 | 2259779 | 6/26/2016 3:23:38 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP057 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | 2 | 2 | The tube ends on 5 boiler tubes exhibited signs of leakage under Hydrostatic test pressure requiring them to be replaced prior to being able to safely run the boiler. The contractor had difficulty removing the damaged tubes due to excessive accumulation of hard scale on the tube outer surfaces. This accumulation is greater than what was observed during last year's annual inspection. The accumulation of hard scale on the boiler tubes will reduce the amount of heat transferred from the heat source to the fluid it is heating resulting in greater output being required from the boiler to achieve the desired setting and lowering the overall efficiency of the boiler. | 2 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | LEAKING_TUBES.png | file://x:/photopub/docs/0000000449/db423892-a810-46a4-9105-cf160406d840.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a64e4aac_bb02_438e_ad1e_a246af7dccf0
GAIN-628582-2016 | GA-422672-2016 | 8/25/2016 7:31:32 AM | ASSESS: GA: Final | png | #asFound | GA039 | Painting of exterior piping | 1 | 1 |  | 1 | Painting of exterior piping | 1540_Davie_St.png | file://x:/photopub/docs/0000000475/05a92d71-5d80-4801-8fc3-e8bbce3e194d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4386d369_f590_4617_a91e_eac36859d680
ELIN-642360-2016 | EL-423688-2016 | 9/1/2016 3:12:30 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | AC90_unstrapped.png | file://x:/photopub/docs/0000000479/10646a9a-2209-4271-ae7c-0398edb103f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c40cfe9_e1f7_4517_8590_22ad2c1b7d21
ELIN-642360-2016 | EL-423688-2016 | 9/1/2016 3:12:30 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Ac90_at_switch.png | file://x:/photopub/docs/0000000479/36366319-f837-4e3f-98d7-db08013fb95b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c40cfe9_e1f7_4517_8590_22ad2c1b7d21
ELIN-607507-2016 | EL-406849-2016 | 7/14/2016 10:45:51 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL134 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | 3 | 3 | Various 15 amp 120 volt exterior and interior outlet boxes are recessed beyond the 6 mm maximum, this creates a thermal hazard to combustible materials exposed to the electrical wiring installation | 3 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | Outlet_box_installation.png | file://x:/photopub/docs/0000000456/586e53be-ac52-4181-9945-706bbcb8c611.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41f33a5a_b350_4cb1_8b46_87190dab3792
ELIN-606147-2016 | EL-250268-2015 | 7/14/2016 12:57:15 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | The 200 amp 120/240 volt energized panel has cover removed. This is a shock hazard. Owner notified no circuits are o be energized prior to inspection | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_panel.png | file://x:/photopub/docs/0000000456/759cbf5f-6f2d-43dc-8295-89ca555065db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b65c4815_28fc_4656_bada_2a63997fd51e
ELIN-641217-2016 | EL-429187-2016 | 9/8/2016 6:11:37 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical equipment is to be installed and guarded so that adequate provisions are made for the safety of persons and property. In this installation, a home owner installed new branch circuit wiring and two feeder cables for two new sub-panels into the existing, energized main electrical panel during a renovation. At the time of the inspection, the main panel and sub-panel in the basement where complete with panel covers. The sub-panel in the garage was open and so was the dryer receptacle which was feed from the sub-panel. No devices where installed on the boxes in the renovation area and the new conductors for branch circuits and sub-panel feeders where terminated onto the breakers of an existing energized panel. The breakers for the new conductors where in the "off" position. If the breakers in the main panel where turned on, there is a potential for a shock hazard if a persons came in contact with the exposed buss in the garage sub-panel or the energized conductors at any of the new device locations. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_buss_and_conductors.png | file://x:/photopub/docs/0000000482/67f5f4ec-a554-46b4-bd6a-d31e742bfc3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e9caaf7_f5d1_4e7b_8871_19ac16cfdf80
ELIN-641217-2016 | EL-429187-2016 | 9/8/2016 6:11:37 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical equipment is to be installed and guarded so that adequate provisions are made for the safety of persons and property. In this installation, a home owner installed new branch circuit wiring and two feeder cables for two new sub-panels into the existing, energized main electrical panel during a renovation. At the time of the inspection, the main panel and sub-panel in the basement where complete with panel covers. The sub-panel in the garage was open and so was the dryer receptacle which was feed from the sub-panel. No devices where installed on the boxes in the renovation area and the new conductors for branch circuits and sub-panel feeders where terminated onto the breakers of an existing energized panel. The breakers for the new conductors where in the "off" position. If the breakers in the main panel where turned on, there is a potential for a shock hazard if a persons came in contact with the exposed buss in the garage sub-panel or the energized conductors at any of the new device locations. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Sub-panel_garage.png | file://x:/photopub/docs/0000000482/cbaced41-f41c-4b63-b2fa-7e8bfe28471c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e9caaf7_f5d1_4e7b_8871_19ac16cfdf80
ELIN-641217-2016 | EL-429187-2016 | 9/8/2016 6:11:37 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical equipment is to be installed and guarded so that adequate provisions are made for the safety of persons and property. In this installation, a home owner installed new branch circuit wiring and two feeder cables for two new sub-panels into the existing, energized main electrical panel during a renovation. At the time of the inspection, the main panel and sub-panel in the basement where complete with panel covers. The sub-panel in the garage was open and so was the dryer receptacle which was feed from the sub-panel. No devices where installed on the boxes in the renovation area and the new conductors for branch circuits and sub-panel feeders where terminated onto the breakers of an existing energized panel. The breakers for the new conductors where in the "off" position. If the breakers in the main panel where turned on, there is a potential for a shock hazard if a persons came in contact with the exposed buss in the garage sub-panel or the energized conductors at any of the new device locations. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | No_devices.png | file://x:/photopub/docs/0000000482/df099614-e7cb-4534-bd17-ac28fd43afe1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e9caaf7_f5d1_4e7b_8871_19ac16cfdf80
ELIN-641217-2016 | EL-429187-2016 | 9/8/2016 6:11:37 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical equipment is to be installed and guarded so that adequate provisions are made for the safety of persons and property. In this installation, a home owner installed new branch circuit wiring and two feeder cables for two new sub-panels into the existing, energized main electrical panel during a renovation. At the time of the inspection, the main panel and sub-panel in the basement where complete with panel covers. The sub-panel in the garage was open and so was the dryer receptacle which was feed from the sub-panel. No devices where installed on the boxes in the renovation area and the new conductors for branch circuits and sub-panel feeders where terminated onto the breakers of an existing energized panel. The breakers for the new conductors where in the "off" position. If the breakers in the main panel where turned on, there is a potential for a shock hazard if a persons came in contact with the exposed buss in the garage sub-panel or the energized conductors at any of the new device locations. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Conductors_on_breakers.png | file://x:/photopub/docs/0000000482/1458222a-54cc-49b3-b8bc-dc017bbc1cb6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e9caaf7_f5d1_4e7b_8871_19ac16cfdf80
ELIN-641217-2016 | EL-429187-2016 | 9/8/2016 6:11:37 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical equipment is to be installed and guarded so that adequate provisions are made for the safety of persons and property. In this installation, a home owner installed new branch circuit wiring and two feeder cables for two new sub-panels into the existing, energized main electrical panel during a renovation. At the time of the inspection, the main panel and sub-panel in the basement where complete with panel covers. The sub-panel in the garage was open and so was the dryer receptacle which was feed from the sub-panel. No devices where installed on the boxes in the renovation area and the new conductors for branch circuits and sub-panel feeders where terminated onto the breakers of an existing energized panel. The breakers for the new conductors where in the "off" position. If the breakers in the main panel where turned on, there is a potential for a shock hazard if a persons came in contact with the exposed buss in the garage sub-panel or the energized conductors at any of the new device locations. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Panel_sub-panel_basement.png | file://x:/photopub/docs/0000000482/631b7f7d-44fb-4f4c-a992-d2f58e28be7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e9caaf7_f5d1_4e7b_8871_19ac16cfdf80
ELIN-641554-2016 | EL-428475-2016 | 8/30/2016 2:05:09 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | In a restraunt under construction an electrical panel was found energized without sufficient covers installed. The panel was accessible to no electrical tradesmen. It was mounted within 1 meter of floor. The hazard is a person could touch the unprotected electrical components and be severely injured or killed. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_208V_panel.png | file://x:/photopub/docs/0000000478/762408c8-824a-44d4-a714-498dd51ce4d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4edee881_6bc2_4d4b_8e2e_c330c014fa02
ELIN-641554-2016 | EL-428475-2016 | 8/30/2016 2:05:09 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | In a restraunt under construction an electrical panel was found energized without sufficient covers installed. The panel was accessible to no electrical tradesmen. It was mounted within 1 meter of floor. The hazard is a person could touch the unprotected electrical components and be severely injured or killed. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Plug_under_panel_with_tester_installed.png | file://x:/photopub/docs/0000000478/1d5c3b47-a42a-423f-9edf-bb4df15d73ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4edee881_6bc2_4d4b_8e2e_c330c014fa02
EDOP-642330-2016 | 2044850 | 8/26/2016 2:33:23 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | If the car is stopped/stuck outside at the landing, the passages are not to open the car door and tried to exit the elevator. They will be exposed to the open hoistway and may fall resulting in a fatality, the car also move also exposing them to shearing/pinching hazards. For rider safety the manual opening of the elevator car doors when an elevator car is outside unlocking zone (landing) is restricted to 4 inches. It was found that the car door restrictor was not adjusted correctly and therefore would allow the door to open fully. There have been many reports of fatalities due to this condition. The picture is for reference only and it's not the actual site photo. | 3 | Defects that are: Not detected by maintenance program Likely to progress | Car_door_restrictor2.png | file://x:/photopub/docs/0000000480/fb1cd2ea-9184-4bfa-8e48-f834ad81f042.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6df5ad4_154b_49e3_9dd2_893bcdab6ea2
EDOP-642327-2016 | 2793817 | 8/26/2016 1:38:36 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | If the car is stopped/stuck outside of the landing, the passengers are not to open the car door and try to exit the elevator. They will be exposed to the open hoistway and may fall resulting in a fatality, The car may also move also exposing them to shearing/pinching hazards. For rider safety, the manual opening of the elevator car doors when an elevator car is outside unlocking zone (landing) is restricted to 4 inches. It was found that the car door restrictor was not adjusted correctly and therefore would allow the door to open fully. There have been many reports of fatalities due to this condition. The picture is for reference only and is not the actual site photo. | 3 | Defects that are: Not detected by maintenance program Likely to progress | Car_door_restrictor.png | file://x:/photopub/docs/0000000480/d6aaeed5-5fee-43ef-82bf-8b1a4f8cb900.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1534e22_3bb5_4cce_8930_b89a992869cb
ELIN-600724-2016 | EL-351161-2016 | 6/29/2016 7:20:19 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables are required to be a minimum distance from the finished edge of a wall surface. Possible damage to wiring is likely and damaged wiring could be a shock or fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Nmsc_location_depth.png | file://x:/photopub/docs/0000000450/0fb0911f-dbec-476d-a212-3a29a6fef8ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0d6e3b3_be7d_401d_b25e_af8e0753239f
ELIN-600724-2016 | EL-351161-2016 | 6/29/2016 7:20:19 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables are required to be a minimum distance from the finished edge of a wall surface. Possible damage to wiring is likely and damaged wiring could be a shock or fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Unit_feeder_cable_location.png | file://x:/photopub/docs/0000000450/c5ae8bdc-6f6a-49c4-94df-7354ea436933.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0d6e3b3_be7d_401d_b25e_af8e0753239f
ELIN-602153-2016 | EL-403336-2016 | 7/19/2016 11:00:44 AM | ASSESS: EL: Service Connection | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | The metal raceway between the meterbase and panel is not bonded with a bond bushing, this could create a high impedance for the fault current when a fault occurs creating a shock hazard during fault conditions. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Meterbase_raceway.png | file://x:/photopub/docs/0000000458/ba248b8f-ce60-4693-8973-8ce9ae6ff7bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3caac1b_e319_4e7e_b50d_f77693f5891e
GAIN-608619-2016 | GA-359868-2016 | 7/19/2016 4:13:01 PM | ASSESS: GA: Final | png | #asFound | GA149 | Gas log set installed with damper not permanently secured in open position | 4 | 4 | The as found hazard was a chimney damper which had not been secured open when the gas log set was installed. This is a hazard because if the damper were to be closed (deliberately or accidentally) the production of combustion from the log set would be introduced into the living space of the home. Risk of carbon monoxide poisoning. | 4 | Gas log set installed with damper not permanently secured in open position | Damper.png | file://x:/photopub/docs/0000000459/f3b5723f-63d7-4208-b96d-813f3f9e61c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__beb987fb_8f3c_45a7_acb7_2fc098cfb458
AMOP-631268-2016 | 3194476 | 8/16/2016 1:34:30 PM | ASSESS: AM OP: Periodic | png | #asFound | AM018 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Ballast missing from track where tie maintenance had been performed. Could possibly cause misaligned track if not corrected | 2 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | Kamloops_train.png | file://x:/photopub/docs/0000000471/f422bb9f-4948-4627-9117-e51d925d5e9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a5a2059_bbf4_4899_8add_b61ca0880e3d
BPVIN-632690-2016 | BPV-425382-2016 | 8/17/2016 12:19:34 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP002 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | 5 | 5 | The name plate of every boiler and pressure vessel shall be stamped in accordance with the requirements of the appropriate section of the American Society of Mechanical Engineers Code. The stamping shall include the Canadian Registration Number, identification traceable to the manufacture and design characteristics. I found no stamping or certification markings on eight unfired pressure vessels. Potential exists for an incident due to design limits being unknown. | 5 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | No_nameplate_attached_.png | file://x:/photopub/docs/0000000472/a1fa64ad-a902-4fca-85e8-0a5d1d48e985.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e2695e9_f773_48c8_b2cd_b7065a5eab9f
BPVIN-632690-2016 | BPV-425382-2016 | 8/17/2016 12:19:34 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP002 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | 5 | 5 | The name plate of every boiler and pressure vessel shall be stamped in accordance with the requirements of the appropriate section of the American Society of Mechanical Engineers Code. The stamping shall include the Canadian Registration Number, identification traceable to the manufacture and design characteristics. I found no stamping or certification markings on eight unfired pressure vessels. Potential exists for an incident due to design limits being unknown. | 5 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | Flux_tank_.png | file://x:/photopub/docs/0000000472/9875ce60-d070-4e62-904f-5881bcbc1297.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e2695e9_f773_48c8_b2cd_b7065a5eab9f
BPVIN-632690-2016 | BPV-425382-2016 | 8/17/2016 12:19:34 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP002 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | 5 | 5 | The name plate of every boiler and pressure vessel shall be stamped in accordance with the requirements of the appropriate section of the American Society of Mechanical Engineers Code. The stamping shall include the Canadian Registration Number, identification traceable to the manufacture and design characteristics. I found no stamping or certification markings on eight unfired pressure vessels. Potential exists for an incident due to design limits being unknown. | 5 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | Flux_tank_no_2.png | file://x:/photopub/docs/0000000472/a81b20b0-bcb8-4b84-8341-870320f14de9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e2695e9_f773_48c8_b2cd_b7065a5eab9f
BPVIN-632690-2016 | BPV-425382-2016 | 8/17/2016 12:19:34 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP002 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | 5 | 5 | The name plate of every boiler and pressure vessel shall be stamped in accordance with the requirements of the appropriate section of the American Society of Mechanical Engineers Code. The stamping shall include the Canadian Registration Number, identification traceable to the manufacture and design characteristics. I found no stamping or certification markings on eight unfired pressure vessels. Potential exists for an incident due to design limits being unknown. | 5 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | Flux_tank_example_3.png | file://x:/photopub/docs/0000000472/cbc94a7b-b284-4e45-9501-f2e26724ca43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e2695e9_f773_48c8_b2cd_b7065a5eab9f
BPVIN-632690-2016 | BPV-425382-2016 | 8/17/2016 12:19:34 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP002 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | 5 | 5 | The name plate of every boiler and pressure vessel shall be stamped in accordance with the requirements of the appropriate section of the American Society of Mechanical Engineers Code. The stamping shall include the Canadian Registration Number, identification traceable to the manufacture and design characteristics. I found no stamping or certification markings on eight unfired pressure vessels. Potential exists for an incident due to design limits being unknown. | 5 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | Pressure_Gage_.png | file://x:/photopub/docs/0000000472/74ab5f4e-117b-4780-b305-9eab729e03d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e2695e9_f773_48c8_b2cd_b7065a5eab9f
BPVOP-604618-2016 | 2270318 | 7/4/2016 9:32:24 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP202 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | 2 | 2 | Upon assessment of boiler it is determined that refractory at burner throat has broken/ fallen off. Refractory lining will deteriorate further resulting in overheating of metal parts if refractory is not repaired. | 2 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | Fallen_off_refractory_at_burner_throat.png | file://x:/photopub/docs/0000000451/0493f932-8e9b-414b-8933-3bc343a7287e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46e90d29_98cb_4eb9_a925_9d7bacbab180
GAHE-609780-2016 | HE-409898-2016 | 7/12/2016 11:32:45 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | Found 2 'Navien 180a' water heaters installed without sufficient air supply for proper combustion. This could result in water heaters starving for air especially under high load conditions, leading to the potential of excessive carbon monoxide in the venting system. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | No_appliance_reg.png | file://x:/photopub/docs/0000000455/58baf8c6-7d65-4d1b-b0d1-73c6010f9013.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07844565_2b26_4c18_ac14_7d5725ac939f
GAHE-609780-2016 | HE-409898-2016 | 7/12/2016 11:32:45 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | Found 2 'Navien 180a' water heaters installed without sufficient air supply for proper combustion. This could result in water heaters starving for air especially under high load conditions, leading to the potential of excessive carbon monoxide in the venting system. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Vent_clearance.png | file://x:/photopub/docs/0000000455/7c38a141-f542-4369-a7c2-be6071142bca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07844565_2b26_4c18_ac14_7d5725ac939f
GAHE-609780-2016 | HE-409898-2016 | 7/12/2016 11:32:45 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | Found 2 'Navien 180a' water heaters installed without sufficient air supply for proper combustion. This could result in water heaters starving for air especially under high load conditions, leading to the potential of excessive carbon monoxide in the venting system. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Undersized_combustion_air.png | file://x:/photopub/docs/0000000455/4c0eefe4-eb4c-42aa-b201-0e8d41a9070d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07844565_2b26_4c18_ac14_7d5725ac939f
ELIN-606275-2016 | EL-280132-2015 | 7/8/2016 5:40:20 AM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | 125A 240V Service Panel has not been effectively grounded, ground wire is terminated to a bonding lug and the bonding screw has been removed. This could result in a shock hazard or equipment damage has the breakers may not operate has designed. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Bonding_screw.png | file://x:/photopub/docs/0000000454/8896bfeb-f9e7-4690-a9d7-7f745bc55bd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71f39e3e_f610_4436_92ea_eea51aae9699
GAUP-602234-2016 | UW-403385-2016 | 6/28/2016 3:57:08 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA069 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | 3 | 3 | The undersized propane piping can lead to delayed ignition causing potential explosion. | 3 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | Wall_furnace_b-vent_not_installed_with_clearances_.png | file://x:/photopub/docs/0000000452/b92b470d-b25a-416f-98bd-c10ad6a0db6c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d001e37c_a1ce_4d3a_90a7_ba9cfc82008f
ELIN-664212-2016 | EL-436758-2016 | 9/15/2016 1:47:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Meter.png | file://x:/photopub/docs/0000000485/c3ba694f-f1b3-4605-a249-ee855993924c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__712357cd_2718_497c_b6e5_1ea56cd5acdf
ELIN-642807-2016 | EL-396183-2016 | 9/15/2016 11:18:33 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | NMD90 used as service conductor and wet location | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Service_conductors.png | file://x:/photopub/docs/0000000485/8112c6d2-e7c7-45ac-8e57-617b321f8f79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be773c70_ecc9_4d20_8cb5_d0e543b37c57
ELIN-642807-2016 | EL-396183-2016 | 9/15/2016 11:18:33 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | NMD90 used as service conductor and wet location | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Wet_location.png | file://x:/photopub/docs/0000000485/d103af08-b379-4953-944d-2360760ed260.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be773c70_ecc9_4d20_8cb5_d0e543b37c57
ELIN-664212-2016 | EL-436758-2016 | 9/15/2016 1:47:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Raceway_support.png | file://x:/photopub/docs/0000000485/b506a9f9-00c0-4cf1-80ba-82d747c07fde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__712357cd_2718_497c_b6e5_1ea56cd5acdf
ELIN-664212-2016 | EL-436758-2016 | 9/15/2016 1:47:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Temp_roofing_material.png | file://x:/photopub/docs/0000000485/ff8701ed-49c4-469d-8255-ee3b414032ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__712357cd_2718_497c_b6e5_1ea56cd5acdf
ELIN-664212-2016 | EL-436758-2016 | 9/15/2016 1:47:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Second_panel_roofing_material.png | file://x:/photopub/docs/0000000485/7d73b2c9-67ab-4e44-bcb1-111dda71c731.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__712357cd_2718_497c_b6e5_1ea56cd5acdf
BPVOP-603108-2016 | 2271384 | 6/29/2016 11:07:40 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP140 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | 1 | 1 |  | 1 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | Pressure_gauge_range_not_to_code.png | file://x:/photopub/docs/0000000451/726b1779-67d9-4024-aebe-e8250351bc07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0940ca29_442d_4a02_9fae_edcd7bffd89b
GAUP-602234-2016 | UW-403385-2016 | 6/28/2016 3:57:08 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA069 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | 3 | 3 | The undersized propane piping can lead to delayed ignition causing potential explosion. | 3 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | Under_sized_copper_tubing.png | file://x:/photopub/docs/0000000449/2f3dea4a-a06e-440d-91cc-c687712460c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d001e37c_a1ce_4d3a_90a7_ba9cfc82008f
GAUP-601602-2016 | UW-402935-2016 | 6/28/2016 10:14:54 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 3 | There were multiple appliances installed incorrectly without clearances to combustibles. If the equipment had been in operation they could over heat the combustibles and create a fire hazard. The improper copper tube and incorrect back fill material used could damage the tubing and create a leak of propane causing a fire hazard. | 2 | Non compliant Type B Vent Clearance | Incorrect_copper_tube_burried.png | file://x:/photopub/docs/0000000449/12dc81e5-71d5-4fec-9288-ccc92a9b9fcf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f1cc883_aa69_495a_800c_9fde038d4964
GAUP-601602-2016 | UW-402935-2016 | 6/28/2016 10:14:54 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 3 | There were multiple appliances installed incorrectly without clearances to combustibles. If the equipment had been in operation they could over heat the combustibles and create a fire hazard. The improper copper tube and incorrect back fill material used could damage the tubing and create a leak of propane causing a fire hazard. | 2 | Non compliant Type B Vent Clearance | Gas_connector_passing_through_a_wall.png | file://x:/photopub/docs/0000000449/42cd2914-71b4-471c-80af-f4ed41fdfe0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f1cc883_aa69_495a_800c_9fde038d4964
GAUP-601602-2016 | UW-402935-2016 | 6/28/2016 10:14:54 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 3 | There were multiple appliances installed incorrectly without clearances to combustibles. If the equipment had been in operation they could over heat the combustibles and create a fire hazard. The improper copper tube and incorrect back fill material used could damage the tubing and create a leak of propane causing a fire hazard. | 2 | Non compliant Type B Vent Clearance | Incorrectly_installed_wall_furnace.png | file://x:/photopub/docs/0000000449/a3f4089d-0fbd-46b3-a215-d48304c0437c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f1cc883_aa69_495a_800c_9fde038d4964
GAUP-601602-2016 | UW-402935-2016 | 6/28/2016 10:14:54 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 3 | There were multiple appliances installed incorrectly without clearances to combustibles. If the equipment had been in operation they could over heat the combustibles and create a fire hazard. The improper copper tube and incorrect back fill material used could damage the tubing and create a leak of propane causing a fire hazard. | 2 | Non compliant Type B Vent Clearance | Copper_tube_not_sleeved.png | file://x:/photopub/docs/0000000449/150bf342-9a75-407d-87e4-5b5744c7baa3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f1cc883_aa69_495a_800c_9fde038d4964
GAUP-601602-2016 | UW-402935-2016 | 6/28/2016 10:14:54 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 3 | There were multiple appliances installed incorrectly without clearances to combustibles. If the equipment had been in operation they could over heat the combustibles and create a fire hazard. The improper copper tube and incorrect back fill material used could damage the tubing and create a leak of propane causing a fire hazard. | 2 | Non compliant Type B Vent Clearance | B-vent_incorrectly_installed.png | file://x:/photopub/docs/0000000449/49fe519d-391c-41c2-b364-debe78e2857b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f1cc883_aa69_495a_800c_9fde038d4964
GAUP-601602-2016 | UW-402935-2016 | 6/28/2016 10:14:54 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 3 | There were multiple appliances installed incorrectly without clearances to combustibles. If the equipment had been in operation they could over heat the combustibles and create a fire hazard. The improper copper tube and incorrect back fill material used could damage the tubing and create a leak of propane causing a fire hazard. | 2 | Non compliant Type B Vent Clearance | Incorrectly_installed_fireplace.png | file://x:/photopub/docs/0000000449/fbfc9a8f-ab20-47e8-a120-249f9ac85823.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f1cc883_aa69_495a_800c_9fde038d4964
GAUP-602234-2016 | UW-403385-2016 | 6/28/2016 3:57:08 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA069 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | 3 | 3 | The undersized propane piping can lead to delayed ignition causing potential explosion. | 3 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | Under_sized_regulator.png | file://x:/photopub/docs/0000000449/09733a36-151c-4a25-87d6-f6752461a5f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d001e37c_a1ce_4d3a_90a7_ba9cfc82008f
GAUP-601602-2016 | UW-402935-2016 | 6/28/2016 10:14:54 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 3 | There were multiple appliances installed incorrectly without clearances to combustibles. If the equipment had been in operation they could over heat the combustibles and create a fire hazard. The improper copper tube and incorrect back fill material used could damage the tubing and create a leak of propane causing a fire hazard. | 2 | Non compliant Type B Vent Clearance | Piping_open_to_water_not_painted.png | file://x:/photopub/docs/0000000449/f5fd0150-bf9f-4fed-8f33-33497e9b96d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f1cc883_aa69_495a_800c_9fde038d4964
EDMA-661811-2016 | ED-408178-2016 | 8/20/2016 7:54:31 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED025 | Accessible location Preventative measure show sign of minor wear and/or damage Contact with Object/human possible Contact could result in property damage | 3 | 3 | The ventilation holes located on the car cab panel walls are meant to give proper ventilation to the elevator occupants. During an acceptance inspection it was found the holes had a straight through passage to the hoistway. Normally the ventilation holes have a baffle to protect the elevator occupants from the hoistway mechanical and moving components in the hoistway. The straight through passage of the ventilation holes poses a considerable risk for items or people's fingers that may be accidentally poked through the the holes and then coming in contact with things in the hoistway resulting in injury. It was found the elevator contractor failed to install the baffles. This 11 stop traction elevator modernization is located in an existing residential building. | 3 | Accessible location Preventative measure show sign of minor wear and/or damage Contact with Object/human possible Contact could result in property damage | Car_cab_ventilation_holes.png | file://x:/photopub/docs/0000000483/0fa55e10-1458-4ce6-9406-5bfba3558504.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c25182df_5193_4406_a12a_c286c8ce1f71
GAIN-608240-2016 | GA-386470-2016 | 7/11/2016 9:13:37 AM | ASSESS: GA: Rough-In | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | A live gas line was found inside of a building without a cap or plug. The opening or failure of the valve would allow gas to enter the space potentially causing an explosion or fire. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Open_gas_line.png | file://x:/photopub/docs/0000000454/dc952680-5828-4e1d-b303-c4a8c00527b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fecb628_cb9f_4302_850d_d742652a90e0
ELHE-640672-2016 | HE-430012-2016 | 8/29/2016 3:01:32 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL083 | Continuity Separately derived system, communication or similar system has not been properly grounded | 4 | 4 | The trailer type generator was found connected to the construction trailer with armoured cable. The conductor of this cable were accessible to anyone on the ground. The generator was not electrically connected to ground. | 4 | Continuity Separately derived system, communication or similar system has not been properly grounded | Energized_conductors.png | file://x:/photopub/docs/0000000477/c6c87a52-6671-4549-8b7a-22f4084a292f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62520699_9d87_4372_b2c9_9006fb25244c
ELHE-640672-2016 | HE-430012-2016 | 8/29/2016 3:01:32 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL083 | Continuity Separately derived system, communication or similar system has not been properly grounded | 4 | 4 | The trailer type generator was found connected to the construction trailer with armoured cable. The conductor of this cable were accessible to anyone on the ground. The generator was not electrically connected to ground. | 4 | Continuity Separately derived system, communication or similar system has not been properly grounded | Ground_point.png | file://x:/photopub/docs/0000000477/1ac7e7a9-300a-42e2-af65-37afa09d2edd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62520699_9d87_4372_b2c9_9006fb25244c
ELHE-640672-2016 | HE-430012-2016 | 8/29/2016 3:01:32 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL083 | Continuity Separately derived system, communication or similar system has not been properly grounded | 4 | 4 | The trailer type generator was found connected to the construction trailer with armoured cable. The conductor of this cable were accessible to anyone on the ground. The generator was not electrically connected to ground. | 4 | Continuity Separately derived system, communication or similar system has not been properly grounded | Generator_wiring.png | file://x:/photopub/docs/0000000477/0729b701-bb71-48c5-ad6a-7e159cf6bf3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62520699_9d87_4372_b2c9_9006fb25244c
ELIN-612865-2016 | EL-406873-2016 | 7/18/2016 10:58:42 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | NMSC cable installed in space between roof rafter and roof sheathing (3/4") is subject to nailing or screw damage from future roof shingling or or metal roofing installation NMSC in concealed locations which is subject to nail or screw damage may present a shock or fire hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Ceiling_space_nailing_protection_not_provided.png | file://x:/photopub/docs/0000000458/50397ea6-a2b4-4078-a1ff-7e93c3aeb86d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb731128_c6a6_4ebe_ac3d_11d900618666
ELHE-611115-2016 | HE-411107-2016 | 7/13/2016 12:59:13 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Emergency equipment such as fire alarm systems must be tested and recertified annually. In this installation a temporary panel was installed in 2015 with the understanding that more work would be done on the system before its certification period expired. After a suite fire in an adjacent building in the same complex required an electrical inspection the safety officer observed that the certification had expired. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 10_zone_panel.png | file://x:/photopub/docs/0000000455/c96b33be-ca01-4963-a7e8-e778b02732d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6396baca_a841_4144_8f06_35f737829feb
ELHE-611115-2016 | HE-411107-2016 | 7/13/2016 12:59:13 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Emergency equipment such as fire alarm systems must be tested and recertified annually. In this installation a temporary panel was installed in 2015 with the understanding that more work would be done on the system before its certification period expired. After a suite fire in an adjacent building in the same complex required an electrical inspection the safety officer observed that the certification had expired. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Certified_May_2015.png | file://x:/photopub/docs/0000000455/bdba4ee1-ba25-4eab-b265-3636e38c384d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6396baca_a841_4144_8f06_35f737829feb
ELOP-226532-2014 | 3945260 | 7/21/2016 11:25:43 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL222 | All Classes, All Zones Area is classified: equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated. | 4 | 4 | Natural gas and propane valves which are capable of venting or releasing gas may not be installed within 1 m and 3 m respectively of electrical devices capable of producing an arc or spark. In this resort installation propane tanks and valves had been positioned too close to exterior receptacles. | 4 | All Classes, All Zones Area is classified: equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated. | South_cabin.png | file://x:/photopub/docs/0000000460/11b35b4c-ecc9-41d4-93f0-fd8f99207344.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e4291cad_3846_4047_98e2_d0dbc3482de5
ELOP-226532-2014 | 3945260 | 7/21/2016 11:25:43 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL222 | All Classes, All Zones Area is classified: equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated. | 4 | 4 | Natural gas and propane valves which are capable of venting or releasing gas may not be installed within 1 m and 3 m respectively of electrical devices capable of producing an arc or spark. In this resort installation propane tanks and valves had been positioned too close to exterior receptacles. | 4 | All Classes, All Zones Area is classified: equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated. | North_cabin.png | file://x:/photopub/docs/0000000460/a5610db0-90c6-4cda-8fd2-6901fa6e04cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e4291cad_3846_4047_98e2_d0dbc3482de5
ELOP-460255-2015 | 6180 | 8/31/2016 11:17:22 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | A Type 1 enclosure 200A 120/240V panel has been placed in a wood enclosure which does not provided weather protection, this could result in equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_Distribution.png | file://x:/photopub/docs/0000000478/35563270-ea50-4fe0-b68b-1fdade75d83e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bfc0a10_0bdb_4797_91d2_868ff55205b6
ELIN-604269-2016 | EL-351778-2016 | 7/5/2016 2:04:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Distribution panels are not in weatherproof enclosures and lockable. 120/240 Volt, 100 amps. This can cause equipment damage from the environment due to building not completely closed up. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Distribution_panels_are_not_weatherproof_and_lockable_.png | file://x:/photopub/docs/0000000452/28a63269-0db9-4d15-87be-fcd3a0862a52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1892563f_9d87_4e35_9d5c_204e93c4f855
GAIN-611757-2016 | GA-411051-2016 | 7/20/2016 11:07:10 AM | ASSESS: GA: Final | png | #asFound | GA080 | Line pressure regulator without required overpressure protection in place | 3 | 3 | 5psi regulator with vent limiter requires OPD protection. Without OPD, excessive pressure could cause failure to gas control valve resulting in over firing of appliance and possible fire to structure. | 3 | Line pressure regulator without required overpressure protection in place | 5psi_regulator1.png | file://x:/photopub/docs/0000000459/29ced4a0-4459-46b0-915a-60149531da43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a0d0f9b_db6d_4770_97ce_a38b1bbb9c73
GAIN-622413-2016 | GA-409999-2016 | 7/19/2016 8:18:39 AM | ASSESS: GA: Rough-In | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Without using certified gas risers, unprotected poly gas lines are subject to damage, which could cause a leak leading to fire and or injury | 3 | Non-compliant material/fittings installed | Poly_transition.png | file://x:/photopub/docs/0000000465/1c9fc7b6-5ed2-4d09-b716-554f9d2521e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2a9de79_665e_4860_8baa_fbed342caced
ELIN-612865-2016 | EL-406873-2016 | 7/18/2016 10:58:42 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | NMSC cable installed in space between roof rafter and roof sheathing (3/4") is subject to nailing or screw damage from future roof shingling or or metal roofing installation NMSC in concealed locations which is subject to nail or screw damage may present a shock or fire hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Nailing_protection_not_provided.png | file://x:/photopub/docs/0000000458/3c4ad440-b396-4d7f-a3ab-a6277d5618ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb731128_c6a6_4ebe_ac3d_11d900618666
ELIN-612865-2016 | EL-406873-2016 | 7/18/2016 10:58:42 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | NMSC cable installed in space between roof rafter and roof sheathing (3/4") is subject to nailing or screw damage from future roof shingling or or metal roofing installation NMSC in concealed locations which is subject to nail or screw damage may present a shock or fire hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Nailing_protection_not_provided2.png | file://x:/photopub/docs/0000000458/6fe4fc85-49f2-437c-b541-b84daaae244a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb731128_c6a6_4ebe_ac3d_11d900618666
ELIN-661685-2016 | EL-436494-2016 | 9/13/2016 12:22:29 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound |  |  |  |  | Shock and arc flash hazard from possible damage of service cable at ground level. |  |  | Cable1.png | file://x:/photopub/docs/0000000484/65f230ce-4b66-4c5f-a0a6-c27aa8ecf0dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9663f13_838a_42bc_bdc8_7a8d95035476
ELIN-661685-2016 | EL-436494-2016 | 9/13/2016 12:22:29 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound |  |  |  |  | Shock and arc flash hazard from possible damage of service cable at ground level. |  |  | Box1.png | file://x:/photopub/docs/0000000484/38095d3b-532d-437b-b267-b0656aa69df4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9663f13_838a_42bc_bdc8_7a8d95035476
ELIN-661685-2016 | EL-436494-2016 | 9/13/2016 12:22:29 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound |  |  |  |  | Shock and arc flash hazard from possible damage of service cable at ground level. |  |  | Cable3.png | file://x:/photopub/docs/0000000484/29a533dd-a178-4b1c-b27a-8e8e12d4b3ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9663f13_838a_42bc_bdc8_7a8d95035476
ELIN-661685-2016 | EL-436494-2016 | 9/13/2016 12:22:29 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound |  |  |  |  | Shock and arc flash hazard from possible damage of service cable at ground level. |  |  | Cable4.png | file://x:/photopub/docs/0000000484/055d7d79-286a-42a2-8f26-db001c939468.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9663f13_838a_42bc_bdc8_7a8d95035476
GAIN-560224-2016 | GA-333386-2016 | 7/13/2016 5:32:05 PM | ASSESS: GA: Final | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | 1) All gas burning appliances are required to be vented to the outdoors. 2) Found 2 vertical cooking broilers in use in a sandwich shop without a exhaust vent canopy. 3) Air born grease vaporizer could ignite causing a fire. Burners could become dirt plugged or defective and produce toxic levels of carbon monoxide within an occupied space. | 3 | Uncertified appliance connected to gas supply but not in service | Uncertified_gas_appliance.png | file://x:/photopub/docs/0000000456/39f05174-a34b-4f72-8b1c-c8c645d5d402.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5050684b_bf4d_41e8_aa41_007b95db1575
GAIN-560224-2016 | GA-333386-2016 | 7/13/2016 5:32:05 PM | ASSESS: GA: Final | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | 1) All gas burning appliances are required to be vented to the outdoors. 2) Found 2 vertical cooking broilers in use in a sandwich shop without a exhaust vent canopy. 3) Air born grease vaporizer could ignite causing a fire. Burners could become dirt plugged or defective and produce toxic levels of carbon monoxide within an occupied space. | 3 | Uncertified appliance connected to gas supply but not in service | Unvented_appliance_.png | file://x:/photopub/docs/0000000456/b573f350-c23a-4470-87bc-f189f38bc87e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5050684b_bf4d_41e8_aa41_007b95db1575
GAIN-580710-2016 | GA-389762-2016 | 7/13/2016 11:39:25 AM | ASSESS: GA: Final | png | #asFound | GA003 | Provision for expansion Incorrect swing joint | 2 | 2 |  | 2 | Provision for expansion Incorrect swing joint | No_swing_joint_under_ground_gas_line_.png | file://x:/photopub/docs/0000000456/adec64ee-3a23-4107-8882-117fc319df4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29f94cd9_be21_4db6_b70e_59ff6d5aabba
EDIN-664100-2016 | ED-310382-2015 | 9/13/2016 7:45:27 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | The emergency 2-way emergency communication in the elevator is a means of communication to a 24 hours/day monitored station. During an acceptance inspection it was found the 2-way emergency communication was not installed. Without a properly functioning 2-way emergency communication in the elevator it may be difficult to get help in case of an elevator entrapment. This may result in a serious situation if panic sets in or if a person had a medical emergency and was trapped in the elevator. This machine room less (MRL) traction elevator is located in a newly constructed residential building It was found the general contractor failed to have the 2-way emergency system installed. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | Car_station_autodialler.png | file://x:/photopub/docs/0000000485/996f1304-851b-4c2f-810d-c126ffe04a5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59b68801_b5c2_4ec3_9052_890f9c623dfd
EDIN-664133-2016 | ED-310387-2015 | 9/13/2016 11:23:30 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | The emergency 2-way emergency communication in the elevator is a means of communication to a 24 hours/day monitored station. During an acceptance inspection it was found the 2-way emergency communication was not installed. Without a properly functioning 2-way emergency communication in the elevator it may be difficult to get help in case of an elevator entrapment. This may result in a serious situation if panic sets in or if a person had a medical emergency and was trapped in the elevator. This machine room less (MRL) traction elevator is located in a newly constructed residential building It was found the general contractor failed to have the 2-way emergency system installed. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | Car_stn_autodialler.png | file://x:/photopub/docs/0000000485/32c0faac-5397-4653-a4f0-41a4a1ae6043.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c20277c6_0e91_4981_9a6b_5e3e5a1b46eb
ELIN-633210-2016 | EL-425702-2016 | 8/18/2016 11:57:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL192 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, within area of energized parts. | 4 | 4 | The existing 100 amp 120/240 volt panelboard has no cover installed and no qualified worker on site. This is a shock hazard | 4 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, within area of energized parts. | Open_energized_panelboard.png | file://x:/photopub/docs/0000000472/f33394dd-332c-492b-aa1a-9f40a90c5253.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f949a015_8649_456c_b639_cea57e4ae34a
GAIN-629799-2016 | GA-420599-2016 | 8/19/2016 2:06:46 PM | ASSESS: GA: Final | png | #asFound | GA080 | Line pressure regulator without required overpressure protection in place | 3 | 3 | Found pressure regulator installed without limiting orifice in the regulator vent. In the case of regulator failure the gas venting into the space would not be restricted to 2.5cf/hr. Causing a potential for an explosion/fire. | 3 | Line pressure regulator without required overpressure protection in place | Missing_limiter.png | file://x:/photopub/docs/0000000473/c3547c29-f2e3-460a-acd2-646145f366d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20adb37c_293f_4950_854f_489b045d7ef7
ELIN-640011-2016 | EL-427567-2016 | 9/8/2016 2:41:26 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Original house demolished, contractor kept original service in unsafe condition for use as construction service. No operating permit. Live service conductors at heights contactable by pedestrians, vehicles and equipment. SSA 18(4) disconnect ordered. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Stairs.png | file://x:/photopub/docs/0000000482/335cf325-94e6-4722-b575-53a8edafe2a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__563bb9f1_91a1_4995_b796_09b07f20e859
ELIN-640011-2016 | EL-427567-2016 | 9/8/2016 2:41:26 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Original house demolished, contractor kept original service in unsafe condition for use as construction service. No operating permit. Live service conductors at heights contactable by pedestrians, vehicles and equipment. SSA 18(4) disconnect ordered. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Attic.png | file://x:/photopub/docs/0000000482/75d56753-aa3a-48b0-b51f-28c9c0ac3832.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__563bb9f1_91a1_4995_b796_09b07f20e859
ELIN-640011-2016 | EL-427567-2016 | 9/8/2016 2:41:26 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Original house demolished, contractor kept original service in unsafe condition for use as construction service. No operating permit. Live service conductors at heights contactable by pedestrians, vehicles and equipment. SSA 18(4) disconnect ordered. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 2x4_support.png | file://x:/photopub/docs/0000000482/9a8b1a4e-2bbf-4de9-aafe-9cf2cdeec1f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__563bb9f1_91a1_4995_b796_09b07f20e859
ELIN-640011-2016 | EL-427567-2016 | 9/8/2016 2:41:26 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Original house demolished, contractor kept original service in unsafe condition for use as construction service. No operating permit. Live service conductors at heights contactable by pedestrians, vehicles and equipment. SSA 18(4) disconnect ordered. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Staples.png | file://x:/photopub/docs/0000000482/bb4519c0-0f9d-4aea-876e-88da74954a4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__563bb9f1_91a1_4995_b796_09b07f20e859
ELIN-640011-2016 | EL-427567-2016 | 9/8/2016 2:41:26 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Original house demolished, contractor kept original service in unsafe condition for use as construction service. No operating permit. Live service conductors at heights contactable by pedestrians, vehicles and equipment. SSA 18(4) disconnect ordered. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Teck.png | file://x:/photopub/docs/0000000482/ba3e039a-6a8c-49d2-bd9e-e145a592a373.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__563bb9f1_91a1_4995_b796_09b07f20e859
ELIN-640011-2016 | EL-427567-2016 | 9/8/2016 2:41:26 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Original house demolished, contractor kept original service in unsafe condition for use as construction service. No operating permit. Live service conductors at heights contactable by pedestrians, vehicles and equipment. SSA 18(4) disconnect ordered. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Broken_mast.png | file://x:/photopub/docs/0000000482/a35fd4b4-d4ca-4b22-ac84-2df85b6f9d1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__563bb9f1_91a1_4995_b796_09b07f20e859
ELIN-632871-2016 | EL-392920-2016 | 8/22/2016 1:18:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | A new commercial service panel rated 200 amps 240 volt one phase has been installed. The service was authorized for connection accessible to the general public. Damage to electrical equipment, persons or property can occur if access is not restricted to unauthorized persons. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_not_lockable.png | file://x:/photopub/docs/0000000474/26c238f3-5111-46a2-bb98-233d9de2fcf5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1eb9a289_26e7_465e_8444_6cac08d52de3
ELIN-630598-2016 | EL-423988-2016 | 8/22/2016 2:19:29 PM | ASSESS: EL: Service Connection | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | 15 amp construction outlets fed with 15 amp rated wire have been connected to 20 amp overcurrent protection. 15 amp receptacles are not tested for safety at ampacities exceeding the rating of the receptacle and noncompliance can result in equipment damage or injury to persons | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 15_amp_receptacles_on_20_amp_breakers_all_4_construction_circuits.png | file://x:/photopub/docs/0000000474/dfc15eb6-a667-4a49-8a15-193115c24531.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c27bba1e_24fc_47a9_8cb9_938aac8286f1
ELOP-614331-2016 | EL-259182-2015 | 7/19/2016 3:52:33 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Open air splice of two cables, splices, joints and terminations of cables are required to be made in approved junction boxes. If wire nuts were to accidentally fall off, energized conductor ends would be present. This potential situation would provide a risk of shock and fire to persons and property | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Splice_not_made_in_approved_junction_box.png | file://x:/photopub/docs/0000000458/bff859a6-1c3e-4740-9a21-f12893711b81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95dff2cc_d0c8_4042_a15f_5607ee9784f8
BPVOP-583670-2016 | 2299006 | 6/24/2016 3:27:42 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP130 | 3.1.1 Safeties will not function - AMMONIA-Risk Registry BPV-19 No evidence that manufacturer recommended or code required tests or checks have been completed. | 3 | 3 | During the inspection of an ammonia refrigeration system of 150 kw, it was found no records of testing of all safeties within the last year and 2 PRD's were overdue as per CSA B 52. | 3 | 3.1.1 Safeties will not function - AMMONIA-Risk Registry BPV-19 No evidence that manufacturer recommended or code required tests or checks have been completed. | Level_switch.png | file://x:/photopub/docs/0000000485/8c83d8fb-02bd-4e50-9772-551d34b5f474.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bb40852_4fa7_4620_bac1_14a1584cd156
BPVOP-604618-2016 | 2270318 | 7/4/2016 9:32:24 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP202 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | 2 | 2 | Upon assessment of boiler it is determined that refractory at burner throat has broken/ fallen off. Refractory lining will deteriorate further resulting in overheating of metal parts if refractory is not repaired. | 2 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | Fallen_off_refractory_at_burner_throat.png | file://x:/photopub/docs/0000000451/ebd66d40-2bb8-4352-9574-4f6100fa6060.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46e90d29_98cb_4eb9_a925_9d7bacbab180
BPVOP-603108-2016 | 2271384 | 6/29/2016 11:07:40 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP140 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | 1 | 1 |  | 1 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | Pressure_gauge_range_not_to_code.png | file://x:/photopub/docs/0000000451/9242144c-22fa-46cf-a830-99fbd0ed4067.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0940ca29_442d_4a02_9fae_edcd7bffd89b
ELIN-601868-2016 | EL-403180-2016 | 7/11/2016 10:07:36 AM | ASSESS: EL: Final | png | #asFound | EL100 | Conductors, Mis-use of flexible cords. | 4 | 4 | A mobile home altered from original 100 amp service to 50 amps 240 volts has been cord connected with flexible cord directly into the panel board. Flexible cord is not to be used as a substitute for fixed wiring and can deteriorate leading to property damage or injury to persons | 4 | Conductors, Mis-use of flexible cords. | Flexible_cord_directly_into_panel.png | file://x:/photopub/docs/0000000454/8b859c0d-e531-4bc8-996c-25ad37663a37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__115a269a_51aa_4ee4_b8ce_dfd555bb817f
ELIN-607387-2016 | EL-356780-2016 | 7/11/2016 12:37:28 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | A panelboard has had a barrier removed which creates a separate box within the equipment. The 200 amp 240 volt feeders enter this portion of the panel. The panel is not specifically tested or approved for this use and could fail unpredictably causing damage to property or injury to persons | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_section_of_panel_altered_and_used_as_junction_box_or_raceway.png | file://x:/photopub/docs/0000000454/37ad5678-f849-47c2-848d-661880430430.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0069139b_0c67_486c_926f_1ed58235e3ec
ELIN-640955-2016 | EL-414491-2016 | 8/30/2016 2:54:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Corroded temporary service no longer safe for use | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel.png | file://x:/photopub/docs/0000000477/9889a8f5-ddf6-4892-b549-64088d14197a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae43c779_8fc2_4f58_adb6_83e3f8797e4a
ELIN-640955-2016 | EL-414491-2016 | 8/30/2016 2:54:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Corroded temporary service no longer safe for use | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Tcs.png | file://x:/photopub/docs/0000000477/71ea75ed-48b6-4f58-8265-0d9403fdcbf8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae43c779_8fc2_4f58_adb6_83e3f8797e4a
ELIN-640955-2016 | EL-414491-2016 | 8/30/2016 2:54:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Corroded temporary service no longer safe for use | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Meterbase.png | file://x:/photopub/docs/0000000477/60b39edb-7ef8-4e86-8fa0-e769601e85af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae43c779_8fc2_4f58_adb6_83e3f8797e4a
ELIN-640955-2016 | EL-414491-2016 | 8/30/2016 2:54:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Corroded temporary service no longer safe for use | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | GFCIs.png | file://x:/photopub/docs/0000000477/1c4b1fc7-697c-4401-a609-4851b005c211.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae43c779_8fc2_4f58_adb6_83e3f8797e4a
ELIN-641346-2016 | EL-430437-2016 | 9/1/2016 10:11:00 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Installation of unapproved service cable type makes the installation susceptible to mechanical damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | UG_ductwork_1.png | file://x:/photopub/docs/0000000479/afe211d0-526a-4db5-bb98-94b2bf5b9134.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__734dfeda_9c75_4080_9ae6_a52259c10cbb
ELIN-641346-2016 | EL-430437-2016 | 9/1/2016 10:11:00 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Installation of unapproved service cable type makes the installation susceptible to mechanical damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Unapproved_service_cable.png | file://x:/photopub/docs/0000000479/fa12d04a-c5bd-46da-bc45-29006bebf4c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__734dfeda_9c75_4080_9ae6_a52259c10cbb
ELIN-641346-2016 | EL-430437-2016 | 9/1/2016 10:11:00 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Installation of unapproved service cable type makes the installation susceptible to mechanical damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Unapproved_service_cable_1.png | file://x:/photopub/docs/0000000479/1693863d-9142-4dd8-ad4f-05cc2de9ec43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__734dfeda_9c75_4080_9ae6_a52259c10cbb
ELIN-641346-2016 | EL-430437-2016 | 9/1/2016 10:11:00 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Installation of unapproved service cable type makes the installation susceptible to mechanical damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Ground_cable_terminated_in_unapproved_location.png | file://x:/photopub/docs/0000000479/955c7c6d-bb3a-4086-b606-ee2ab3b4d42a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__734dfeda_9c75_4080_9ae6_a52259c10cbb
ELIN-644011-2016 | EL-425669-2016 | 9/6/2016 9:36:32 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unfused service conductors pose a fire hazard if damaged | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Unfused_service_conductors_2.png | file://x:/photopub/docs/0000000480/75ecf07f-5edc-484a-8c69-020444853acd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5a8b3d3_a229_4d52_9bc5_9e7aee977f0e
ELIN-644011-2016 | EL-425669-2016 | 9/6/2016 9:36:32 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unfused service conductors pose a fire hazard if damaged | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Unfused_conductors.png | file://x:/photopub/docs/0000000480/9e0fbe45-0c57-4da0-a70d-b29c2a85d87f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5a8b3d3_a229_4d52_9bc5_9e7aee977f0e
ELIN-644031-2016 | EL-409973-2016 | 9/6/2016 2:57:14 PM | ASSESS: EL: Final | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 3 | Devices installed in a fire alarm system must be supervised and verified as to their operational ability | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Staff_room.png | file://x:/photopub/docs/0000000480/8e5eb609-2fae-4258-b782-28cd0719d552.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c96175ed_4ed9_4d17_9e4e_6a8e065f9596
ELIN-644031-2016 | EL-409973-2016 | 9/6/2016 2:57:14 PM | ASSESS: EL: Final | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 3 | Devices installed in a fire alarm system must be supervised and verified as to their operational ability | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | New_Kindergarten_classroom.png | file://x:/photopub/docs/0000000480/34606ba5-1b89-4cc2-a722-b60f11ff580f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c96175ed_4ed9_4d17_9e4e_6a8e065f9596
BPVOP-640593-2016 | 2285521 | 9/2/2016 9:11:11 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Relief_location.png | file://x:/photopub/docs/0000000479/43f00dfc-550d-437a-ab58-7cb3915dcc37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8fd6886f_4780_4db6_970e_f3e80df657a8
BPVOP-640233-2016 | 4285913 | 8/29/2016 2:04:10 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Relief_line_location.png | file://x:/photopub/docs/0000000479/0344f608-f0b7-4f4c-9712-8c652b9c33e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7c63b45_fa58_43c8_82ea_58d6d6764e2c
GAIN-587560-2016 | GA-391318-2016 | 7/4/2016 4:21:33 PM | ASSESS: GA: Final | png | #asFound | GA069 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | 3 | 3 | Under sized gas line could result in improper operation of the appliance due to low fuel pressure. Possible heat exchanger damage and or Carbon monoxide risk. | 3 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | Gas_line.png | file://x:/photopub/docs/0000000452/65527b1a-9d94-4bc5-b177-ae0d0764f6df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__873a55a6_4c65_4162_b580_fb5974d00157
ELIN-622843-2016 | EL-415055-2016 | 8/9/2016 1:28:27 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The use of the mud ring creates openings >6.75mm allowing a conductive rod to enter the energized enclosure, this is a shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Openings_greater_than_6_75mm.png | file://x:/photopub/docs/0000000468/dcb6d0f7-fa07-4fd5-ad92-d4c769146d47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf9647a3_3ab1_4492_a713_bf661473aec5
ELIN-611754-2016 | UW-399954-2016 | 7/14/2016 11:13:14 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 | The electrical distribution equipment is not accessible due to the room being used as a storage room. It is not possible to turn off the main power off to the sub feeds if it was required. | 1 | General Working space or dedicated space is being used for storage | Pdc_storage.png | file://x:/photopub/docs/0000000456/c13fba3d-2b60-4fd7-8056-48017e00b49f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9844d1c8_6aba_4cd2_8f5a_b01f8e37f0c8
ELIN-611336-2016 | EL-261376-2015 | 7/14/2016 10:45:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | The electrical code requires that within dwelling units at least one receptacle be installed on each kitchen peninsular counter over 600 mm in length and 300mm in width. This requirement is so that appliances used on the peninsula can be plugged into an outlet without using an extension cord. Improper use of extension cords can lead to damage of the cords and improperly sized/rated cords could be overloaded when appliances are plugged into them. In this installation of a kitchen renovation for a house no receptacle was installed for the kitchen peninsula counter space. Left uncorrected this is a potential shock or fire hazard. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Kitchen_Cabinets.png | file://x:/photopub/docs/0000000456/db60579a-8cd9-4694-a947-5a6d2f1d8e83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__569a4833_bb49_455d_b153_8071553ac982
ELIN-611336-2016 | EL-261376-2015 | 7/14/2016 10:45:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | The electrical code requires that within dwelling units at least one receptacle be installed on each kitchen peninsular counter over 600 mm in length and 300mm in width. This requirement is so that appliances used on the peninsula can be plugged into an outlet without using an extension cord. Improper use of extension cords can lead to damage of the cords and improperly sized/rated cords could be overloaded when appliances are plugged into them. In this installation of a kitchen renovation for a house no receptacle was installed for the kitchen peninsula counter space. Left uncorrected this is a potential shock or fire hazard. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Kitchen_counter_space.png | file://x:/photopub/docs/0000000456/77116348-9b40-4346-8596-210cdface455.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__569a4833_bb49_455d_b153_8071553ac982
ELIN-611336-2016 | EL-261376-2015 | 7/14/2016 10:45:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | The electrical code requires that within dwelling units at least one receptacle be installed on each kitchen peninsular counter over 600 mm in length and 300mm in width. This requirement is so that appliances used on the peninsula can be plugged into an outlet without using an extension cord. Improper use of extension cords can lead to damage of the cords and improperly sized/rated cords could be overloaded when appliances are plugged into them. In this installation of a kitchen renovation for a house no receptacle was installed for the kitchen peninsula counter space. Left uncorrected this is a potential shock or fire hazard. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Front_of_house.png | file://x:/photopub/docs/0000000456/7c797412-dc1f-44dc-96a8-95ece2be02aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__569a4833_bb49_455d_b153_8071553ac982
ELIN-625518-2016 | EL-420210-2016 | 8/10/2016 7:57:29 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | An outdoor receptacle has been installed connected to an interior lighting circuit operating at 120 V and 15 amps. Outdoor receptacles at grade must be robust enough to handle the types of loads imposed upon them. Equipment damage or inconvenience to operator can occur when the circuit is inadequate for the purpose | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Outdoor_receptacle_at_grade_on_lighting_circuit.png | file://x:/photopub/docs/0000000469/8cdf7838-c7c6-4940-9da9-500bbd359245.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bee17238_cdaf_46aa_8daf_aeb428565192
ELIN-644031-2016 | EL-409973-2016 | 9/6/2016 2:57:14 PM | ASSESS: EL: Final | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 3 | Devices installed in a fire alarm system must be supervised and verified as to their operational ability | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | New_panel_for_staff_room_iring.png | file://x:/photopub/docs/0000000480/83e59396-e702-4254-bb98-baa6f76e997a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c96175ed_4ed9_4d17_9e4e_6a8e065f9596
ELIN-617026-2016 | EL-407880-2016 | 7/25/2016 2:00:34 PM | ASSESS: EL: Final | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | A residential service upgrade to 200 amps 240 volt was performed. Existing grounding type receptacles are installed. These receptacles are not grounded or ground fault protected. Electrical equipment requiring a bonding conductor can be plugged into these receptacles and be unsafe for persons operating the equipment or cause damage to property upon failure. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Outlets_many_locations_not_bonded.png | file://x:/photopub/docs/0000000461/f11ae4be-f48a-4be9-841b-b817b9144385.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2932fe6f_5b6b_4285_a70b_df4f19be4072
BPVIN-628416-2016 | BPV-422676-2016 | 8/10/2016 10:49:54 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | Relieving capacity of a safety valve on an air receiver must match or exceed capacity of all attached compressors. I found the relieving capacity of the safety valve was less than that what's required. The air receiver may rupture due to restricted capacity of the safety valve | 0 | No Created Hazard Identified | Air_receiver.png | file://x:/photopub/docs/0000000468/574eabeb-4ab7-4af0-b66d-6109dbddb046.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83ee7245_f3cc_4896_a98f_70a5c8844dbc
BPVIN-628416-2016 | BPV-422676-2016 | 8/10/2016 10:49:54 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | Relieving capacity of a safety valve on an air receiver must match or exceed capacity of all attached compressors. I found the relieving capacity of the safety valve was less than that what's required. The air receiver may rupture due to restricted capacity of the safety valve | 0 | No Created Hazard Identified | Air_compressor_data.png | file://x:/photopub/docs/0000000468/d40d307d-b74f-4ff8-a8fa-b883adddfed8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83ee7245_f3cc_4896_a98f_70a5c8844dbc
BPVIN-628416-2016 | BPV-422676-2016 | 8/10/2016 10:49:54 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | Relieving capacity of a safety valve on an air receiver must match or exceed capacity of all attached compressors. I found the relieving capacity of the safety valve was less than that what's required. The air receiver may rupture due to restricted capacity of the safety valve | 0 | No Created Hazard Identified | Safety_valve_data.png | file://x:/photopub/docs/0000000468/0d0a23d8-1a77-4590-99bd-467d013d7085.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83ee7245_f3cc_4896_a98f_70a5c8844dbc
BPVOP-628529-2016 | 2266922 | 8/10/2016 12:25:18 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP201 | 5.1.0 In service proc/process - Burner setup incorrect | 2 | 2 | Upon assessment it is found that 4 out of 8 burner throat attaching studs are broken. If all studs are not restored as per original design remaining studs may fail due to overload and may lead to expensive repair. | 2 | 5.1.0 In service proc/process - Burner setup incorrect | Burner_throat_securing_arrangement.png | file://x:/photopub/docs/0000000469/f015e905-267a-41eb-880c-bd39081529b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03b38400_0c02_425c_a137_42f270b0fff7
ELIN-663410-2016 | EL-400747-2016 | 9/15/2016 6:13:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | 100A 240V Service Disconnect Switch is not accessible to the occupant, this poses safety concerns if the service must be de-energized, also the power may be disconnected by others. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Suite_Service_Switch.png | file://x:/photopub/docs/0000000486/bd123517-c512-49e1-b03d-882d99367206.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93dd13fc_8fca_44fb_9579_1b69df57c965
ELIN-663416-2016 | EL-434349-2016 | 9/15/2016 5:04:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 120/240V 200A Main Panel has been installed in the new home under construction and is not properly protected from the weather, mechanical damage or unauthorized persons. This could result in a shock hazard to persons and damage to the equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_Panel.png | file://x:/photopub/docs/0000000486/c948db3f-3c7d-42c2-8e15-88434f26608a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__60e9e7f1_6609_486a_9957_9ee0f77bc774
GAIN-621092-2016 | GA-388220-2016 | 8/3/2016 1:52:31 PM | ASSESS: GA: Final | png | #asFound | GA139 | Incorrect appliance type installed for application | 3 | 3 | Insert fireplace installed in a uncertified solid fuel fireplace. Appliance is rated for installation in a certified wood burning fireplace and installation in a fireplace other than a certified solid fuel fireplace doesn't meet clearance to combustible ratings and could cause a fire. | 3 | Incorrect appliance type installed for application | Uncertified_solid_fuel_burning_fireplace_.png | file://x:/photopub/docs/0000000465/8f122a11-5258-4bb2-b043-dff050ea2444.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b548683d_0b98_44c6_b823_d20c638e6960
GAIN-622695-2016 | GA-414710-2016 | 8/3/2016 10:15:33 AM | ASSESS: GA: Final | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | Deep fat fryer installed next to an open flame creates a fire hazard if non combustible divider is not installed. Fryer grease can catch fire from the open flame of the Chinese cooker. | 2 | Appliance installed in a proposed hazardous location | No_protection_between_deep_fat_fryer_and_open_flame_.png | file://x:/photopub/docs/0000000465/372e4f2a-e62a-42e5-8c49-71196bb246bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2dbab007_d5c9_4920_9156_71a9b598593b
GAIN-617717-2016 | GA-413294-2016 | 8/3/2016 7:33:23 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | Vent_term.png | file://x:/photopub/docs/0000000465/0c8b2a36-2f13-4874-bf04-1e91828ae71d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a2a1736_9f86_41c3_8aa3_c6e05f087e05
ELIN-628672-2016 | EL-417409-2016 | 8/10/2016 2:24:22 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Consumer service pole deteriorated and not back guyed. This creates a risk of personal injury (shock) or property damage (thermal event) due to failure of the consumer service pole. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | View01_Service_pole.png | file://x:/photopub/docs/0000000469/2030790d-9512-43b9-8d6a-7380dd8f8c74.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__764b199b_c11a_45ea_bd4d_4c2391a67d0e
ELIN-628672-2016 | EL-417409-2016 | 8/10/2016 2:24:22 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Consumer service pole deteriorated and not back guyed. This creates a risk of personal injury (shock) or property damage (thermal event) due to failure of the consumer service pole. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Detail03_service_pole.png | file://x:/photopub/docs/0000000469/87935c35-4f7e-4c73-8f2f-5196ab322214.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__764b199b_c11a_45ea_bd4d_4c2391a67d0e
ELIN-628672-2016 | EL-417409-2016 | 8/10/2016 2:24:22 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Consumer service pole deteriorated and not back guyed. This creates a risk of personal injury (shock) or property damage (thermal event) due to failure of the consumer service pole. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | View02_service_pole.png | file://x:/photopub/docs/0000000469/9f5c27e6-5003-427c-9804-927f2732811c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__764b199b_c11a_45ea_bd4d_4c2391a67d0e
ELIN-625459-2016 | EL-413838-2016 | 8/9/2016 2:55:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | This assssment found an outdoor receptacle that was exposed to the weather and without a cover plate. There's a fire hazard should the receptacle become wet and a shock hazard if a person contacts the energized terminals. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Receptacle.png | file://x:/photopub/docs/0000000468/0a30db7f-7710-4c1e-a573-1099f86f3c80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ab622f2_c3d2_496e_9ba3_b51ebb253f43
ELIN-662499-2016 | UW-437028-2016 | 9/15/2016 1:03:01 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Exposed energized electrical equipment in existing future electrical building and unit #28. 100 Amps, 120/240 Volt. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_exposed_energized_splitter_.png | file://x:/photopub/docs/0000000486/b741409d-2e19-46c8-8ac9-b4c77b73c915.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34996a6f_5c84_4663_a950_fc3b74f5fd95
ELIN-662499-2016 | UW-437028-2016 | 9/15/2016 1:03:01 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Exposed energized electrical equipment in existing future electrical building and unit #28. 100 Amps, 120/240 Volt. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_exposed_distribution_panel_.png | file://x:/photopub/docs/0000000486/166c600a-c9ab-4d8b-bb5c-270960736d0e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34996a6f_5c84_4663_a950_fc3b74f5fd95
ELIN-621501-2016 | EL-395681-2016 | 8/2/2016 11:09:28 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 2 | Raceway required between thermostat junction box and floor for non-heating leads of floor heat. | 3 | Protection and control Low voltage protection damaged or not provided. | 4606_Sheridan_1.png | file://x:/photopub/docs/0000000464/e18c2814-780a-4bcd-bfa2-f50469a33a0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3d6ada8_649a_410a_9f3e_82a925c55b07
ELIN-621501-2016 | EL-395681-2016 | 8/2/2016 11:09:28 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 2 | Raceway required between thermostat junction box and floor for non-heating leads of floor heat. | 3 | Protection and control Low voltage protection damaged or not provided. | 4606_sheridan_2.png | file://x:/photopub/docs/0000000464/a47f3a6a-3fb4-4d6d-a2c4-632e1204e301.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3d6ada8_649a_410a_9f3e_82a925c55b07
BPVOP-626772-2016 | 2268623 | 8/8/2016 9:46:28 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | Upon assessment of low pressure steam boiler with 100 square meters of heating surface, it is determined that safety valve is leaking. Leaky safety may result in complete failure of safety valve with likelihood of severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | LEAKY_SAFETY_VALVE.png | file://x:/photopub/docs/0000000468/519fc2e9-d03b-45f8-b7ee-2b79d5bbd87d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7ec9dfb_e3e5_407e_96b2_5d44c9c32084
ELIN-658592-2016 | EL-383747-2016 | 9/9/2016 1:21:01 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Potential shock hazard in the shower. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Image_1.png | file://x:/photopub/docs/0000000482/3eb1f072-106c-45cd-9bea-d2a848414717.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef699c28_cb96_4456_bcc0_ea238913490b
ELIN-650589-2016 | UW-435100-2016 | 9/2/2016 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found 240 volt 2 pole breaker is of a different manufacturer, design and compatibility than panelboard manufacturer. When electrical equipment is not comatible and approved for the use, the electrical equipment might not work properly and could fail and become a possible electrical fire or shock hazard. | 3 | General Equipment is not approved for the specific use | 11.png | file://x:/photopub/docs/0000000482/87e7d74b-44b4-4da4-88ef-9a2d31764cab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9caa207_cc5c_4454_aeeb_432656851620
ELIN-650589-2016 | UW-435100-2016 | 9/2/2016 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found 240 volt 2 pole breaker is of a different manufacturer, design and compatibility than panelboard manufacturer. When electrical equipment is not comatible and approved for the use, the electrical equipment might not work properly and could fail and become a possible electrical fire or shock hazard. | 3 | General Equipment is not approved for the specific use | 12.png | file://x:/photopub/docs/0000000482/d8338e13-b3e1-470a-a0fa-b2e5832ff6e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9caa207_cc5c_4454_aeeb_432656851620
ELIN-650589-2016 | UW-435100-2016 | 9/2/2016 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found 240 volt 2 pole breaker is of a different manufacturer, design and compatibility than panelboard manufacturer. When electrical equipment is not comatible and approved for the use, the electrical equipment might not work properly and could fail and become a possible electrical fire or shock hazard. | 3 | General Equipment is not approved for the specific use | 13.png | file://x:/photopub/docs/0000000482/220a346a-0ac6-4ea9-a457-1b26cf5d0077.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9caa207_cc5c_4454_aeeb_432656851620
ELIN-650589-2016 | UW-435100-2016 | 9/2/2016 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found 240 volt 2 pole breaker is of a different manufacturer, design and compatibility than panelboard manufacturer. When electrical equipment is not comatible and approved for the use, the electrical equipment might not work properly and could fail and become a possible electrical fire or shock hazard. | 3 | General Equipment is not approved for the specific use | 16.png | file://x:/photopub/docs/0000000482/36751c35-fc13-4d95-8351-8277a4e1d389.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9caa207_cc5c_4454_aeeb_432656851620
ELIN-650589-2016 | UW-435100-2016 | 9/2/2016 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found 240 volt 2 pole breaker is of a different manufacturer, design and compatibility than panelboard manufacturer. When electrical equipment is not comatible and approved for the use, the electrical equipment might not work properly and could fail and become a possible electrical fire or shock hazard. | 3 | General Equipment is not approved for the specific use | 14.png | file://x:/photopub/docs/0000000482/9c378a59-0e0a-43f6-ab89-a2edf52fd202.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9caa207_cc5c_4454_aeeb_432656851620
ELIN-650589-2016 | UW-435100-2016 | 9/2/2016 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found 240 volt 2 pole breaker is of a different manufacturer, design and compatibility than panelboard manufacturer. When electrical equipment is not comatible and approved for the use, the electrical equipment might not work properly and could fail and become a possible electrical fire or shock hazard. | 3 | General Equipment is not approved for the specific use | 15.png | file://x:/photopub/docs/0000000482/58cfadba-8b82-4f5b-a4a7-6be5ced08572.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9caa207_cc5c_4454_aeeb_432656851620
GAIN-614079-2016 | GA-407630-2016 | 9/12/2016 8:33:53 PM | ASSESS: GA: Final | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | 20 pound propane cylinder with recreational vehicle lantern attached with hose was being used in cabin bedroom.lantern was to close to combustible materials. Lantern could cause the combustible material to ignight causing cabin to burn down and possible loss of life. | 3 | Code prohibited practices or materials | 7__cricket_Lane__Kennedy_Lake.png | file://x:/photopub/docs/0000000483/41a5a1ac-69c7-4733-a4a7-e4845c17e52b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__423de74b_1879_445d_b1fa_adfed1f2d6f7
ELIN-641107-2016 | EL-376515-2016 | 9/6/2016 2:15:10 PM | ASSESS: EL: Final | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | The 200 amp 120/240 volt service panel has open breaker spaces exposing the possibility of accidental contact to energized bussing in panelboard. This a is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Main_Service_panel.png | file://x:/photopub/docs/0000000481/5096b714-0b9e-4bb1-ab72-7fbe9d8e3893.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ccee90d_1b67_4463_998c_58fb3cd93ce0
EDIN-620727-2016 | ED-368257-2016 | 8/2/2016 12:12:53 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED003 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 3 | 3 | Unit has a shallow pit, there is a stand that is to be erected when work is to be done in pit. This stand will prevent the elevator coming down and crushing personnel working in pit. The stand was not secured properly to the floor with appropriate hardware. | 3 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | Improper__fastening.png | file://x:/photopub/docs/0000000465/226ec160-29b7-485b-abde-026d48143630.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e4f3639_2f81_4a18_b1fc_ec92ff770431
EDIN-620727-2016 | ED-368257-2016 | 8/2/2016 12:12:53 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED003 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 3 | 3 | Unit has a shallow pit, there is a stand that is to be erected when work is to be done in pit. This stand will prevent the elevator coming down and crushing personnel working in pit. The stand was not secured properly to the floor with appropriate hardware. | 3 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | Bent_fastener.png | file://x:/photopub/docs/0000000465/0c0e051b-7a48-4464-b63c-39fa4356aa46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e4f3639_2f81_4a18_b1fc_ec92ff770431
EDIN-620727-2016 | ED-368257-2016 | 8/2/2016 12:12:53 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED003 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 3 | 3 | Unit has a shallow pit, there is a stand that is to be erected when work is to be done in pit. This stand will prevent the elevator coming down and crushing personnel working in pit. The stand was not secured properly to the floor with appropriate hardware. | 3 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | Pit_safety_stand.png | file://x:/photopub/docs/0000000465/bb2d1328-2d7c-40d2-b7da-12659f7f1f69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e4f3639_2f81_4a18_b1fc_ec92ff770431
ELIN-643543-2016 | EL-409514-2016 | 9/9/2016 9:26:32 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | The 120/240V 200A AC System has not been effectively grounded, this could result in a shock hazard to persons and a failure of the breakers to operate as designed. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_Connection.png | file://x:/photopub/docs/0000000482/72b9d3fd-baf1-43e2-8bac-d548d35eb45e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15bad72c_1f8c_47dd_83df_edc6a61a8165
ELIN-626786-2016 | EL-374878-2016 | 8/18/2016 2:35:33 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | A new residence has had a 129 volt 20 amp receptacle installed for use with a built in vacuum. Combination arc fault protection has not been provided for the branch circuit or the receptacle. Combination arc fault breakers protect persons and property from potential damage due to arc fault potential of the circuit | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Standard_breaker_provided_for_built_in_vacuum_receptacle.png | file://x:/photopub/docs/0000000473/ac551076-2df1-455d-96ff-6e6137791bbd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67ceea19_5e4d_4534_91a0_dc9410d2802f
AMIN-612459-2016 | AM-391125-2016 | 7/15/2016 3:01:09 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM028 | Procedures/Signs not posted Improper training or procedure | 1 | 1 | In review of the operations and maintenance manual it was determined that no indication was given as to how to evaluate the need to conduct the wind test procedure specified in the manual (hanging 6'x4' plywood sheets formed in an X). There is a risk that operators may continuing operations of the ride in dangerous wind speeds, because in their opinion the wind speeds were not significant enough to conduct the wind test procedure. | 1 | Procedures/Signs not posted Improper training or procedure | Operations_manual_page_6_regarding_windy_conditions.png | file://x:/photopub/docs/0000000457/b9755be9-0d02-43ed-8280-bc5df54dab90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__858ce15a_4968_499a_8b89_7d1434f138eb
BPVOP-629391-2016 | 2270754 | 8/11/2016 11:27:18 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Upon assessment of low pressure steam heating boiler with 93 square meters heating surface it is determined that combined capacity of safety valves is less than theoretical minimum capacity required. In the event of over-pressure built up in the boiler (due to failure of control and other safety devices) there is possibility of permanent damage or even rupture of pressure boundary of boiler which can lead to incident. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_valves_for_boiler1.png | file://x:/photopub/docs/0000000469/5125bc7b-17cf-469f-beb6-353b23a1f63d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64dc9d16_fa54_491d_a5c9_d6add80b3e7e
BPVOP-629389-2016 | 2270755 | 8/11/2016 1:36:48 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Upon assessment of low pressure steam heating boiler with 93 square meters heating surface it is determined that combined capacity of safety valves is less than theoretical minimum capacity required. In the event of over-pressure built up in the boiler (due to failure of control and other safety devices) there is possibility of permanent damage or even rupture of pressure boundary of boiler which can lead to incident. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | SAFETY_VALVES.png | file://x:/photopub/docs/0000000469/db3f9073-440c-46d5-908b-f7a9d7a2abd0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b36c2ccc_f241_46aa_9320_16abe6999fa2
EDIN-620952-2016 | ED-112510-2014 | 7/20/2016 | ASSESS: ED IN: Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | Loose hardware on travel cable hanger under car | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Travel_cable_hanger.png | file://x:/photopub/docs/0000000468/47be42db-ae22-45ca-b9f4-7fb7bce0004e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56d3117c_4f6f_45c3_9535_2b28c72f4607
GAIN-658800-2016 | GA-427598-2016 | 9/9/2016 9:26:33 AM | ASSESS: GA: Rough-In | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 2 | Non compliant fittings. Connections in piping over 2 1/2" must be welded. | 3 | Non-compliant material/fittings installed | 3_inch_threaded_connection_to_natural_gas_compressor_.png | file://x:/photopub/docs/0000000483/1bfa2df5-b8d5-49b0-b26f-7d243e095ab0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__77aff3cf_c3c4_476f_88d6_950f2ea083f2
GAIN-643524-2016 | GA-416810-2016 | 9/12/2016 4:10:21 PM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | Clearance to combustible material from commercial moisture exhaust duct not maintained. Potential for fire is created when clearance to combustible materials are not maintained. | 3 | Non compliant Type C Vent clearance | Clearance_to_combustible_material_not_maintained_.png | file://x:/photopub/docs/0000000483/b8d94761-3924-4d8f-8732-13a54984b934.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c596045f_e126_4c84_9cd0_c65a65217163
ELOP-623390-2016 | 5400100 | 8/4/2016 10:32:21 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | Fire alarm systems are required to be in safe working conditions. This is required to ensure the fire alarm system will function in the event of a fire and provide early warning to protect persons and structures. An annual electrical inspection of a grocery store showed a trouble condition ( ground fault)on the fire alarm panel. A fire alam panel with a trouble condition may not function correctly in the event of a fire. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Fire_alarm_panel.png | file://x:/photopub/docs/0000000466/50c7f238-1037-46bd-b4b6-150c8b13c53d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0552493f_5950_4f55_ac73_4c278b805c65
BPVOP-641725-2016 | 2250760 | 8/30/2016 7:31:11 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | All pressure retaining components must be of a sufficient thickness in order to contain maximum average operation pressure of the working substance. I found that some ammonia carrying pipelines were substantially affected by corrosion under insulation, which reduces the thickness of the component and possible rendering it unfit to carry the ammonia under the service conditions. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Corrosion.png | file://x:/photopub/docs/0000000477/232fb804-1d0c-4aea-bf27-5bed3e9e5445.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21276087_472d_4202_aa19_907c8d744a36
BPVOP-641725-2016 | 2250760 | 8/30/2016 7:31:11 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | All pressure retaining components must be of a sufficient thickness in order to contain maximum average operation pressure of the working substance. I found that some ammonia carrying pipelines were substantially affected by corrosion under insulation, which reduces the thickness of the component and possible rendering it unfit to carry the ammonia under the service conditions. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Corrosion_2.png | file://x:/photopub/docs/0000000477/b85bf462-696a-4006-8d01-a9112728f279.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21276087_472d_4202_aa19_907c8d744a36
BPVOP-641725-2016 | 2250760 | 8/30/2016 7:31:11 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | All pressure retaining components must be of a sufficient thickness in order to contain maximum average operation pressure of the working substance. I found that some ammonia carrying pipelines were substantially affected by corrosion under insulation, which reduces the thickness of the component and possible rendering it unfit to carry the ammonia under the service conditions. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Corrosion_3.png | file://x:/photopub/docs/0000000477/b0735ccd-fd8c-4208-96ee-b62c616a9f30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21276087_472d_4202_aa19_907c8d744a36
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Piping_unprotected_move_underground.png | file://x:/photopub/docs/0000000462/1f571805-6eea-4315-98b5-c2baa658ed2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Non_compliant_appliance_connector.png | file://x:/photopub/docs/0000000462/657c7707-cd80-4bc6-abf6-6feb316f1690.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Regulator_below_liquid_level.png | file://x:/photopub/docs/0000000462/41789a89-4a30-459c-9eb2-299f1f6966d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | No_proper_tank_protection.png | file://x:/photopub/docs/0000000462/66beaea3-cee7-4349-b4b4-0a9637182af0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Tank_protective_dome_missing.png | file://x:/photopub/docs/0000000462/b0615431-1e32-4f6c-b2f2-aba866f0159b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Damaged_hose.png | file://x:/photopub/docs/0000000462/05b56de3-1fe3-4740-8ca8-a98079705381.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Tank_to_close_to_bank.png | file://x:/photopub/docs/0000000462/a55e7b2d-b6ff-4c26-b24e-a271a1e40e3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | No_swing_joints.png | file://x:/photopub/docs/0000000462/4c6ebd83-e27a-4a6b-ae19-296c30bb27ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Furnace_not_secured.png | file://x:/photopub/docs/0000000462/5a9562bd-8b53-494b-ab99-1635a6aa51f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Regulator_mounted_to_low.png | file://x:/photopub/docs/0000000462/66fdde1f-1b12-490d-ae5b-3874931084f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Regulator_mounted_below_liquid_level.png | file://x:/photopub/docs/0000000462/bb505223-55ac-4b0e-889e-e97688600762.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | _2_regulator_below_liquid_level.png | file://x:/photopub/docs/0000000462/08524a64-591b-43cc-87b7-8802bbb0c594.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Regulator_below_liquid_level_.png | file://x:/photopub/docs/0000000462/06fe0a93-b9da-4dd9-b1aa-34923e99aff7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Sched_80_pipeing_required.png | file://x:/photopub/docs/0000000462/52088e44-e80c-4c67-91ab-bb4bfae1576d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Reg_below_liquid_level.png | file://x:/photopub/docs/0000000462/085c2907-84cb-4d4e-aa51-da5be854ec82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Tank_liquid_levels_.png | file://x:/photopub/docs/0000000462/23ea8229-daa3-4cea-bd41-134580e16b53.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Pipe_not_painted.png | file://x:/photopub/docs/0000000462/1c589dca-2f54-48ad-8438-9493fd9947b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-616210-2016 | UW-414751-2016 | 7/27/2016 11:11:35 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | Vent_termination_to_close_to_grade.png | file://x:/photopub/docs/0000000462/fdf0605b-1d75-4492-864e-d588e05cf6e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd3e0299_a9ee_4862_9768_a0dc9ed851af
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Tank_liquid_levels_do_not_match.png | file://x:/photopub/docs/0000000462/395225ad-4ca8-4327-9936-0b492e387279.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Cylinder_not_on_concrete_base.png | file://x:/photopub/docs/0000000462/8e9817e6-5752-47d1-8f6f-d52c7eff97ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
GAUP-617999-2016 | UW-415824-2016 | 6/6/2016 3:17:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | When the regulator is mounted below the liquid level of a propane tank liquid propane could enter the regulator. When liquid propane is trapped in the regulator it will expand into high pressure vapour damaging the regulator and over pressuring the system down stream. The over pressure condition will damage the safety controls of the connected equipment. | 4 | 1st stage regulator installed below container liquid level | Missing_valve.png | file://x:/photopub/docs/0000000462/547aaa86-ab37-4926-85cd-96a76a55eb17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ce911e7_fa57_4f4c_a861_66aeb110ae5c
ELIN-640871-2016 | EL-377454-2016 | 8/31/2016 8:50:48 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Cables installed in wood construction should be protected with a minimum of 32 mm of wood or approved steel protection plates. This protects the cables from being damaged during installation of wall finishes. During the inspection it was observed that cables had not been installed with adequate protection. This presents a possible shock hazard to the installer of the wall finishes and/or a short circuit that could cause a fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Singlehurst.png | file://x:/photopub/docs/0000000478/b94d86d5-69d9-40e0-84d8-066b683ec235.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ea4e65a_d4e9_4b23_b7de_733b6e048e4f
GAIN-640698-2016 | GA-394075-2016 | 8/29/2016 8:41:06 PM | ASSESS: GA: Final | png | #asFound | [7 empty] | Improper_dirt_pocket_.png | file://x:/photopub/docs/0000000477/f49ee6e6-5df8-47df-b259-2383d0fbde3d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__005088a2_33ce_4bd5_b82f_fb17536dab56
GAUP-643499-2016 | UW-433153-2016 | 9/1/2016 9:11:53 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The improper vent connection of the water heater causes products of combustion to spill into the occupied area of the building. The vent connector being pushed tight to the heat shield puts the heat shield in contact with combustible ceiling material creating a fire hazard. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Electrical_wires_in_contact_with_C_vent_.png | file://x:/photopub/docs/0000000480/cc937f49-d8cd-4827-9e70-050a6e088b8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__382582f0_fc80_429b_b136_d9a58fdc6d1b
GAUP-643499-2016 | UW-433153-2016 | 9/1/2016 9:11:53 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The improper vent connection of the water heater causes products of combustion to spill into the occupied area of the building. The vent connector being pushed tight to the heat shield puts the heat shield in contact with combustible ceiling material creating a fire hazard. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Live_electrical_wiring.png | file://x:/photopub/docs/0000000480/1946b164-5820-4880-ae8b-0e440229bab1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__382582f0_fc80_429b_b136_d9a58fdc6d1b
GAUP-643499-2016 | UW-433153-2016 | 9/1/2016 9:11:53 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The improper vent connection of the water heater causes products of combustion to spill into the occupied area of the building. The vent connector being pushed tight to the heat shield puts the heat shield in contact with combustible ceiling material creating a fire hazard. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | C_vent_tight_to_heat_shield.png | file://x:/photopub/docs/0000000480/d6ef3186-9abe-409e-ae64-42766ce62442.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__382582f0_fc80_429b_b136_d9a58fdc6d1b
BPVOP-615745-2016 | UW-414444-2016 | 8/3/2016 6:14:57 PM | ASSESS: BPV OP: Compliance Boiler | png | #asFound | BP105 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | Safety_Relief_Valve_piping.png | file://x:/photopub/docs/0000000465/5bbdf39c-01ce-4d8e-93b7-a0f728a2584b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90df1cd3_daec_414c_8c48_02f33d3e3f86
BPVIN-608207-2016 | BPV-408973-2016 | 7/11/2016 1:42:50 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | During the inspection of a steam Kettle with maximum allowable working pressure (MAWP) of 50 psig I found that the Safety Relief Valve was overdue for servicing/replacement as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | OVerdue_SV.png | file://x:/photopub/docs/0000000454/64b5f8ba-adac-426d-b107-172c3b3ee06d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb20ff2e_4189_4f85_9e04_f8ad24c27a5c
ELIN-624847-2016 | UW-384718-2016 | 8/4/2016 10:47:07 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords cannot be used as a replacement for permanent wiring. In this high traffic fish and chips restaurant flexible cords were observed in several locations where they should not have been used. | 4 | Conductors, Misuse of flexible cords. | Under_the_door.png | file://x:/photopub/docs/0000000465/c13f295b-f221-4980-a429-95a0824c39fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f5f3c6d_c037_40cc_b63f_4ff0287f2b53
BPVOP-603108-2016 | 2271384 | 6/29/2016 11:07:40 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP140 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | 1 | 1 |  | 1 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | Pressure_gauge_range_not_to_code.png | file://x:/photopub/docs/0000000451/3cb4adee-071d-432d-bc55-84d445ccf018.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0940ca29_442d_4a02_9fae_edcd7bffd89b
ELOP-195846-2014 | 4272 | 7/29/2016 9:58:56 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | The service panel at the ski hill service shed has no bond screw in the panel. This would require a fault to use the bond conductor as a fault path doing a fault. This creates a shock hazard during a fault. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Panel_skihill.png | file://x:/photopub/docs/0000000463/116d700e-5a70-40d2-b182-cc1ded22f1cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8bd9f4a_fe18_410a_8fe3_415943d7c2b9
ELIN-614001-2016 | EL-402461-2016 | 7/29/2016 3:46:19 PM | ASSESS: EL: Final | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 2 | This assessment found the service switch to be inaccessible. Without the ability to inspect and perform maintenance a fire hazard could go unnoticed. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Switch_location.png | file://x:/photopub/docs/0000000463/ebb241af-d452-4980-a317-40edf5772eec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__311917c9_505a_444e_9fe6_0aacb7b30208
ELIN-626037-2016 | EL-420046-2016 | 8/12/2016 12:32:51 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | No approved cover plates provided for energized 120v 15a outlets, increasing the likelihood of accidental electrical shock as a result of contact with energized device terminals. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_wiring_and_outlets_with_no_covers.png | file://x:/photopub/docs/0000000470/c3718003-3a45-4379-b6c5-f75a1140fd1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53d0d4ea_7c4f_48e5_86b1_5cf2776783b4
ELIN-622267-2016 | EL-416570-2016 | 8/4/2016 10:43:55 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found fluorescent luminaire on 120 volt circuit has branch circuit bonding conductor terminated under a wedge shaped head wood screw that is screwed into the wood used for bonding and the luminaire electrical equipment is not bonded at all. When electrical equipment is not bonded correctly and if there is a fault condition on the electrical system, the over-current devices might not operate effectively or immediately and this could be a possible electrical fire or shock hazard to people or property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Fluorescent_luminaires_not_supported_properly.png | file://x:/photopub/docs/0000000465/ca3f0b19-8f07-4bde-8ae0-43710e22959b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e594ad7_8c95_479a_8989_c71078a2e314
ELIN-622267-2016 | EL-416570-2016 | 8/4/2016 10:43:55 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found fluorescent luminaire on 120 volt circuit has branch circuit bonding conductor terminated under a wedge shaped head wood screw that is screwed into the wood used for bonding and the luminaire electrical equipment is not bonded at all. When electrical equipment is not bonded correctly and if there is a fault condition on the electrical system, the over-current devices might not operate effectively or immediately and this could be a possible electrical fire or shock hazard to people or property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Fluorescent_luminaire_not_bonded_correctly_2.png | file://x:/photopub/docs/0000000465/8d07492e-626d-4a2d-adc7-2e04d1ff8ede.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e594ad7_8c95_479a_8989_c71078a2e314
ELIN-622267-2016 | EL-416570-2016 | 8/4/2016 10:43:55 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found fluorescent luminaire on 120 volt circuit has branch circuit bonding conductor terminated under a wedge shaped head wood screw that is screwed into the wood used for bonding and the luminaire electrical equipment is not bonded at all. When electrical equipment is not bonded correctly and if there is a fault condition on the electrical system, the over-current devices might not operate effectively or immediately and this could be a possible electrical fire or shock hazard to people or property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Fluorescent_luminaire_not_bonded_correctly_1.png | file://x:/photopub/docs/0000000465/7ca691d3-23a5-4a6a-9e17-b2f40bf57eda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e594ad7_8c95_479a_8989_c71078a2e314
ELIN-622267-2016 | EL-416570-2016 | 8/4/2016 10:43:55 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found fluorescent luminaire on 120 volt circuit has branch circuit bonding conductor terminated under a wedge shaped head wood screw that is screwed into the wood used for bonding and the luminaire electrical equipment is not bonded at all. When electrical equipment is not bonded correctly and if there is a fault condition on the electrical system, the over-current devices might not operate effectively or immediately and this could be a possible electrical fire or shock hazard to people or property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Fluorescent_luminaire_not_bonded_correctly_4.png | file://x:/photopub/docs/0000000465/d730c22b-3659-4a5f-af4d-10a440e548e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e594ad7_8c95_479a_8989_c71078a2e314
ELIN-622267-2016 | EL-416570-2016 | 8/4/2016 10:43:55 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found fluorescent luminaire on 120 volt circuit has branch circuit bonding conductor terminated under a wedge shaped head wood screw that is screwed into the wood used for bonding and the luminaire electrical equipment is not bonded at all. When electrical equipment is not bonded correctly and if there is a fault condition on the electrical system, the over-current devices might not operate effectively or immediately and this could be a possible electrical fire or shock hazard to people or property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Fluorescent_luminaire_not_bonded_correctly_3.png | file://x:/photopub/docs/0000000465/4b40c4f7-145e-4df3-9863-3448e4528a9f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e594ad7_8c95_479a_8989_c71078a2e314
BPVOP-628922-2016 | 4232586 | 8/11/2016 9:45:08 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | Fireside pressures too high for the burner to shell seal, seal has ruptured and allows flue gases into the boiler enclosure and equipment room | 4 | 5.1.0 In service proc/process - Casing leakage | Heat_exchanger_fin_tube_pluggage.png | file://x:/photopub/docs/0000000469/dd178764-bbbf-4731-b8ae-95dea49fa0e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae08d6d6_7db5_470f_a8f3_f15fef1d5fc7
ELIN-631384-2016 | UW-424480-2016 | 8/12/2016 8:48:13 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Found unapproved electrical equipment for 120volt connected hot water heater with exposed component approved pump motor and exposed open spliced flexible cord connection to exposed single conductors. When electrical equipment and its wiring system is assembled and wired on site and is unapproved electrical equipment, the electrical equipment is a possible electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 100.png | file://x:/photopub/docs/0000000471/d8cff742-1b14-4807-a3ff-dfdd69bf938e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d2e3f4d_85cd_4cb7_ad57_82428a5f94f9
ELIN-631384-2016 | UW-424480-2016 | 8/12/2016 8:48:13 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Found unapproved electrical equipment for 120volt connected hot water heater with exposed component approved pump motor and exposed open spliced flexible cord connection to exposed single conductors. When electrical equipment and its wiring system is assembled and wired on site and is unapproved electrical equipment, the electrical equipment is a possible electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 102.png | file://x:/photopub/docs/0000000471/58f71fa5-a9fb-44c5-aff2-13667ac4d050.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d2e3f4d_85cd_4cb7_ad57_82428a5f94f9
ELIN-631384-2016 | UW-424480-2016 | 8/12/2016 8:48:13 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Found unapproved electrical equipment for 120volt connected hot water heater with exposed component approved pump motor and exposed open spliced flexible cord connection to exposed single conductors. When electrical equipment and its wiring system is assembled and wired on site and is unapproved electrical equipment, the electrical equipment is a possible electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 105.png | file://x:/photopub/docs/0000000471/57a43ce4-d91b-4956-8f81-37138567bdc2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d2e3f4d_85cd_4cb7_ad57_82428a5f94f9
ELIN-631384-2016 | UW-424480-2016 | 8/12/2016 8:48:13 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Found unapproved electrical equipment for 120volt connected hot water heater with exposed component approved pump motor and exposed open spliced flexible cord connection to exposed single conductors. When electrical equipment and its wiring system is assembled and wired on site and is unapproved electrical equipment, the electrical equipment is a possible electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 101.png | file://x:/photopub/docs/0000000471/ede73f10-a913-4ed4-80df-aba63ed418f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d2e3f4d_85cd_4cb7_ad57_82428a5f94f9
ELIN-631384-2016 | UW-424480-2016 | 8/12/2016 8:48:13 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Found unapproved electrical equipment for 120volt connected hot water heater with exposed component approved pump motor and exposed open spliced flexible cord connection to exposed single conductors. When electrical equipment and its wiring system is assembled and wired on site and is unapproved electrical equipment, the electrical equipment is a possible electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 104.png | file://x:/photopub/docs/0000000471/95943da6-10dc-4171-8cad-be73047af4e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d2e3f4d_85cd_4cb7_ad57_82428a5f94f9
ELIN-631384-2016 | UW-424480-2016 | 8/12/2016 8:48:13 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Found unapproved electrical equipment for 120volt connected hot water heater with exposed component approved pump motor and exposed open spliced flexible cord connection to exposed single conductors. When electrical equipment and its wiring system is assembled and wired on site and is unapproved electrical equipment, the electrical equipment is a possible electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 103.png | file://x:/photopub/docs/0000000471/20204611-5b09-4b34-8be5-bfc6ad194df1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d2e3f4d_85cd_4cb7_ad57_82428a5f94f9
ELHE-598775-2016 | HE-401193-2016 | 6/28/2016 10:34:33 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 | Electrical equipment is not accessible. Unable to operate equipment. | 1 | General Working space or dedicated space is being used for storage | Office_and_storage.png | file://x:/photopub/docs/0000000449/eb31e8a1-fd59-4818-a04d-242fd805b705.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ded62a33_1869_47cd_a7a5_f9ab82b47033
BPVOP-640592-2016 | 2268829 | 8/29/2016 4:28:09 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP065 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | 4 | 4 | Found High Pressure Steam Boiler (150 PSI) leaking water and steam because of a crack located between the tubesheet and combustion chamber. A potential for an incident exists because the boiler is not watertight and crack is likely to propagate. | 4 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | Crack.png | file://x:/photopub/docs/0000000477/fe2619f0-8603-4405-be3b-e1816cbdc23d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53b5a2ce_2182_47ff_bbb6_be4d929b7efd
GAUP-621214-2016 | UW-418632-2016 | 7/29/2016 11:15:48 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA103 | Power vent not installed according to installation instruction. | 3 | 3 | Found furnace vent termination to close to furnace air intake. This could result in the re-circulation of flue gases back into furnace and could cause incomplete combustion and the production of carbon monoxide. | 3 | Power vent not installed according to installation instruction. | Vent_termination_clearance.png | file://x:/photopub/docs/0000000463/bbdc6a36-d0c6-41b6-ac0b-de473809274f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad91b087_f7a7_49d1_9e7a_32b8d52be1e6
ELOP-446235-2015 | EL-195276-2014 | 8/3/2016 7:52:01 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | The service ground conductor has pulled out of the neutral lug due to power shed settling. This would create a shock hazard during a fault on the system. | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | Service_ground_damaged.png | file://x:/photopub/docs/0000000465/bde1bacd-dadb-4373-adef-5779b738cf69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81b2db36_9314_4d77_9edd_a151d31a6119
ELIN-633684-2016 | EL-382976-2016 | 8/17/2016 5:06:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | In an existing single family dwelling service upgrade installation, a 200amp 120/240volt service was found where the system ground conductor is not attached to the required neutral conductor. This can lead to a thermal effect. Pic attached. | 4 | Installation Grounding; conductor is not continuous. | Ground_conductor_too_short.png | file://x:/photopub/docs/0000000472/5c028b70-82c6-4c8e-958d-867e2f5ea541.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__771726a7_759c_41a1_8636_aa026886bf80
GAIN-532611-2016 | GA-305238-2015 | 8/9/2016 11:15:53 AM | ASSESS: GA: Final | png | #asFound | GA055 | Bonding for Corrugated Stainless Steel Tubing missing | 3 | 3 | Bonding on Corrugated stainless steel tubing missing. Corrugated stainless steel tubing can be damaged by electrical faults causing uncontrolled release of gas. | 3 | Bonding for Corrugated Stainless Steel Tubing missing | Unbonded_CSST_tubing.png | file://x:/photopub/docs/0000000468/59c2113c-c8eb-43a4-9d8e-7fe3e77c12fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a03fdde2_4671_48c8_b7b3_baf69cc1a5a9
BPVOP-642002-2016 | BPV-099132-2014 | 8/31/2016 9:22:47 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Boiler_scale_.png | file://x:/photopub/docs/0000000478/8cd76b8e-173c-4ea4-b20e-872dc0481cdd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c830d452_40e3_4c46_80a3_4b8bd29bcca6
ELIN-661719-2016 | EL-279063-2015 | 9/13/2016 8:05:54 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL109 | Conductors Identified conductor or neutral conductor has not been properly identified | 1 | 1 |  | 1 | Conductors Identified conductor or neutral conductor has not been properly identified | Meterbase_.png | file://x:/photopub/docs/0000000484/de372fe2-3ad0-4603-a24b-f7fc364f4173.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27089b82_55a8_4177_815e_c8bf6f2494d1
ELIN-642431-2016 | EL-428011-2016 | 9/1/2016 2:37:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL109 | Conductors Identified conductor or neutral conductor has not been properly identified | 1 | 1 | The main neutral has not been correctly identified therefore a potential hazard exists for the electrical worker identifying the correct grounded conductor at the main service. | 1 | Conductors Identified conductor or neutral conductor has not been properly identified | Main_meterbase.png | file://x:/photopub/docs/0000000479/064d8f3d-f2eb-456c-b799-04f0aefa0f93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e33dbc7_bf4c_491b_99bb_0cea2127221a
ELIN-640312-2016 | EL-399318-2016 | 9/1/2016 2:14:10 PM | ASSESS: EL: Service Connection | png | #asFound | EL035 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | 3 | 3 | Incorrect terminations could result in an electrical worker incorrectly assuming conductors are de-energized and therefore potential shock hazard may exist. | 3 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | Line_side_terminations.png | file://x:/photopub/docs/0000000479/169e46a6-a4d5-441e-81a0-2536f7648608.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a1359c6_9f43_476c_a663_a8997e8ec730
ELIN-642431-2016 | EL-428011-2016 | 9/1/2016 2:37:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL109 | Conductors Identified conductor or neutral conductor has not been properly identified | 1 | 1 | The main neutral has not been correctly identified therefore a potential hazard exists for the electrical worker identifying the correct grounded conductor at the main service. | 1 | Conductors Identified conductor or neutral conductor has not been properly identified | Sub_panel.png | file://x:/photopub/docs/0000000479/8a647ff1-b9ba-4c81-a507-cb430c0b8cdc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e33dbc7_bf4c_491b_99bb_0cea2127221a
GAIN-600381-2016 | GA-402110-2016 | 7/13/2016 3:31:45 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 2 | Concentric vent installed through roof too low. In winter time when snow is sitting on roof snow may block combustion air intake of vent causing the furnace too shutdown | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_rooftop.png | file://x:/photopub/docs/0000000455/d8079771-dbff-435d-b149-ac46488554bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63fb5280_a33e_46dd_abd8_d7e39d57f4a0
EDRI-644618-2016 | ED-380743-2016 | 9/6/2016 10:01:17 AM | ASSESS: ED RI: Extension | png | #asFound | ED057 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 2 | 2 | Gaps in landing floor creates a trip hazard. | 2 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | Landing_10.png | file://x:/photopub/docs/0000000480/1286c4b9-7057-4bf2-a87c-edeecf5533f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c6e0f91_8e98_4bf1_a867_7174b88171ff
ELIN-616176-2016 | EL-414703-2016 | 8/5/2016 10:30:08 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | This assessment found that a counter receptacle within 1.5m of a sink, was not Ground Fault protected. Having the receptacle near a sink without this protection presents a shock hazard. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Outlet_sink.png | file://x:/photopub/docs/0000000466/c4c60c31-5857-47e1-8fec-e79d29f43408.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57659f04_01dc_4bf8_b8b2_57d53745162f
ELIN-616176-2016 | EL-414703-2016 | 8/5/2016 10:30:08 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | This assessment found that a counter receptacle within 1.5m of a sink, was not Ground Fault protected. Having the receptacle near a sink without this protection presents a shock hazard. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Power_supply_covers.png | file://x:/photopub/docs/0000000466/4897d815-9a67-4855-8362-036e30fcfce5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57659f04_01dc_4bf8_b8b2_57d53745162f
GAHE-628793-2016 | HE-422939-2016 | 8/11/2016 1:35:33 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA089 | No hydrostatic relief in liquid propane system where required | 5 | 4 | No hydrostatic relief in piping between pump isolation valves, relief valves required in the event of over pressurization. | 5 | No hydrostatic relief in liquid propane system where required | Rainbow1.png | file://x:/photopub/docs/0000000470/27b79ccc-87c7-4f07-b57f-5bd41ac65c73.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ffd7937_18e9_48ec_8bb4_d4c11e03ade6
GAHE-628778-2016 | HE-422933-2016 | 8/10/2016 6:50:37 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA018 | Venting of pressure relief device indoors where source of ignition is present | 5 | 5 | 1000 USWG tank installed in a building, with relief valve terminated inside of building. Relief valve to terminate to the outdoors in the event of over pressurization relief will vent indoors where electrical installed. | 5 | Venting of pressure relief device indoors where source of ignition is present | Reynolds.png | file://x:/photopub/docs/0000000470/d53657ba-d096-4229-bcc7-28b69b4f2bd2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__892d64df_c694_4446_84ce_8a437afd512a
GAHE-628793-2016 | HE-422939-2016 | 8/11/2016 1:35:33 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA089 | No hydrostatic relief in liquid propane system where required | 5 | 4 | No hydrostatic relief in piping between pump isolation valves, relief valves required in the event of over pressurization. | 5 | No hydrostatic relief in liquid propane system where required | Rainbow2.png | file://x:/photopub/docs/0000000470/5dcd6f7f-9e91-49e5-98e5-d000024c14da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ffd7937_18e9_48ec_8bb4_d4c11e03ade6
GAHE-628797-2016 | HE-422946-2016 | 8/10/2016 8:14:40 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA089 | No hydrostatic relief in liquid propane system where required | 5 | 4 | Hydrostatic relief missing in liquid piping, relief valves required where liquid could be trapped to avoid over pressurization | 5 | No hydrostatic relief in liquid propane system where required | Likely1.png | file://x:/photopub/docs/0000000470/3f65085c-a60f-4519-94ba-6fda087997af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1651a33_6c71_44fb_8147_deb93863e5b6
ELIN-640713-2016 | EL-427526-2016 | 9/2/2016 10:32:54 AM | ASSESS: EL: Final | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | Branch circuit wiring splices and connections to light fixtures are required to be made in electrical outlet boxes. This is required to protect the wiring and connections, provided a means for mounting devices and fixtures, and to contain thermal energy in the event that the wiring, equipment, or connections fail. This existing installation in a green house and shed in the back yard of a residential property has 15A 120V wiring that is not spliced in outlet boxes and connections to light fixtures that are not contained in outlet boxes. Energized terminals of the light fixtures are in contact with the wood structure they are mounted to. This is a fire hazard if an electrical failure or damage to equipment and connections occur. It is also a potential shock hazard if a person or object contacts the energized parts on the light fixtures. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | Open_splice_in_green_house.png | file://x:/photopub/docs/0000000480/1328cb9b-1225-4262-ba92-039a1aeaabb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c812e79_4c40_4563_8e0b_f98d50a1ddb5
ELIN-640713-2016 | EL-427526-2016 | 9/2/2016 10:32:54 AM | ASSESS: EL: Final | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | Branch circuit wiring splices and connections to light fixtures are required to be made in electrical outlet boxes. This is required to protect the wiring and connections, provided a means for mounting devices and fixtures, and to contain thermal energy in the event that the wiring, equipment, or connections fail. This existing installation in a green house and shed in the back yard of a residential property has 15A 120V wiring that is not spliced in outlet boxes and connections to light fixtures that are not contained in outlet boxes. Energized terminals of the light fixtures are in contact with the wood structure they are mounted to. This is a fire hazard if an electrical failure or damage to equipment and connections occur. It is also a potential shock hazard if a person or object contacts the energized parts on the light fixtures. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | Shed_in_back_yard.png | file://x:/photopub/docs/0000000480/9e024d3a-365a-4708-8927-24c390cfee95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c812e79_4c40_4563_8e0b_f98d50a1ddb5
GAIN-619896-2016 | GA-375595-2016 | 7/29/2016 11:56:24 AM | ASSESS: GA: Final | png | #asFound | GA005 | Tubing connected to an unsupported meter | 2 | 2 |  | 2 | Tubing connected to an unsupported meter | No_meter_support_.png | file://x:/photopub/docs/0000000465/4b9c6856-e8fd-462d-a92c-bfd824752059.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6f4279c_34ae_4798_b9f9_49335ec56676
ELIN-603032-2016 | EL-403495-2016 | 6/30/2016 12:08:19 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL041 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | 1" PVC conduit has been used inside the building to run the branch wiring from the solar panels to the inverter, this poses a shock hazard to firefighters. | 3 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | PVC_Conduit.png | file://x:/photopub/docs/0000000451/551217f5-1b72-4404-98de-426cb7730f0d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f380fe1_a190_4ca4_a7ae_c6b8359c25ba
BPVIN-629431-2016 | BPV-423343-2016 | 8/17/2016 3:08:25 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP018 | 1.0.2 Clearances/Maintenance - Pipe supports not compliant but in place | 2 | 2 |  | 2 | 1.0.2 Clearances/Maintenance - Pipe supports not compliant but in place | Expansion_tank_support.png | file://x:/photopub/docs/0000000472/4ff768bc-1731-42cf-a472-21d1f0213846.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc8e37c3_30f9_4a5a_aef2_d3b9f625e8c5
BPVOP-629326-2016 | 3174764 | 8/11/2016 10:43:19 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP222 | 1.2.3 Boiler construction - Code required drain or blow off not provided. | 3 | 3 | Each steam or hot water boiler shall have one or more drain connections fitted with valves or cocks connecting to the lowest water containing spaces. I found no drain piping or valves installed on a 160 psi domestic hot water boiler. Potential exists for scolding or damage to equipment due to not having a a proper drain system in place. | 3 | 1.2.3 Boiler construction - Code required drain or blow off not provided. | Domestic_hot_water_boiler_no_drain.png | file://x:/photopub/docs/0000000472/27409878-bc2f-4ed4-8b5e-82d34e9ed8e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da36ddf1_c07c_436d_9e40_c21ab8ad39c1
GAIN-641658-2016 | GA-430150-2016 | 9/6/2016 2:04:32 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Black iron pipe and fittings buried underground, this could cause the pipe to erode and cause earlier deterioration. | 2 | Physical protection of piping and tubing absent. | 1.png | file://x:/photopub/docs/0000000480/b07a8f87-90f7-4168-b315-dbf50f15eec7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f3898bbe_d4de_42fa_9089_651efb08d0bd
ELIN-626859-2016 | EL-267094-2015 | 8/15/2016 10:25:04 AM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The acwu cables penetrate thought the roof without use of roof flashings to protect moisture from entering and allowing the possibility of ice buildup in winter conditions which could cause movement of the cable against the sharp metal roofing edge. This is an equipment damage issue | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | No_roof_flashing.png | file://x:/photopub/docs/0000000470/5ad1677e-6dd9-476d-9e4a-f3eddaa17ad7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12cbd9ce_3cc7_4834_a3a2_cd3c36421251
ELIN-626859-2016 | EL-267094-2015 | 8/15/2016 10:25:04 AM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The acwu cables penetrate thought the roof without use of roof flashings to protect moisture from entering and allowing the possibility of ice buildup in winter conditions which could cause movement of the cable against the sharp metal roofing edge. This is an equipment damage issue | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Underside_of_roof_penetration.png | file://x:/photopub/docs/0000000470/1b0c11bd-042b-4ebc-9469-8f40edafa50d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12cbd9ce_3cc7_4834_a3a2_cd3c36421251
ELIN-631168-2016 | EL-260466-2015 | 8/15/2016 2:19:46 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL251 | Category 1 Area classification required | 2 | 2 |  | 2 | Category 1 Area classification required | Meterbase.png | file://x:/photopub/docs/0000000470/7124a784-bc67-4252-b54f-0e6502a83dce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce4c3bfd_67ee_4a91_9753_8f5bd9faa96b
ELIN-631168-2016 | EL-260466-2015 | 8/15/2016 2:19:46 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL251 | Category 1 Area classification required | 2 | 2 |  | 2 | Category 1 Area classification required | Front_of_house.png | file://x:/photopub/docs/0000000470/a8671d0a-ee99-448a-9403-bfd3f5939580.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce4c3bfd_67ee_4a91_9753_8f5bd9faa96b
ELIN-625511-2016 | EL-418917-2016 | 8/15/2016 1:02:05 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Unapproved 30a 250v single female receptacle for use with standby generator, using a double-ended male cord, can result in the likelihood of electrical shock, due to exposed parts, when generator is running and cord is plugged into generator but not into outlet. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 30a_female_generator_receptacle.png | file://x:/photopub/docs/0000000470/a91d8bb6-4656-494c-b6b2-8dc4e08cc74b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e06d35bd_9d3a_4169_8619_4e1eb4e2c1b6
BPVIN-628573-2016 | BPV-422806-2016 | 8/10/2016 1:23:59 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP123 | 3.1.1 Safeties will not function - Pressure Relief Device Safety relief valve removed or bypassed | 5 | 5 | Pressure relief devices protect equipment from over pressure conditions and damage. Devices must be installed according to all applicable standards. I found a plug installed in lieu of a pressure relief device on a 200psi air receiver mounted with machine. Potential exists for an over pressure incident to occur due to a safety device not providing intended control. | 5 | 3.1.1 Safeties will not function - Pressure Relief Device Safety relief valve removed or bypassed | Plug_installed_in_lieu_of_PRD.png | file://x:/photopub/docs/0000000469/3ca4526f-19bb-444f-afe5-4d3a4a1923c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67ab04f5_97e6_4d63_a3e3_5da58afd5615
BPVIN-628573-2016 | BPV-422806-2016 | 8/10/2016 1:23:59 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP123 | 3.1.1 Safeties will not function - Pressure Relief Device Safety relief valve removed or bypassed | 5 | 5 | Pressure relief devices protect equipment from over pressure conditions and damage. Devices must be installed according to all applicable standards. I found a plug installed in lieu of a pressure relief device on a 200psi air receiver mounted with machine. Potential exists for an over pressure incident to occur due to a safety device not providing intended control. | 5 | 3.1.1 Safeties will not function - Pressure Relief Device Safety relief valve removed or bypassed | Air_compressor.png | file://x:/photopub/docs/0000000469/3143eb1d-16ad-4b30-900a-8e15b4f18656.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67ab04f5_97e6_4d63_a3e3_5da58afd5615
ELIN-640713-2016 | EL-427526-2016 | 9/2/2016 10:32:54 AM | ASSESS: EL: Final | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | Branch circuit wiring splices and connections to light fixtures are required to be made in electrical outlet boxes. This is required to protect the wiring and connections, provided a means for mounting devices and fixtures, and to contain thermal energy in the event that the wiring, equipment, or connections fail. This existing installation in a green house and shed in the back yard of a residential property has 15A 120V wiring that is not spliced in outlet boxes and connections to light fixtures that are not contained in outlet boxes. Energized terminals of the light fixtures are in contact with the wood structure they are mounted to. This is a fire hazard if an electrical failure or damage to equipment and connections occur. It is also a potential shock hazard if a person or object contacts the energized parts on the light fixtures. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | Open_splice_in_shed.png | file://x:/photopub/docs/0000000480/37330025-0381-40fb-8b32-24670159fc44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c812e79_4c40_4563_8e0b_f98d50a1ddb5
ELIN-640713-2016 | EL-427526-2016 | 9/2/2016 10:32:54 AM | ASSESS: EL: Final | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | Branch circuit wiring splices and connections to light fixtures are required to be made in electrical outlet boxes. This is required to protect the wiring and connections, provided a means for mounting devices and fixtures, and to contain thermal energy in the event that the wiring, equipment, or connections fail. This existing installation in a green house and shed in the back yard of a residential property has 15A 120V wiring that is not spliced in outlet boxes and connections to light fixtures that are not contained in outlet boxes. Energized terminals of the light fixtures are in contact with the wood structure they are mounted to. This is a fire hazard if an electrical failure or damage to equipment and connections occur. It is also a potential shock hazard if a person or object contacts the energized parts on the light fixtures. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | Exterior_of_mobile_home.png | file://x:/photopub/docs/0000000480/9f164c12-e87b-437e-8cf2-61635d28f150.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c812e79_4c40_4563_8e0b_f98d50a1ddb5
ELIN-640713-2016 | EL-427526-2016 | 9/2/2016 10:32:54 AM | ASSESS: EL: Final | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | Branch circuit wiring splices and connections to light fixtures are required to be made in electrical outlet boxes. This is required to protect the wiring and connections, provided a means for mounting devices and fixtures, and to contain thermal energy in the event that the wiring, equipment, or connections fail. This existing installation in a green house and shed in the back yard of a residential property has 15A 120V wiring that is not spliced in outlet boxes and connections to light fixtures that are not contained in outlet boxes. Energized terminals of the light fixtures are in contact with the wood structure they are mounted to. This is a fire hazard if an electrical failure or damage to equipment and connections occur. It is also a potential shock hazard if a person or object contacts the energized parts on the light fixtures. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | Connection_to_light_fixture_in_shed_in_contact_with_wood.png | file://x:/photopub/docs/0000000480/367cd034-080b-4ee2-a957-2b2cefb1bbc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c812e79_4c40_4563_8e0b_f98d50a1ddb5
ELIN-640713-2016 | EL-427526-2016 | 9/2/2016 10:32:54 AM | ASSESS: EL: Final | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | Branch circuit wiring splices and connections to light fixtures are required to be made in electrical outlet boxes. This is required to protect the wiring and connections, provided a means for mounting devices and fixtures, and to contain thermal energy in the event that the wiring, equipment, or connections fail. This existing installation in a green house and shed in the back yard of a residential property has 15A 120V wiring that is not spliced in outlet boxes and connections to light fixtures that are not contained in outlet boxes. Energized terminals of the light fixtures are in contact with the wood structure they are mounted to. This is a fire hazard if an electrical failure or damage to equipment and connections occur. It is also a potential shock hazard if a person or object contacts the energized parts on the light fixtures. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | Sheds_and_green_house_in_back_yard.png | file://x:/photopub/docs/0000000480/da647cf1-2b89-4025-8f8c-bde396287ae2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c812e79_4c40_4563_8e0b_f98d50a1ddb5
ELIN-640713-2016 | EL-427526-2016 | 9/2/2016 10:32:54 AM | ASSESS: EL: Final | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | Branch circuit wiring splices and connections to light fixtures are required to be made in electrical outlet boxes. This is required to protect the wiring and connections, provided a means for mounting devices and fixtures, and to contain thermal energy in the event that the wiring, equipment, or connections fail. This existing installation in a green house and shed in the back yard of a residential property has 15A 120V wiring that is not spliced in outlet boxes and connections to light fixtures that are not contained in outlet boxes. Energized terminals of the light fixtures are in contact with the wood structure they are mounted to. This is a fire hazard if an electrical failure or damage to equipment and connections occur. It is also a potential shock hazard if a person or object contacts the energized parts on the light fixtures. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | Wiring_in_green_house.png | file://x:/photopub/docs/0000000480/0d8088ae-2fcf-4cba-9277-2a6433e115a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c812e79_4c40_4563_8e0b_f98d50a1ddb5
ELIN-640713-2016 | EL-427526-2016 | 9/2/2016 10:32:54 AM | ASSESS: EL: Final | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | Branch circuit wiring splices and connections to light fixtures are required to be made in electrical outlet boxes. This is required to protect the wiring and connections, provided a means for mounting devices and fixtures, and to contain thermal energy in the event that the wiring, equipment, or connections fail. This existing installation in a green house and shed in the back yard of a residential property has 15A 120V wiring that is not spliced in outlet boxes and connections to light fixtures that are not contained in outlet boxes. Energized terminals of the light fixtures are in contact with the wood structure they are mounted to. This is a fire hazard if an electrical failure or damage to equipment and connections occur. It is also a potential shock hazard if a person or object contacts the energized parts on the light fixtures. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | Connection_to_fixture_in_contact_with_wood_in_green_house.png | file://x:/photopub/docs/0000000480/14d6a255-643b-4271-940a-7549f3be61eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c812e79_4c40_4563_8e0b_f98d50a1ddb5
GAIN-596373-2016 | GA-398003-2016 | 7/15/2016 12:26:33 PM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | Open window currently used to provide convection here to atmospheric appliances in mechanical room. In the case that the windows is closed A negative pressure can be created and effect the venting of the products of combustion allowing the unit to potentially backdraft or spill from the equipments draft hood and and enter the mechanical room. Insufficient air can all also contribute to poor combustion performance and efficiency. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Image_of_open_window_.png | file://x:/photopub/docs/0000000456/1cbb162e-5e49-4a1f-8b18-ac40ac8a0613.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c68ec38d_94e0_464e_b720_e305bdcabfe2
ELOP-460245-2015 | 2014579 | 8/24/2016 3:11:45 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | Access has been restricted to the 200A 208V panel by an added communication rack built in front of the panel. This poses a shock hazard to persons maintaining the panel as there is no clear working space. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Panel_H.png | file://x:/photopub/docs/0000000475/7aaf132c-22eb-44b3-9fc6-f8fffd43391e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf1bb445_a7ed_496c_90fd_cbe25fb4b961
ELIN-628693-2016 | EL-054400-2013 | 8/18/2016 11:35:58 AM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire branch circuits are required to be terminated to circuit breakers that are connected to different polarity line buses in circuit breaker panels. This is required so that the three wire circuit operates correctly with the neutral conductor carrying only the imbalance of current between the two line conductors of the circuit. This installation for a new 41 unit apartment building has multiple 15A 240V three wire branch circuits that have been terminated to circuit breakers connected to the same line bus in multiple panels throughout the building. This can cause the neutral conductor of these incorrectly terminated branch circuits to be subjected to 30A of current when both 15A circuit are fully loaded. The #14 gauge neutral conductors for these circuits are only rated to carry 15A of current. Left uncorrected this is a potential fire hazard if over heated neutral conductors or termination points cause thermal damage to conductor insulation on incorrectly terminated circuits that are loaded in excess | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Unit_209_where_three_wire_circuit_is_terminated_incorrectly_to_the_same_bus_in_the_panel.png | file://x:/photopub/docs/0000000472/bce2b924-b126-46eb-9bab-8f3da2f6c68a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bee5bb7_3185_43c4_b99d_c22f56a5292d
ELIN-628693-2016 | EL-054400-2013 | 8/18/2016 11:35:58 AM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire branch circuits are required to be terminated to circuit breakers that are connected to different polarity line buses in circuit breaker panels. This is required so that the three wire circuit operates correctly with the neutral conductor carrying only the imbalance of current between the two line conductors of the circuit. This installation for a new 41 unit apartment building has multiple 15A 240V three wire branch circuits that have been terminated to circuit breakers connected to the same line bus in multiple panels throughout the building. This can cause the neutral conductor of these incorrectly terminated branch circuits to be subjected to 30A of current when both 15A circuit are fully loaded. The #14 gauge neutral conductors for these circuits are only rated to carry 15A of current. Left uncorrected this is a potential fire hazard if over heated neutral conductors or termination points cause thermal damage to conductor insulation on incorrectly terminated circuits that are loaded in excess | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Exterior_of_apartment_building.png | file://x:/photopub/docs/0000000472/2c2e5ae3-9c52-43a6-ad94-d2f309cdf7f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bee5bb7_3185_43c4_b99d_c22f56a5292d
ELIN-628693-2016 | EL-054400-2013 | 8/18/2016 11:35:58 AM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire branch circuits are required to be terminated to circuit breakers that are connected to different polarity line buses in circuit breaker panels. This is required so that the three wire circuit operates correctly with the neutral conductor carrying only the imbalance of current between the two line conductors of the circuit. This installation for a new 41 unit apartment building has multiple 15A 240V three wire branch circuits that have been terminated to circuit breakers connected to the same line bus in multiple panels throughout the building. This can cause the neutral conductor of these incorrectly terminated branch circuits to be subjected to 30A of current when both 15A circuit are fully loaded. The #14 gauge neutral conductors for these circuits are only rated to carry 15A of current. Left uncorrected this is a potential fire hazard if over heated neutral conductors or termination points cause thermal damage to conductor insulation on incorrectly terminated circuits that are loaded in excess | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Unit_310_where_a_three_wire_circuit_is_incorrectly_terminated_onto_the_same_bus_in_the_panel_.png | file://x:/photopub/docs/0000000472/924240bb-42f0-4a17-9585-8f22e1ca2f40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bee5bb7_3185_43c4_b99d_c22f56a5292d
ELIN-628693-2016 | EL-054400-2013 | 8/18/2016 11:35:58 AM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire branch circuits are required to be terminated to circuit breakers that are connected to different polarity line buses in circuit breaker panels. This is required so that the three wire circuit operates correctly with the neutral conductor carrying only the imbalance of current between the two line conductors of the circuit. This installation for a new 41 unit apartment building has multiple 15A 240V three wire branch circuits that have been terminated to circuit breakers connected to the same line bus in multiple panels throughout the building. This can cause the neutral conductor of these incorrectly terminated branch circuits to be subjected to 30A of current when both 15A circuit are fully loaded. The #14 gauge neutral conductors for these circuits are only rated to carry 15A of current. Left uncorrected this is a potential fire hazard if over heated neutral conductors or termination points cause thermal damage to conductor insulation on incorrectly terminated circuits that are loaded in excess | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Apartment_building.png | file://x:/photopub/docs/0000000472/05c672c3-aef7-4a50-9f00-4fd9dcdaf0bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bee5bb7_3185_43c4_b99d_c22f56a5292d
ELIN-628693-2016 | EL-054400-2013 | 8/18/2016 11:35:58 AM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire branch circuits are required to be terminated to circuit breakers that are connected to different polarity line buses in circuit breaker panels. This is required so that the three wire circuit operates correctly with the neutral conductor carrying only the imbalance of current between the two line conductors of the circuit. This installation for a new 41 unit apartment building has multiple 15A 240V three wire branch circuits that have been terminated to circuit breakers connected to the same line bus in multiple panels throughout the building. This can cause the neutral conductor of these incorrectly terminated branch circuits to be subjected to 30A of current when both 15A circuit are fully loaded. The #14 gauge neutral conductors for these circuits are only rated to carry 15A of current. Left uncorrected this is a potential fire hazard if over heated neutral conductors or termination points cause thermal damage to conductor insulation on incorrectly terminated circuits that are loaded in excess | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Unit_302_where_a_three_wire_circuit_is_incorrectly_terminated_to_the_same_bus_in_the_panel.png | file://x:/photopub/docs/0000000472/51f8a390-5bc3-4f1c-8372-7072b662cf5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bee5bb7_3185_43c4_b99d_c22f56a5292d
ELIN-603944-2016 | UW-406363-2016 | 6/30/2016 12:23:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 5 | Electrical equipment with uncontrolled ground faults are a significant electrical shock hazard. In locations where persons may swim or play in the vicinity of faulted electrical equipment the shock risk can be severe. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Main_switch_equipment.png | file://x:/photopub/docs/0000000451/834e8fa3-448c-48be-9ae4-fd38559660f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe047bd4_12ef_46b7_975e_8a02c1434527
ELIN-603944-2016 | UW-406363-2016 | 6/30/2016 12:23:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 5 | Electrical equipment with uncontrolled ground faults are a significant electrical shock hazard. In locations where persons may swim or play in the vicinity of faulted electrical equipment the shock risk can be severe. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Well_pump_control_equipment.png | file://x:/photopub/docs/0000000451/83730d6e-b16c-48ee-8d18-cccaf9b5eae7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe047bd4_12ef_46b7_975e_8a02c1434527
ELIN-603944-2016 | UW-406363-2016 | 6/30/2016 12:23:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 5 | Electrical equipment with uncontrolled ground faults are a significant electrical shock hazard. In locations where persons may swim or play in the vicinity of faulted electrical equipment the shock risk can be severe. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Well_pump_circuit_conductors_at_well_house.png | file://x:/photopub/docs/0000000451/6a283957-efe5-46e6-bde7-ba59f252c6d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe047bd4_12ef_46b7_975e_8a02c1434527
ELIN-603944-2016 | UW-406363-2016 | 6/30/2016 12:23:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 5 | Electrical equipment with uncontrolled ground faults are a significant electrical shock hazard. In locations where persons may swim or play in the vicinity of faulted electrical equipment the shock risk can be severe. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Wet_rocks_where_voltmeter_probe_attached.png | file://x:/photopub/docs/0000000451/60a638e0-f419-44e8-a1e7-6a5593473c80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe047bd4_12ef_46b7_975e_8a02c1434527
ELIN-603944-2016 | UW-406363-2016 | 6/30/2016 12:23:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 5 | Electrical equipment with uncontrolled ground faults are a significant electrical shock hazard. In locations where persons may swim or play in the vicinity of faulted electrical equipment the shock risk can be severe. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Dead_fish_in_vicinity_of_well_house.png | file://x:/photopub/docs/0000000451/b6e7a27f-60b6-457b-8454-7fd0f1d3157c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe047bd4_12ef_46b7_975e_8a02c1434527
ELIN-603944-2016 | UW-406363-2016 | 6/30/2016 12:23:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 5 | Electrical equipment with uncontrolled ground faults are a significant electrical shock hazard. In locations where persons may swim or play in the vicinity of faulted electrical equipment the shock risk can be severe. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Well_house_location_on_river_channel.png | file://x:/photopub/docs/0000000451/3ed75732-1ff4-4944-87ee-4d977ae1ca91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe047bd4_12ef_46b7_975e_8a02c1434527
ELIN-603944-2016 | UW-406363-2016 | 6/30/2016 12:23:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 5 | Electrical equipment with uncontrolled ground faults are a significant electrical shock hazard. In locations where persons may swim or play in the vicinity of faulted electrical equipment the shock risk can be severe. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Concrete_well_house_enclosure.png | file://x:/photopub/docs/0000000451/24d293f8-41e5-405d-8a9f-0ccfd3558856.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe047bd4_12ef_46b7_975e_8a02c1434527
ELHE-607446-2016 | HE-408499-2016 | 7/12/2016 2:11:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Pedestrian access to service conductors | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_conductor_clearance.png | file://x:/photopub/docs/0000000455/90b074d0-d30b-4efd-9837-9b1d2c9765f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a6556ec_bc08_42c9_bfd6_99a7400967f4
EDOP-628315-2016 | 3084054 | 6/24/2016 2:38:17 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED003 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 3 | 3 | If the car is stopped/stuck outside the landing, the passengers are not to open the car door and try to exit the elevator. They will be exposed to an open hoistway and may fall resulting in a fatality, the car may also move also exposing them to shearing/pinching hazards. For rider safety the manual opening of the elevator car doors when an elevator car is outside unlocking zone (landing) is restricted to 4 inches. It was found that the car door restrictor was not adjusted correctly and therefore would allow the door to open fully. There have been many reports of fatalities due to this condition. | 3 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | Door_restrictor.png | file://x:/photopub/docs/0000000469/3fcf7629-d693-4f79-8375-88dd07a18f7f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ddce972_88fd_453b_b45c_ad53a488258a
EDOP-628387-2016 | ED-418692-2016 | 6/24/2016 3:06:01 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED003 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 3 | 3 | If the car is stopped/stuck outside of the landing, the passengers are not to open the car door and try to exit the elevator. They will be exposed to the open hoistway and may fall resulting in a fatality, the car may also move also exposing them to shearing/pinching hazards. For rider safety the manual opening of the elevator car doors when an elevator car is outside unlocking zone (landing) is restricted to 4 inches. It was found that the car door restrictor was not adjusted correctly and therefore would allow the door to open fully. There have been many reports of fatalities due to this condition. | 3 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | Door_restrictor_2.png | file://x:/photopub/docs/0000000469/cb21d13d-4171-41a9-bbb2-079d43d432ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e51acc18_54e9_45cd_9a4a_519345a24150
GAIN-585398-2016 | GA-374721-2016 | 7/5/2016 10:01:36 AM | ASSESS: GA: Final | png | #asFound | GA085 | Regulator vent not terminated as per manufacturers instruction | 3 | 3 | Vent limiter found in wrong position and in the event of diaphragm failure the release of gas may not be controlled in a safe manner. | 3 | Regulator vent not terminated as per manufacturers instruction | Reg1.png | file://x:/photopub/docs/0000000451/46b932fa-2e0d-4cf2-bd59-5b858a372e6f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d28cac4_1d7b_4909_9f23_c700b383a41e
GAIN-638024-2016 | GA-428343-2016 | 9/8/2016 9:58:20 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | While assessing this installation I found a mechanical air intake located too close to a regulator relief opening. Should the furnace be firing and the regulator relieve, raw gas may be drawn into the combustion chamber causing the appliance to overfire. This would create the potential for fire or explosion. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Appliance_termination.png | file://x:/photopub/docs/0000000482/00688d44-0366-46ef-b9f6-cc194fd04f16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7947f7c_067a_412c_969f_2f41b633978c
ELIN-600487-2016 | EL-399236-2016 | 7/5/2016 2:41:44 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service conductors installed more than 1.5m within a building create a fire hazard if they should fail or suffer mechanical damage | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_cable_length_exceeds_1_5m.png | file://x:/photopub/docs/0000000452/bc9c6e58-fd7f-4003-8a84-261c30bd7310.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cb2b3a23_a50c_4b44_a9fc_2044df5c8a3b
ELIN-629976-2016 | EL-419597-2016 | 8/15/2016 11:46:17 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Addition NMSC wiring in 2x3 walls are drilled closer than 32mm from edge of 2x3 members NMSC drilled to close to the edge of structural support Members are subject to damage from nailing or screw penetration and present a possible thermal hazard if damaged | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Panel_storage_cabinet.png | file://x:/photopub/docs/0000000471/dd47e13d-1736-47e1-8a25-512c13aeedf4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93bfc13f_6d74_49a5_aee1_5a74648fcefe
ELIN-629976-2016 | EL-419597-2016 | 8/15/2016 11:46:17 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Addition NMSC wiring in 2x3 walls are drilled closer than 32mm from edge of 2x3 members NMSC drilled to close to the edge of structural support Members are subject to damage from nailing or screw penetration and present a possible thermal hazard if damaged | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Holes_drilled_to_close.png | file://x:/photopub/docs/0000000471/d1e5c46d-187d-484c-9470-a1dabda8d1ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93bfc13f_6d74_49a5_aee1_5a74648fcefe
ELIN-631211-2016 | EL-383139-2016 | 8/16/2016 2:06:27 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Shock hazard in case of plugged in equipment failure and person is touching it and grounded sink at same time. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | No_GFCI.png | file://x:/photopub/docs/0000000471/1cefa30e-74cc-414f-a2e2-fa07ae4267f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40bd6cec_a8d3_4682_81df_fbf297499f75
ELIN-618286-2016 | EL-298636-2015 | 8/4/2016 8:22:40 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 120 volt approved portable cord connected fluorescent luminaire with three prong plug male cord cap end has bonding conductor blade broken off and completely removed intentionally for plugging into two prong female screw shell adapter for luminaire. When electrical equipment is not bonded as required for use of approved electrical equipment, the luminaire is a possible electrical fire or shock hazard to people or property if there is a fault condition within luminaire wiring system. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 42.png | file://x:/photopub/docs/0000000466/f9b078c0-1cc3-4ee8-a039-00140a623d8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__690f0bc1_6161_4376_9888_9e7a6253481d
ELIN-636147-2016 | EL-398637-2016 | 9/8/2016 2:40:44 PM | ASSESS: EL: Final | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Electrical metallic tubing connecters are not tightened. conduit and connecters form a bonding path back to ground which is not completed. Arcing and fire is likely when the connecters are not properly tighten and secured. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Bonding_is__bonding_is_not_completed_on_EMT_connecters.png | file://x:/photopub/docs/0000000482/255a944e-a408-432d-8e6c-0391cea5a0ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dbb66d3f_c4c7_4963_b379_686d002f6125
GAWP-645014-2016 | GA-338929-2016 | 9/8/2016 11:12:00 AM | ASSESS: GA Work In Progress | png | #asFound | GA085 | Regulator vent not terminated as per manufacturers instruction | 3 | 3 | Vent limiter Relief not rated for outdoors, and is installed below snow level. This could cause the regulator to malfunction supplying excessive pressure to equipment | 3 | Regulator vent not terminated as per manufacturers instruction | Gen.png | file://x:/photopub/docs/0000000482/fbb415c1-f508-4b02-bff8-f206bb436293.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc8a5d63_7cac_4595_97dd_0c9f581ca0ea
GAIN-645502-2016 | GA-257270-2015 | 9/8/2016 4:41:04 PM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | Single wall vent through wall and under soffits, clearance to combustibles not met. This could create overheating and ignite combustible materials. | 3 | Non compliant Type C Vent clearance | T.png | file://x:/photopub/docs/0000000482/51dbe68f-0ad7-4c27-9c47-00b2e8fc53b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c5473a4_3e88_4881_9088_52c2ab0c449a
BPVIN-607005-2016 | BPV-359908-2016 | 8/5/2016 2:18:29 PM | ASSESS: BPV IN: Construction REF/PV | png | #asFound | BP015 | 1.0.2 Clearances/Maintenance - Weld undercut that exceeds Code limits but does no encroach on minimum thickness | 1 | 1 |  | 1 | 1.0.2 Clearances/Maintenance - Weld undercut that exceeds Code limits but does no encroach on minimum thickness | Undercut.png | file://x:/photopub/docs/0000000466/84a5ec69-4308-4f6a-8f24-852a98ac857a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d167f0fa_47e1_4e33_8f43_36aaa969d2a1
ELIN-603855-2016 | EL-349932-2016 | 7/4/2016 1:35:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | The 200 amp 120/240 volt service has no ground conductor connection, contractor has used aluminum bond conductor from feeder cable from meterbase as path to connect grounding conductor. Feeder cable is below grade in wet location- aluminum is not acceptable. The missing grounding conductor creates an unequally potential plane between the service grounded conductor and earth ground, this is a shock hazard | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Main_panelboard.png | file://x:/photopub/docs/0000000451/4a5878f2-b8ae-4979-a962-2c34b3566aa1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee91f52b_1fa3_4896_8517_c89a2284e9ac
ELIN-603855-2016 | EL-349932-2016 | 7/4/2016 1:35:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | The 200 amp 120/240 volt service has no ground conductor connection, contractor has used aluminum bond conductor from feeder cable from meterbase as path to connect grounding conductor. Feeder cable is below grade in wet location- aluminum is not acceptable. The missing grounding conductor creates an unequally potential plane between the service grounded conductor and earth ground, this is a shock hazard | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Panel.png | file://x:/photopub/docs/0000000451/38b5a2af-7be2-40ac-82ce-57560b1b1a05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee91f52b_1fa3_4896_8517_c89a2284e9ac
ELIN-601964-2016 | EL-402126-2016 | 7/4/2016 9:01:56 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 100 amp 120/240 volt temporary service is mounted on non-treated plywood, this can lead to equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Temp_service.png | file://x:/photopub/docs/0000000451/47c97055-36de-4bed-8573-8297e851ac1e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dbc7510c_511d_45bc_a727_ba84251a0496
ELIN-603855-2016 | EL-349932-2016 | 7/4/2016 1:35:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | The 200 amp 120/240 volt service has no ground conductor connection, contractor has used aluminum bond conductor from feeder cable from meterbase as path to connect grounding conductor. Feeder cable is below grade in wet location- aluminum is not acceptable. The missing grounding conductor creates an unequally potential plane between the service grounded conductor and earth ground, this is a shock hazard | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Meterbase.png | file://x:/photopub/docs/0000000451/093da93b-1f67-4589-99b0-362e6717c5a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee91f52b_1fa3_4896_8517_c89a2284e9ac
BPVOP-614780-2016 | 2888848 | 7/19/2016 5:11:06 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP120 | 3.0.1 Safeties will not function - Safety devices not functional, by-passed or missing with no back up corresponding safety/ operating control device | 5 | 5 | Safety device(s) protect boilers from dangerous conditions. I Found that a Low Water Cut-Off safety devices on this High Pressure Steam Boiler ( high pressure (150 PSI) were not operating correctly which lead to a low water incident and boiler damage. | 5 | 3.0.1 Safeties will not function - Safety devices not functional, by-passed or missing with no back up corresponding safety/ operating control device | Damage.png | file://x:/photopub/docs/0000000458/e92f4952-3808-43d0-b5cb-d85993bd1ab4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ead2730_0df3_445a_981e_9a6dc137ced3
BPVOP-614780-2016 | 2888848 | 7/19/2016 5:11:06 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP120 | 3.0.1 Safeties will not function - Safety devices not functional, by-passed or missing with no back up corresponding safety/ operating control device | 5 | 5 | Safety device(s) protect boilers from dangerous conditions. I Found that a Low Water Cut-Off safety devices on this High Pressure Steam Boiler ( high pressure (150 PSI) were not operating correctly which lead to a low water incident and boiler damage. | 5 | 3.0.1 Safeties will not function - Safety devices not functional, by-passed or missing with no back up corresponding safety/ operating control device | Failed_Low_Water_Cut-Off_safety_device_.png | file://x:/photopub/docs/0000000458/85034ee6-288b-42cc-afa8-4a8098e6c936.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ead2730_0df3_445a_981e_9a6dc137ced3
ELIN-654109-2016 | EL-276672-2015 | 9/9/2016 4:55:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Undersized conductors may overheat and become fire hazard. Device outlet boxes with too many conductors may overheat and become fire hazard. Too full an outlet box may cause wiring to fail when attempting to install the device. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Bonding_wire_connections.png | file://x:/photopub/docs/0000000483/a9c0d418-e56d-4818-ba9f-893d6569c07d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8aaefea_1353_4a85_b521_97e077a42265
ELIN-642255-2016 | EL-431127-2016 | 9/9/2016 1:47:28 PM | ASSESS: EL: Final | png | #asFound | EL169 | Protection and control Disconnect is not of proper type or rating. | 3 | 3 | A disconnect is required to protect service men from accidental energization of the circuit | 3 | Protection and control Disconnect is not of proper type or rating. | AC_without_disconnect_switch.png | file://x:/photopub/docs/0000000483/cb62ad6c-fcb8-434d-bfcd-f05f5c3b4ecf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a214d4ce_5536_49f7_851c_ed282f9e3f38
ELIN-654109-2016 | EL-276672-2015 | 9/9/2016 4:55:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Undersized conductors may overheat and become fire hazard. Device outlet boxes with too many conductors may overheat and become fire hazard. Too full an outlet box may cause wiring to fail when attempting to install the device. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Switch_box_wiring.png | file://x:/photopub/docs/0000000483/ad5bf1f5-cdc0-4e84-8bd2-6704775aa374.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8aaefea_1353_4a85_b521_97e077a42265
ELIN-654109-2016 | EL-276672-2015 | 9/9/2016 4:55:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Undersized conductors may overheat and become fire hazard. Device outlet boxes with too many conductors may overheat and become fire hazard. Too full an outlet box may cause wiring to fail when attempting to install the device. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Range_receptacle_wiring.png | file://x:/photopub/docs/0000000483/65d6abf3-740f-4f82-bd1a-0d7024e39b6f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8aaefea_1353_4a85_b521_97e077a42265
ELIN-639163-2016 | EL-428419-2016 | 8/31/2016 2:40:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | The 100 amp panel was located outdoors and is not approved for outdoor locations. Continued use could cause damage to the panel and components in the form of rust and could prevent the over current devices from operating correctly in an overload or short circuit situation. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | OSB_backing_on_plywood_enclosure_.png | file://x:/photopub/docs/0000000478/747f39f6-4895-4d7e-9839-1f39625bc40a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__edfbe007_66f8_48ee_8c26_9604a72b9c36
ELIN-639163-2016 | EL-428419-2016 | 8/31/2016 2:40:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | The 100 amp panel was located outdoors and is not approved for outdoor locations. Continued use could cause damage to the panel and components in the form of rust and could prevent the over current devices from operating correctly in an overload or short circuit situation. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Pole_mounted_service.png | file://x:/photopub/docs/0000000478/9056eea9-2958-405f-847e-74062265df0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__edfbe007_66f8_48ee_8c26_9604a72b9c36
ELIN-639163-2016 | EL-428419-2016 | 8/31/2016 2:40:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | The 100 amp panel was located outdoors and is not approved for outdoor locations. Continued use could cause damage to the panel and components in the form of rust and could prevent the over current devices from operating correctly in an overload or short circuit situation. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 100_amp_combination_panel_.png | file://x:/photopub/docs/0000000478/ecbbd272-a6bd-468e-befb-417a2c71c456.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__edfbe007_66f8_48ee_8c26_9604a72b9c36
GAIN-656590-2016 | GA-242519-2015 | 9/9/2016 11:06:17 AM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 |  | 2 | Certified appliance connector installed but not approved for application | Flex_connector.png | file://x:/photopub/docs/0000000482/17c910ed-4dcd-4250-a728-88b7ceb09ddf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ad030c6_703c_4fb5_b191_f25f5172159d
AMOP-634357-2016 | 3315427 | 8/19/2016 10:27:38 AM | ASSESS: AM OP: Periodic | png | #asFound | AM035 | Defects found where the required strength may no longer exist. | 4 | 4 | Fibreglass at PCU does not conform to manufacturers specifications. Could cause PCU to travel out of its pre-determined path | 4 | Defects found where the required strength may no longer exist. | Fibreglass_at_PCU.png | file://x:/photopub/docs/0000000473/d888c814-a3e8-4f97-843f-0dfd1bc93390.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f899b41_baec_44a2_8473_09e70ce96bf4
BPVOP-616908-2016 | 2276630 | 7/22/2016 10:10:50 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety valves and pressure relief devices require periodic service or replacement. I found no record of testing\service\replacement for safety valve on a 100 psi hot water boiler(s). Potential exists for a safety valve not to function properly in an over pressure situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Relief_valve_.png | file://x:/photopub/docs/0000000460/42a6ba0f-059e-425b-8f68-0b5e1ef2e33a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4bab7c29_bf8c_477f_a9c5_481bf5cafa4a
GAIN-619899-2016 | GA-375600-2016 | 7/29/2016 12:20:15 PM | ASSESS: GA: Final | png | #asFound | GA005 | Tubing connected to an unsupported meter | 2 | 2 |  | 2 | Tubing connected to an unsupported meter | Tubing_connected_to_unsupported_gas_meter.png | file://x:/photopub/docs/0000000468/1a5a25d7-142c-4274-b355-e1e15eb43b0d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__108c2a7b_ec34_4808_8181_d450662fa846
BPVIN-616216-2016 | BPV-414753-2016 | 7/21/2016 12:16:59 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP002 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | 5 | 5 | The name plate of every boiler and pressure vessel shall be stamped in accordance with the requirements of the appropriate section of the American Society of Mechanical Engineers Code. The stamping shall include the Canadian Registration Number, identification traceable to the manufacture and design characteristics. I found no stamping or certification markings on eight unfired pressure vessels. Potential exists for an incident due to design limits being unknown. | 5 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | compressed_air_flux_tank.png | file://x:/photopub/docs/0000000459/edf75f94-8b6a-411f-ad2e-ac9c6b371a87.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceb526da_11ba_4c1b_b1c3_1f9f79bc1fb7
BPVIN-616216-2016 | BPV-414753-2016 | 7/21/2016 12:16:59 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP002 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | 5 | 5 | The name plate of every boiler and pressure vessel shall be stamped in accordance with the requirements of the appropriate section of the American Society of Mechanical Engineers Code. The stamping shall include the Canadian Registration Number, identification traceable to the manufacture and design characteristics. I found no stamping or certification markings on eight unfired pressure vessels. Potential exists for an incident due to design limits being unknown. | 5 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | Pressure_relief_and_Gage_.png | file://x:/photopub/docs/0000000459/32a8b039-03bf-4d6e-898a-55d54a24ab3d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceb526da_11ba_4c1b_b1c3_1f9f79bc1fb7
BPVIN-616216-2016 | BPV-414753-2016 | 7/21/2016 12:16:59 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP002 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | 5 | 5 | The name plate of every boiler and pressure vessel shall be stamped in accordance with the requirements of the appropriate section of the American Society of Mechanical Engineers Code. The stamping shall include the Canadian Registration Number, identification traceable to the manufacture and design characteristics. I found no stamping or certification markings on eight unfired pressure vessels. Potential exists for an incident due to design limits being unknown. | 5 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | Flux_tank_no_stamping.png | file://x:/photopub/docs/0000000459/01a21893-be5d-4403-b62c-403aaa83d593.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceb526da_11ba_4c1b_b1c3_1f9f79bc1fb7
BPVOP-641932-2016 | 2298623 | 9/1/2016 11:12:54 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP184 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | 3 | 3 | During the external inspection of an air receiver with MAWP of 150 psig many combustibles were stored near or on top of the receiver. | 3 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | Combustibles_on_the_air_receiver.png | file://x:/photopub/docs/0000000479/c9ec9a90-1936-412d-8880-dfa01e6d90ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c31ec2a_3c8a_45c0_8fe7_ec964b2fc808
BPVOP-641931-2016 | 2260799 | 9/1/2016 10:07:27 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Pitting__.png | file://x:/photopub/docs/0000000479/db1925a5-04cf-4ff3-9eda-0a1aafdd1046.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15a638a6_afaf_49ae_80d6_36d14f45ff2f
GAIN-598170-2016 | GA-347873-2016 | 8/18/2016 2:01:31 PM | ASSESS: GA: Final | png | #asFound | GA096 | Supports in place but not in compliance with certified instructions | 1 | 1 |  | 1 | Supports in place but not in compliance with certified instructions | Vent_not_properly_supported.png | file://x:/photopub/docs/0000000473/c778010f-7302-4b76-8e1c-143864a04127.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a95d5725_556d_489f_af47_c47b9dbdeae3
GAIN-618206-2016 | GA-171680-2014 | 8/19/2016 11:31:43 AM | ASSESS: GA: Final | png | #asFound | GA069 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | 3 | 3 | A hazard is created when the burners are at maximum firing rate because the piping system cannot provide the required amount of fuel to burn reliably. Low gas pressure can cause delayed ignition that can lead to explosion and heat exchanger damage. | 3 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | Roof_top_gas_piping.png | file://x:/photopub/docs/0000000473/d4bb033a-19e7-4630-9b4e-23d45b0ceedc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc87bbda_02e1_4965_8413_04acffb97fb8
ELIN-610228-2016 | EL-394593-2016 | 7/22/2016 12:27:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Covers are required to be installed on panel boards that are intended to be energized. This is required to prevent accidental contact with energized parts from persons or objects, to mechanically protect the internal parts of the panel, and to contain thermal energy if a failure occurs within the panel. This installation has a new service panel installed within a mobile home that does not have the cover installed. An inspection for service connection was requested without the required panel cover in place. This is a potential shock hazard if persons or objects come in contact with energized parts and potential fire hazard if a failure occurs within the electrical panel board. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Front_of_Mobile.png | file://x:/photopub/docs/0000000460/2d3644fb-e41b-45a3-a15b-d04a75a4e81a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__839b6ac7_a02c_44ed_96f5_460995923109
ELIN-610228-2016 | EL-394593-2016 | 7/22/2016 12:27:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Covers are required to be installed on panel boards that are intended to be energized. This is required to prevent accidental contact with energized parts from persons or objects, to mechanically protect the internal parts of the panel, and to contain thermal energy if a failure occurs within the panel. This installation has a new service panel installed within a mobile home that does not have the cover installed. An inspection for service connection was requested without the required panel cover in place. This is a potential shock hazard if persons or objects come in contact with energized parts and potential fire hazard if a failure occurs within the electrical panel board. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | New_Service_pole.png | file://x:/photopub/docs/0000000460/6731c329-ec0e-480d-b753-0f13ce35dd2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__839b6ac7_a02c_44ed_96f5_460995923109
ELIN-610228-2016 | EL-394593-2016 | 7/22/2016 12:27:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Covers are required to be installed on panel boards that are intended to be energized. This is required to prevent accidental contact with energized parts from persons or objects, to mechanically protect the internal parts of the panel, and to contain thermal energy if a failure occurs within the panel. This installation has a new service panel installed within a mobile home that does not have the cover installed. An inspection for service connection was requested without the required panel cover in place. This is a potential shock hazard if persons or objects come in contact with energized parts and potential fire hazard if a failure occurs within the electrical panel board. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Main_Panel.png | file://x:/photopub/docs/0000000460/bd3da82c-172f-48fa-8517-34b20da6f57c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__839b6ac7_a02c_44ed_96f5_460995923109
ELOP-662175-2016 | 5289950 | 9/13/2016 11:07:57 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL179 | General Construction Indoor: Inadequate spacing from walls for transformer. | 4 | 4 | Electrical operating permit assessment on Inn. Two 600 V transformers have insufficient clearances at the rear from combustible walls. These clearances are well below the clearances required by code. The heat build-up can bake the combustible surface leading to fire. It can also lead to premature failure of the transformers. | 4 | General Construction Indoor: Inadequate spacing from walls for transformer. | Clearance_of_50mm_to_rear_of_transformers.png | file://x:/photopub/docs/0000000484/7a677f57-6461-4ed7-8e49-febd3dbf1938.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7297dd48_aa84_4b49_8bd6_61ebb289a80d
ELIN-616526-2016 | UW-414925-2016 | 7/22/2016 12:49:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Private high voltage overhead transformer mounted on a pole set in 1958, feeding a submarine cable. The pole and cross arm have visible signs of rot and require maintenance. The 600V 400A switch supports have rotted off. This is a shock and fire hazard. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | C.png | file://x:/photopub/docs/0000000460/a52840a3-7d2b-4cb8-8a13-4c765c2d0405.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01a33ad3_6e3b_4c5f_87bc_68a65e69c255
ELIN-616526-2016 | UW-414925-2016 | 7/22/2016 12:49:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Private high voltage overhead transformer mounted on a pole set in 1958, feeding a submarine cable. The pole and cross arm have visible signs of rot and require maintenance. The 600V 400A switch supports have rotted off. This is a shock and fire hazard. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | D.png | file://x:/photopub/docs/0000000460/383f3dcf-abd8-4e1b-810d-aceaa00a33e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01a33ad3_6e3b_4c5f_87bc_68a65e69c255
ELIN-616526-2016 | UW-414925-2016 | 7/22/2016 12:49:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Private high voltage overhead transformer mounted on a pole set in 1958, feeding a submarine cable. The pole and cross arm have visible signs of rot and require maintenance. The 600V 400A switch supports have rotted off. This is a shock and fire hazard. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | A.png | file://x:/photopub/docs/0000000460/1c725e0f-9387-432f-b39f-dff0f6ec20fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01a33ad3_6e3b_4c5f_87bc_68a65e69c255
ELIN-616526-2016 | UW-414925-2016 | 7/22/2016 12:49:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Private high voltage overhead transformer mounted on a pole set in 1958, feeding a submarine cable. The pole and cross arm have visible signs of rot and require maintenance. The 600V 400A switch supports have rotted off. This is a shock and fire hazard. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | B.png | file://x:/photopub/docs/0000000460/f62e044d-d153-4e16-9c8f-57570954dd34.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01a33ad3_6e3b_4c5f_87bc_68a65e69c255
ELIN-615165-2016 | EL-413865-2016 | 7/21/2016 1:13:57 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | A residential service 200 A 240 volt one phase service has been authorized for connection with the main service disconnect portion barrier missing. Main service conductors are required to be in separate enclosures from branch circuit wiring. A panel board is not approved for connection when missing the barrier and damage to equipment can result or misuse of this portion of panel can occur when this condition is present | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Barrier_missing_from_service_main_portion_of_panel_board.png | file://x:/photopub/docs/0000000460/8cb6694e-e657-4a36-98a2-a5a85c538a77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b540e79_dde2_4a27_9e14_2ce05721baa2
ELIN-627892-2016 | EL-387518-2016 | 8/10/2016 5:18:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | 200A 120/240V Main Panel has been installed for use while the home is under construction but the panel is exposed to the weather, no roof has yet been constructed. This could damage the panel by allowing water to enter the interior eventually causing corrosion which may allow the electrical components to fail at a later date. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Main_Panel.png | file://x:/photopub/docs/0000000469/53b61631-8987-4caf-983e-c41d824d1681.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__713f1f40_6efb_4392_986e_196be5bcfd4f
ELIN-610820-2016 | EL-395685-2016 | 7/14/2016 10:49:03 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Indoor rated service equipment installed in a wet location. This is a shock hazard. Service equipment installed in buildings prior to the roof being installed for construction purposes shall be weather proof and lockable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | A.png | file://x:/photopub/docs/0000000456/69898909-345d-4112-bf14-6d3b72142ca2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7dfb5c4c_f6d2_4849_b995_c39980936073
GAIN-612270-2016 | GA-373628-2016 | 7/15/2016 9:41:08 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | Termination.png | file://x:/photopub/docs/0000000456/ddb4dc32-6f68-497c-aa96-8b8c798bb286.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__116c8dec_3ab1_4799_af3f_a7aea2f57533
GAIN-612270-2016 | GA-373628-2016 | 7/15/2016 9:41:08 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | Manifold.png | file://x:/photopub/docs/0000000456/68714e4e-d583-4d40-a746-1b5fbab6c2a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__116c8dec_3ab1_4799_af3f_a7aea2f57533
GAIN-612193-2016 | GA-378166-2016 | 7/15/2016 9:49:59 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | Vent_termination_.png | file://x:/photopub/docs/0000000456/7eba6733-34a4-4c1f-aee0-263eccf5fddf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__674f24fc_dba6_4c47_b2c7_4e427c4de6c7
GAIN-612193-2016 | GA-378166-2016 | 7/15/2016 9:49:59 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | Gas_manifold_.png | file://x:/photopub/docs/0000000456/5e8ea221-565d-45f0-aa95-ada19be0d33f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__674f24fc_dba6_4c47_b2c7_4e427c4de6c7
ELIN-627063-2016 | EL-417329-2016 | 8/12/2016 8:41:20 AM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Panel_fillers.png | file://x:/photopub/docs/0000000470/82826301-439f-4c75-9913-4579dc0dc2e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c4133fe_d2d1_4488_b1f7_f28e07c2c0a9
ELIN-618653-2016 | EL-411679-2016 | 8/30/2016 8:48:44 AM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Conductors sized smaller than 1/0 American Wire Gauge (awg) are not permitted to be installed in parallel for service conductors, feeders, and branch circuits. This is not permitted because of concerns with the integrity of the terminations and conductor strength in the smaller size range. If the termination fails or a conductor is damaged or broken the smaller sized conductors may be subject to currents that they are not rated to carry. This installation of a clothes dryer branch circuit in a mobile home has two #12 awg conductors that have been installed in parallel and connected to the same circuit breaker terminations. Left uncorrected this is a fire hazard if either the conductor or termination points fail and the remaining conductor is left to carry more current than it is rated for. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Dryer_circuit_has_parallel_12_awg_conductors.png | file://x:/photopub/docs/0000000477/61c8068d-8d5b-42ef-8413-b28fe27f34ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eac4bf31_4362_4551_9545_3e8e5acc42f4
ELIN-618653-2016 | EL-411679-2016 | 8/30/2016 8:48:44 AM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Conductors sized smaller than 1/0 American Wire Gauge (awg) are not permitted to be installed in parallel for service conductors, feeders, and branch circuits. This is not permitted because of concerns with the integrity of the terminations and conductor strength in the smaller size range. If the termination fails or a conductor is damaged or broken the smaller sized conductors may be subject to currents that they are not rated to carry. This installation of a clothes dryer branch circuit in a mobile home has two #12 awg conductors that have been installed in parallel and connected to the same circuit breaker terminations. Left uncorrected this is a fire hazard if either the conductor or termination points fail and the remaining conductor is left to carry more current than it is rated for. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Panel_in_mobile_home.png | file://x:/photopub/docs/0000000477/72ed79ae-46e4-4992-9a95-ddbb7c1273b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eac4bf31_4362_4551_9545_3e8e5acc42f4
ELIN-618653-2016 | EL-411679-2016 | 8/30/2016 8:48:44 AM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Conductors sized smaller than 1/0 American Wire Gauge (awg) are not permitted to be installed in parallel for service conductors, feeders, and branch circuits. This is not permitted because of concerns with the integrity of the terminations and conductor strength in the smaller size range. If the termination fails or a conductor is damaged or broken the smaller sized conductors may be subject to currents that they are not rated to carry. This installation of a clothes dryer branch circuit in a mobile home has two #12 awg conductors that have been installed in parallel and connected to the same circuit breaker terminations. Left uncorrected this is a fire hazard if either the conductor or termination points fail and the remaining conductor is left to carry more current than it is rated for. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Exterior_of_used_mobile_home.png | file://x:/photopub/docs/0000000477/35b9153a-e92e-4868-b879-40d478a06424.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eac4bf31_4362_4551_9545_3e8e5acc42f4
ELIN-618653-2016 | EL-411679-2016 | 8/30/2016 8:48:44 AM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Conductors sized smaller than 1/0 American Wire Gauge (awg) are not permitted to be installed in parallel for service conductors, feeders, and branch circuits. This is not permitted because of concerns with the integrity of the terminations and conductor strength in the smaller size range. If the termination fails or a conductor is damaged or broken the smaller sized conductors may be subject to currents that they are not rated to carry. This installation of a clothes dryer branch circuit in a mobile home has two #12 awg conductors that have been installed in parallel and connected to the same circuit breaker terminations. Left uncorrected this is a fire hazard if either the conductor or termination points fail and the remaining conductor is left to carry more current than it is rated for. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Panel_directory_.png | file://x:/photopub/docs/0000000477/8367163b-97b1-469c-9b2b-0b26fe2638dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eac4bf31_4362_4551_9545_3e8e5acc42f4
ELIN-618653-2016 | EL-411679-2016 | 8/30/2016 8:48:44 AM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Conductors sized smaller than 1/0 American Wire Gauge (awg) are not permitted to be installed in parallel for service conductors, feeders, and branch circuits. This is not permitted because of concerns with the integrity of the terminations and conductor strength in the smaller size range. If the termination fails or a conductor is damaged or broken the smaller sized conductors may be subject to currents that they are not rated to carry. This installation of a clothes dryer branch circuit in a mobile home has two #12 awg conductors that have been installed in parallel and connected to the same circuit breaker terminations. Left uncorrected this is a fire hazard if either the conductor or termination points fail and the remaining conductor is left to carry more current than it is rated for. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Interior_of_panel_in_mobile_home.png | file://x:/photopub/docs/0000000477/85a377fc-9f1e-44a4-aa53-6c4605871193.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eac4bf31_4362_4551_9545_3e8e5acc42f4
ELIN-616133-2016 | EL-409698-2016 | 7/25/2016 12:31:39 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | 240V 20A breaker not properly installed. The breaker was found in the on position and lightly touching the bus bars. This is a fire hazard as arcing can occur at the poor connection. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | B.png | file://x:/photopub/docs/0000000461/0eac2a70-4d84-4950-b425-0814828f7448.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8ccd10f_64e1_49f8_9ddf_161ee94a8923
ELIN-616133-2016 | EL-409698-2016 | 7/25/2016 12:31:39 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | 240V 20A breaker not properly installed. The breaker was found in the on position and lightly touching the bus bars. This is a fire hazard as arcing can occur at the poor connection. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | A.png | file://x:/photopub/docs/0000000461/91110102-8ded-4843-ad4d-28782f595893.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8ccd10f_64e1_49f8_9ddf_161ee94a8923
ELIN-592072-2016 | EL-391811-2016 | 7/18/2016 11:36:47 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | In an existing single family dwelling, the upgrade of all 15amp 120volt outlets with the approved copper pigtails is near completion, just covers have not been installed. This could lead to a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outlet_in_spare_basement_bedroom.png | file://x:/photopub/docs/0000000457/7f1e6535-4799-4a36-8a87-3529d6456a92.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5de4eea3_bde1_4098_8376_a35f41ea7113
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Sabotaged_cable.png | file://x:/photopub/docs/0000000458/e7a990f2-cf8d-4da2-93b8-ddfcc51796ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 1.png | file://x:/photopub/docs/0000000458/a583c96e-5123-46aa-a25a-73d77791a348.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Unprotected_feeder_leaving_ground.png | file://x:/photopub/docs/0000000458/1b583f81-23ff-496b-aee3-c66a8bff1bfd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Electrical_room_and_mast.png | file://x:/photopub/docs/0000000458/367a81ac-758b-4537-8ca8-53753882e5bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Lighting_open_splices.png | file://x:/photopub/docs/0000000458/7720fcd6-84a0-41b6-b9ff-633f9cc895c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4.png | file://x:/photopub/docs/0000000458/4147aa36-4577-4d6a-8840-d2977863e957.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Service_dry_coupling.png | file://x:/photopub/docs/0000000458/5183a390-b587-4f8f-b5d7-74dfc9e91567.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 2.png | file://x:/photopub/docs/0000000458/41797399-6b60-415d-ad69-fd8f35c3dd2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Clearance_of_70mm.png | file://x:/photopub/docs/0000000458/f9f4506d-780a-4bed-829c-6d43cbf284c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Lighting_with_open_splices.png | file://x:/photopub/docs/0000000458/3d30d3d6-0558-4505-8b03-bebcf15d6377.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Equipment_clearance_.png | file://x:/photopub/docs/0000000458/a768a6e8-a801-4131-8bb9-843f58a0e97c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Service_below_attachment_point_.png | file://x:/photopub/docs/0000000458/8d8cb936-6809-44b9-aaa6-a575b7fc9d40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Connected_ballasts.png | file://x:/photopub/docs/0000000458/39595695-938b-4a23-a88d-7322b1fad63a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | EMT_connector_on_ACWU.png | file://x:/photopub/docs/0000000458/60e308bf-8b44-4120-ab8c-1f7e9f923069.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | service_conduits_entering_top_of_switch.png | file://x:/photopub/docs/0000000458/1b3e42ca-00c2-4531-80b1-e926797d5430.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
EDOP-612773-2016 | 3904837 | 7/11/2016 | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED016 | Oil/Water/Other Debris is found that: Is likely to affect components or operation | 4 | 4 | Found excessive oil accumulation in the elevator pit. Found no comments in maintenance log books regarding oil accumulation in pit. Found 9-20 Litre pails of hydraulic oil in elevator machine room. 7 of the 9 pails are empty. The elevator hydraulic system is leaking oil and the oil is accumulating in the pit. The maintenance log books have no indications of when the oil issue began and no oil log sheet was found. This could potentially cause an entrapment due to the hydraulic system not having enough oil for the elevator to reach the top landing. The elevator maintenance person could slip and trip if accessing the elevator pit for monthly maintenance. | 4 | Oil/Water/Other Debris is found that: Is likely to affect components or operation | Oil_pails_in_machine_room.png | file://x:/photopub/docs/0000000457/209a4683-0080-4e02-bba8-1e5f956d7adb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b7c81cb8_fb09_432d_9017_9c973b518f79
EDOP-612773-2016 | 3904837 | 7/11/2016 | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED016 | Oil/Water/Other Debris is found that: Is likely to affect components or operation | 4 | 4 | Found excessive oil accumulation in the elevator pit. Found no comments in maintenance log books regarding oil accumulation in pit. Found 9-20 Litre pails of hydraulic oil in elevator machine room. 7 of the 9 pails are empty. The elevator hydraulic system is leaking oil and the oil is accumulating in the pit. The maintenance log books have no indications of when the oil issue began and no oil log sheet was found. This could potentially cause an entrapment due to the hydraulic system not having enough oil for the elevator to reach the top landing. The elevator maintenance person could slip and trip if accessing the elevator pit for monthly maintenance. | 4 | Oil/Water/Other Debris is found that: Is likely to affect components or operation | Full_oil_pail_in_elevator_machine_room.png | file://x:/photopub/docs/0000000457/ff8388cc-2232-4758-88f2-df63c486dd40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b7c81cb8_fb09_432d_9017_9c973b518f79
EDOP-612774-2016 | 3904838 | 7/11/2016 | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED016 | Oil/Water/Other Debris is found that: Is likely to affect components or operation | 4 | 4 | Found excessive oil accumulation in the elevator pit. Found no comments in maintenance log books regarding oil accumulation in pit. Found 9-20 Litre pails of hydraulic oil in elevator machine room. 7 of the 9 pails are empty. The elevator hydraulic system is leaking oil and the oil is accumulating in the pit. The maintenance log books have no indications of when the oil issue began and no oil log sheet was found. This could potentially cause an entrapment due to the hydraulic system not having enough oil for the elevator to reach the top landing. The elevator maintenance person could slip and trip if accessing the elevator pit for monthly maintenance. | 4 | Oil/Water/Other Debris is found that: Is likely to affect components or operation | Full_pail_of_oil_.png | file://x:/photopub/docs/0000000457/568a9fd2-714d-4f07-826a-f4780bbd438d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97cb798a_6a32_46f9_85a0_7dc910eb06db
EDOP-612774-2016 | 3904838 | 7/11/2016 | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED016 | Oil/Water/Other Debris is found that: Is likely to affect components or operation | 4 | 4 | Found excessive oil accumulation in the elevator pit. Found no comments in maintenance log books regarding oil accumulation in pit. Found 9-20 Litre pails of hydraulic oil in elevator machine room. 7 of the 9 pails are empty. The elevator hydraulic system is leaking oil and the oil is accumulating in the pit. The maintenance log books have no indications of when the oil issue began and no oil log sheet was found. This could potentially cause an entrapment due to the hydraulic system not having enough oil for the elevator to reach the top landing. The elevator maintenance person could slip and trip if accessing the elevator pit for monthly maintenance. | 4 | Oil/Water/Other Debris is found that: Is likely to affect components or operation | Pails_of_oil_in_machine_room.png | file://x:/photopub/docs/0000000457/0fc07bf0-a01a-41ca-81ea-46ae28e7fd83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97cb798a_6a32_46f9_85a0_7dc910eb06db
ELIN-631290-2016 | EL-408626-2016 | 8/16/2016 11:50:27 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | Neutral bond screw/strap has not been removed in sub distribution. Isolating the neutral in the sub distribution would have the bond conductor provide a path for a fault to get to ground. If screw/strap is left in place there would be a potential for a fault to circulate and it may provide a risk of shock and fire to persons or property. | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | Sub_distribution_neutral_not_isolated.png | file://x:/photopub/docs/0000000471/5d0902e2-5dc8-4d97-8422-5b2642fa9eb1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__634e1cb9_6b7e_427d_8f2a_78ff7e3ecd1d
ELIN-627063-2016 | EL-417329-2016 | 8/12/2016 8:41:20 AM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Missing_receptacle.png | file://x:/photopub/docs/0000000470/65ff3f62-7804-452d-86e6-b16197fae3bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c4133fe_d2d1_4488_b1f7_f28e07c2c0a9
ELOP-438932-2015 | EL-287189-2015 | 8/12/2016 8:28:41 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | Exposed receptacle is energized. Potential for electric shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Receptacle_not_installed_.png | file://x:/photopub/docs/0000000470/8967b446-cd33-4e56-a5dd-79a6b60fe3a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__725b60d3_517d_4431_b889_c5283a038220
GAIN-645481-2016 | GA-257274-2015 | 9/8/2016 9:11:01 AM | ASSESS: GA: Final | png | #asFound | GA080 | Line pressure regulator without required overpressure protection in place | 3 | 3 | Roof top has 2 psi to the gas valve the equipment requires maximum of 14" WC inlet pressure. The equipment could become over fired creating a fire hazard. | 3 | Line pressure regulator without required overpressure protection in place | 2_psi_meter.png | file://x:/photopub/docs/0000000482/2717b700-fb2a-499b-b181-548c58166b62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__311ca03b_596f_479d_8e65_c8b2e6264f43
ELIN-638328-2016 | EL-343736-2016 | 8/25/2016 11:15:42 AM | ASSESS: EL: Final | png | #asFound | EL156 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | 3 | 3 | Lack of strapping for feeder to equipment | 3 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | Feed_to_heat_pump.png | file://x:/photopub/docs/0000000475/fa7b804f-1326-4a80-9502-224d753eaeba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__761fb5fb_4eda_49ea_8ce1_8e4e56eb60c5
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Building_not_protected_from_weather.png | file://x:/photopub/docs/0000000458/85d30c0f-608f-4ffa-a48a-38c08ca3c210.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 6.png | file://x:/photopub/docs/0000000458/285cbe3b-f1a0-437a-9a9f-be5fc5eb57a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 7_sabotage_.png | file://x:/photopub/docs/0000000458/c4442a80-9994-4bdd-a4b6-a35737341667.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 3.png | file://x:/photopub/docs/0000000458/35e32d35-e2ec-41a5-9c12-86b60d9f9901.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 8.png | file://x:/photopub/docs/0000000458/cf56eca4-af55-4292-a0f3-c23ec9305ca6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 10.png | file://x:/photopub/docs/0000000458/1f8ccd73-57a6-4af0-bf66-3b3e40fd19b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 5.png | file://x:/photopub/docs/0000000458/cfbddcc9-c7de-46d7-b971-fc6b7a6f44d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Sabotaged_feeder.png | file://x:/photopub/docs/0000000458/12c95597-a5ca-42eb-b420-7f63917821b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 9.png | file://x:/photopub/docs/0000000458/4b7b3447-9eb0-421e-b50f-f7ee8befe744.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Panel_with_no_cover.png | file://x:/photopub/docs/0000000458/a384d8a2-9f54-4af1-9c80-6162576d77ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_electrical_equipment.png | file://x:/photopub/docs/0000000458/8f34e347-50c8-4348-b937-3e46c3be900d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-611475-2016 | EL-406679-2016 | 7/18/2016 4:33:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical installation has many non-compliances. Some of these are unprotected branch circuits , dry equipment that has limited protection from the weather.This will probably result in a fire or a shock hazard if not corrected. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | CT_.png | file://x:/photopub/docs/0000000458/c7a70c74-276f-4d4f-93a7-d334500ed66a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__653a1d0c_3579_43af_a766_8f7f8d2d0e00
ELIN-610792-2016 | EL-408456-2016 | 7/19/2016 9:19:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead service conductor support attachment device is located too high above consumer's service head on pole. When overhead service conductor support attachment device is located too high above consumer's service head then elements of weather such as moisture or water could possibly enter electrical equipment and could cause damage or become a possible electrical shock or fire hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 102.png | file://x:/photopub/docs/0000000458/777b36fa-d1b9-4265-9e1b-546f835d5a64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__426f7ed5_b73a_4477_bd26_61ab8d951de3
ELIN-610792-2016 | EL-408456-2016 | 7/19/2016 9:19:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead service conductor support attachment device is located too high above consumer's service head on pole. When overhead service conductor support attachment device is located too high above consumer's service head then elements of weather such as moisture or water could possibly enter electrical equipment and could cause damage or become a possible electrical shock or fire hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 101.png | file://x:/photopub/docs/0000000458/9d94a699-78f7-41ad-929a-382d1aa1cb38.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__426f7ed5_b73a_4477_bd26_61ab8d951de3
ELIN-612764-2016 | EL-394027-2016 | 7/27/2017 | ASSESS: EL: Final | png | #asFound |  |  |  |  | Found overhead service conductor support attachment device is located too high above consumer's service head on pole. When overhead service conductor support attachment device is located too high above consumer's service head then elements of weather such as moisture or water could possibly enter electrical equipment and could cause damage or become a possible electrical shock or fire hazard. |  |  | 12.png | file://x:/photopub/docs/0000000458/69d45447-6074-45cc-9e10-c9542a1d5fae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8634fe3e_8489_4ac3_b48d_0909b895497d
ELIN-610792-2016 | EL-408456-2016 | 7/19/2016 9:19:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead service conductor support attachment device is located too high above consumer's service head on pole. When overhead service conductor support attachment device is located too high above consumer's service head then elements of weather such as moisture or water could possibly enter electrical equipment and could cause damage or become a possible electrical shock or fire hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 112.png | file://x:/photopub/docs/0000000458/ad60e641-dddb-4b01-9396-7859504317e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__426f7ed5_b73a_4477_bd26_61ab8d951de3
ELIN-610792-2016 | EL-408456-2016 | 7/19/2016 9:19:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead service conductor support attachment device is located too high above consumer's service head on pole. When overhead service conductor support attachment device is located too high above consumer's service head then elements of weather such as moisture or water could possibly enter electrical equipment and could cause damage or become a possible electrical shock or fire hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 103.png | file://x:/photopub/docs/0000000458/9a139cce-958f-4c47-b38d-aedff980ce9e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__426f7ed5_b73a_4477_bd26_61ab8d951de3
ELIN-612764-2016 | EL-394027-2016 | 7/27/2017 | ASSESS: EL: Final | png | #asFound |  |  |  |  | Found overhead service conductor support attachment device is located too high above consumer's service head on pole. When overhead service conductor support attachment device is located too high above consumer's service head then elements of weather such as moisture or water could possibly enter electrical equipment and could cause damage or become a possible electrical shock or fire hazard. |  |  | 10.png | file://x:/photopub/docs/0000000458/03a72f78-a1a9-4dfe-bd29-b49a6c8d3423.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8634fe3e_8489_4ac3_b48d_0909b895497d
ELIN-612764-2016 | EL-394027-2016 | 7/27/2017 | ASSESS: EL: Final | png | #asFound |  |  |  |  | Found overhead service conductor support attachment device is located too high above consumer's service head on pole. When overhead service conductor support attachment device is located too high above consumer's service head then elements of weather such as moisture or water could possibly enter electrical equipment and could cause damage or become a possible electrical shock or fire hazard. |  |  | 11.png | file://x:/photopub/docs/0000000458/0589727f-b2d1-4746-919e-b37cf927f56a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8634fe3e_8489_4ac3_b48d_0909b895497d
ELIN-622490-2016 | EL-349687-2016 | 8/3/2016 11:38:26 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Main distribution panel is not in a weatherproof lockable enclosure. 120/240 Volt, 200 Amp. This can cause equipment damage from the environment due to building not completely framed up. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Distribution_panel_panel_exposed_to_weather_.png | file://x:/photopub/docs/0000000465/69519789-e720-432d-a885-a91073cf0cae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b10e8914_13ee_47d2_aba4_0e484c6ec0e0
ELIN-622484-2016 | EL-413846-2016 | 8/3/2016 3:07:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Service conductor cable at the meter base and at the main distribution is not properly secured and protected from mechanical damage. This is a mechanical damage condition. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Consumer_service_conductors_not_properly_secured_and_protected_from_mechanical_protection.png | file://x:/photopub/docs/0000000465/4a784ba0-6762-4163-9294-4fa2f865c01f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d10cb1c_f1df_43c0_a68d_53086f367e14
ELIN-622489-2016 | EL-419001-2016 | 8/3/2016 2:27:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Main distribution panel mounted in pump house building without a lockable door for the building. This can be accessible to unauthorized persons. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_distribution_panel_located_in_pump_house_building_without_a_lockable_door_.png | file://x:/photopub/docs/0000000465/1d1f3974-636c-407e-a3cd-a0c4e977bed3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f3bdedf_60f2_4588_9a91_412d494a6284
ELIN-625786-2016 | EL-418750-2016 | 8/16/2016 11:12:39 AM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | Receptacle exposed to weather requires an in-use type of weatherproof cover to prevent water from contacting live parts while a cord is plugged in to the receptacle. Water and energized electrical parts combine for potential shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Pole_mount_receptacle_with_incorrect_weatherproof_cover_installed.png | file://x:/photopub/docs/0000000471/a5656b6b-025c-4785-b340-f4489c48f3c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6cca68a1_b857_4d4d_966f_79e4ee5399a9
ELOP-571345-2016 | EL-383085-2016 | 7/20/2016 8:19:07 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Multiple shock and fire hazards. Conductors exposed to mechanical damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Cable_is_damaged.png | file://x:/photopub/docs/0000000456/1e7f72ef-9505-468b-a691-9478c883c34e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cb39958_8264_4306_823e_6a52c48444c8
ELOP-571345-2016 | EL-383085-2016 | 7/20/2016 8:19:07 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Multiple shock and fire hazards. Conductors exposed to mechanical damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Transformer_cable_mechanical_damage.png | file://x:/photopub/docs/0000000456/ca6131fb-ae75-4804-97d5-c2395c3770ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cb39958_8264_4306_823e_6a52c48444c8
ELOP-571345-2016 | EL-383085-2016 | 7/20/2016 8:19:07 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Multiple shock and fire hazards. Conductors exposed to mechanical damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | AC90_across_doorway.png | file://x:/photopub/docs/0000000456/af78e265-cb3f-4e30-bc78-63e268d64c52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cb39958_8264_4306_823e_6a52c48444c8
ELOP-571345-2016 | EL-383085-2016 | 7/20/2016 8:19:07 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Multiple shock and fire hazards. Conductors exposed to mechanical damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Panel_not_accessible.png | file://x:/photopub/docs/0000000456/5ad1c830-51bf-46f0-baba-3b74d7f6df75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cb39958_8264_4306_823e_6a52c48444c8
ELOP-571345-2016 | EL-383085-2016 | 7/20/2016 8:19:07 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Multiple shock and fire hazards. Conductors exposed to mechanical damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | AC90_not_terminated_.png | file://x:/photopub/docs/0000000456/c5f308d8-c77a-4eba-a369-78eb9edf0940.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cb39958_8264_4306_823e_6a52c48444c8
ELOP-571345-2016 | EL-383085-2016 | 7/20/2016 8:19:07 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Multiple shock and fire hazards. Conductors exposed to mechanical damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Receptacle_not_mounted.png | file://x:/photopub/docs/0000000456/54ee9c90-3952-4234-bc05-753f80460a8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cb39958_8264_4306_823e_6a52c48444c8
ELOP-571345-2016 | EL-383085-2016 | 7/20/2016 8:19:07 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Multiple shock and fire hazards. Conductors exposed to mechanical damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Conductors_not_supported.png | file://x:/photopub/docs/0000000456/35b46c1b-57a1-422b-aa8d-02de047fd5d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cb39958_8264_4306_823e_6a52c48444c8
ELOP-571345-2016 | EL-383085-2016 | 7/20/2016 8:19:07 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Multiple shock and fire hazards. Conductors exposed to mechanical damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | AC90_exposed_to_weather.png | file://x:/photopub/docs/0000000456/68a5dd15-08a7-4e6d-9493-ab52a985c5fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cb39958_8264_4306_823e_6a52c48444c8
ELOP-571345-2016 | EL-383085-2016 | 7/20/2016 8:19:07 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Multiple shock and fire hazards. Conductors exposed to mechanical damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | TECK_cable_used_for_flexible_cable.png | file://x:/photopub/docs/0000000456/0401b909-f0ff-4e7b-91ba-a322623f23ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cb39958_8264_4306_823e_6a52c48444c8
GAIN-640063-2016 | GA-420069-2016 | 8/30/2016 12:45:19 PM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | All gas piping over 2 inches must be welded because threaded connections over 2 inch or prone to leak overtime this would cause a gas leak the potentially cause a fire | 3 | Non-compliant material/fittings installed | 3_inch__3_inch_threaded_gas_fitting.png | file://x:/photopub/docs/0000000477/5d910fd5-2ca1-4f51-b9ea-4583f1a48df8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29363e88_e646_46d4_8f1d_5969ed20ebd5
ELOP-585443-2016 | 5237 | 8/30/2016 4:05:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 |  | 1 | General Working space or dedicated space is being used for storage | Storage_Electrical_Room.png | file://x:/photopub/docs/0000000477/0513b56a-4fce-4c27-b58b-93eee4eb4c74.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6fe4149f_f23a_4087_a447_496547747dd5
ELIN-640668-2016 | EL-429659-2016 | 8/30/2016 2:50:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | A new service has been requested for energization, the 200A 120/240V Main Panel has been installed in the construction stage into a garage with no weather protection yet completed, the roof has not been completed. This could result in damage to the electrical equipment and a shock hazard to persons. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_Panel.png | file://x:/photopub/docs/0000000477/6908e00f-e575-485b-9a29-d6f70f69b7f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b57112d7_4654_4025_8628_a3d773d26bf2
BPVOP-640238-2016 | 2270776 | 8/30/2016 3:49:30 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP065 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | 4 | 4 | During the inspection of a Hot Water Boiler with MAWP of 140 psig a leak from 1mm pinhole was found. | 4 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | Leaking_shell.png | file://x:/photopub/docs/0000000477/20c147c3-9840-40d0-8f62-1fdd543cf3f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1c5b8bf_58bf_4d00_8c81_9134e3f2bdff
BPVOP-640238-2016 | 2270776 | 8/30/2016 3:49:30 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP065 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | 4 | 4 | During the inspection of a Hot Water Boiler with MAWP of 140 psig a leak from 1mm pinhole was found. | 4 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | Leaking_Boiler_Shell.png | file://x:/photopub/docs/0000000477/45844841-9240-4c68-aa0e-14833181a7a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1c5b8bf_58bf_4d00_8c81_9134e3f2bdff
ELIN-610792-2016 | EL-408456-2016 | 7/19/2016 9:19:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead service conductor support attachment device is located too high above consumer's service head on pole. When overhead service conductor support attachment device is located too high above consumer's service head then elements of weather such as moisture or water could possibly enter electrical equipment and could cause damage or become a possible electrical shock or fire hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 113.png | file://x:/photopub/docs/0000000458/e3cf39ad-d423-4fcc-b55f-ccf9b5f389b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__426f7ed5_b73a_4477_bd26_61ab8d951de3
ELIN-610792-2016 | EL-408456-2016 | 7/19/2016 9:19:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead service conductor support attachment device is located too high above consumer's service head on pole. When overhead service conductor support attachment device is located too high above consumer's service head then elements of weather such as moisture or water could possibly enter electrical equipment and could cause damage or become a possible electrical shock or fire hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 111.png | file://x:/photopub/docs/0000000458/1661aedc-828e-4ca3-be7c-c41d3ae871e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__426f7ed5_b73a_4477_bd26_61ab8d951de3
GAOP-623659-2016 | 2172141 | 8/10/2016 1:46:37 PM | ASSESS: GA OP: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | The uncapped gas pipe could leak large amounts of gas if the manual or electrically operated valves were turned on. The leaking gas could create a fire and explosion in the building. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Gas_turret_pipe_open.png | file://x:/photopub/docs/0000000470/3ce45dc8-3a26-43b5-9f9a-3e6695a0591e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15BEF8AB_FC0E_4F2E_8CB9_E3B36EC95064
GAWP-629556-2016 | GA-145075-2014 | 8/12/2016 8:58:11 AM | ASSESS: GA Work In Progress | png | #asFound | GA053 | Non-certified appliance connector | 3 | 3 | The stainless steel gas connector will flex each time the heater cycles on and off. After repeated cycles the stainless steel connector will break and leak gas. The leaking gas will create a fire hazard or explosion hazard. | 3 | Non-certified appliance connector | Wrong_gas_connector_.png | file://x:/photopub/docs/0000000470/7d4b1f0b-1782-4f07-8eb0-a9da7f779422.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7abf043b_cbfb_4dbf_9662_2db00a7c5582
GAOP-623659-2016 | 2172141 | 8/10/2016 1:46:37 PM | ASSESS: GA OP: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | The uncapped gas pipe could leak large amounts of gas if the manual or electrically operated valves were turned on. The leaking gas could create a fire and explosion in the building. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Uncapped_gas_turret_pipe_.png | file://x:/photopub/docs/0000000470/4c6de636-66ce-4257-bd78-e5bea26c6ddc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15BEF8AB_FC0E_4F2E_8CB9_E3B36EC95064
BPVOP-613021-2016 | 2264100 | 7/18/2016 4:51:58 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP190 | 5.1.0 In service proc/process - Overheated or damaged tubes | 4 | 4 | Boiler tubes must not have any cracks in them. I found boiler tube(s) on this high pressure steam boiler have developed cracks, most likely due to overheating. A potential for an incident exists due to poor condition of the boiler tube(s). | 4 | 5.1.0 In service proc/process - Overheated or damaged tubes | Crack.png | file://x:/photopub/docs/0000000457/eff62f34-7944-409e-9d88-76442cc635b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a359eff2_75a3_4297_9c70_ee8549435d43
BPVOP-640238-2016 | 2270776 | 8/30/2016 3:49:30 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP065 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | 4 | 4 | During the inspection of a Hot Water Boiler with MAWP of 140 psig a leak from 1mm pinhole was found. | 4 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | Pinhole.png | file://x:/photopub/docs/0000000477/d5181210-f57a-4f9c-a6be-b751cfbe961d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1c5b8bf_58bf_4d00_8c81_9134e3f2bdff
GAIN-599726-2016 | GA-349997-2016 | 7/6/2016 1:02:04 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | Exhaust vent installed too close to fresh air intake of Furnace. Fresh air intake can pull in combustion gases from exhaust and distribute combustion gases through home causing carbon monoxide poisoning to occupants | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Exhaust_too_close_to_air_supply_on_right.png | file://x:/photopub/docs/0000000452/8204e22e-e155-4a13-9287-1e4cf0ac115a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33946d47_7e4e_4982_a84b_aaecb1f38109
AMOP-636312-2016 | 2053221 | 8/23/2016 12:04:09 PM | ASSESS: AM OP: Operational | png | #asFound | AM018 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Heavy corrosion of the Waterslide and stair structure. | 2 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | SA_WS_pic1.png | file://x:/photopub/docs/0000000474/fb3f8055-1e9b-47d4-8fc3-0ac253432dae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a531cef_59e7_4e50_ba2f_7532f4f648d2
AMOP-636312-2016 | 2053221 | 8/23/2016 12:04:09 PM | ASSESS: AM OP: Operational | png | #asFound | AM018 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Heavy corrosion of the Waterslide and stair structure. | 2 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | SA_WS_pic3.png | file://x:/photopub/docs/0000000474/386f274f-626d-427b-8d42-a07219b76cc9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a531cef_59e7_4e50_ba2f_7532f4f648d2
AMOP-636312-2016 | 2053221 | 8/23/2016 12:04:09 PM | ASSESS: AM OP: Operational | png | #asFound | AM018 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Heavy corrosion of the Waterslide and stair structure. | 2 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | SA_WS_pic2.png | file://x:/photopub/docs/0000000474/dd1b099f-e6d6-4141-b115-65e1679c2129.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a531cef_59e7_4e50_ba2f_7532f4f648d2
ELIN-602663-2016 | EL-327765-2015 | 7/15/2016 7:05:47 AM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | At final inspection of a new single family dwelling it was noted that a kitchen counter space measuring 350 mm located between the range and the kitchen sink had not been provided with a kitchen counter receptacle. Occupants using electrical appliances may resort to the use of extension cords which can be damaged by proximity to heating elements, water, and other hazards. This can result in damage to property or injury to persons | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 350_mm_counter_between_range_and_sink_no_receptacle.png | file://x:/photopub/docs/0000000456/2cbb4f45-cb2c-4407-9645-738f0127c384.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e148f30_f2c8_4c61_b125_c14dea1f9ddd
ELIN-612882-2016 | UW-412166-2016 | 7/15/2016 3:13:17 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Terminations for lighting equipment are not made in approved boxes, exposed connections are susceptible to having the wire nut loosen and fall off. Exposed termination ends of wiring pose a risk of shock and fire to persons and property. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Lighting_not_spliced_in_a_box.png | file://x:/photopub/docs/0000000456/64097639-7609-48da-8135-d9029f74c081.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f569bfc_b920_4421_8799_7ac1643e44ba
ELOP-492520-2015 | 5866 | 7/20/2016 11:57:17 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL138 | Installation of electrical equipment General: boxes are not accessible. | 3 | 3 | Junction boxes are required to be accessible. This is a fire hazard as there is no access if the connections were to become loose/corroded or damaged. | 3 | Installation of electrical equipment General: boxes are not accessible. | B.png | file://x:/photopub/docs/0000000459/89d73729-abc7-4f49-afa6-fe9b32fe3fdc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6903b1b_f7ac_441b_a4e3_1fe78f571dce
ELOP-461838-2015 | 5865 | 7/20/2016 12:25:33 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Metal gas and water lines are required to be bonded. This poses a shock hazard if the lines become accidentally energized the over current device won't trip. | 3 | Equipment Gas line, cast or water pipe has not been bonded | C.png | file://x:/photopub/docs/0000000459/7280d238-eb24-411d-ba89-fcb5f01f9e93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1562c6df_f632_4871_b5e9_b5894db6230e
ELOP-461838-2015 | 5865 | 7/20/2016 12:25:33 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Metal gas and water lines are required to be bonded. This poses a shock hazard if the lines become accidentally energized the over current device won't trip. | 3 | Equipment Gas line, cast or water pipe has not been bonded | D.png | file://x:/photopub/docs/0000000459/1bb5a587-04e6-4c60-ab39-cfbbd3f97516.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1562c6df_f632_4871_b5e9_b5894db6230e
ELOP-461835-2015 | 5857 | 7/20/2016 10:49:48 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | A.png | file://x:/photopub/docs/0000000459/ee0c34ea-5060-4724-9033-a171d33858a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2629c91_689f_4944_be39_206fbfe0002e
ELIN-603000-2016 | EL-353221-2016 | 7/6/2016 1:10:41 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumer service cabling exceeds 1.5m of unprotected portion inside structure before terminating in an overcurrent device. This poses a serious risk of personal injury (shock) or property damage (thermal event) due to mechanical damage to unprotected portions of cabling. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View01_consumer_service_raceway.png | file://x:/photopub/docs/0000000453/8c911333-74a6-4c95-9232-6268d8945b6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01a22432_6f8d_4bc9_876d_95336fee893d
ELIN-604608-2016 | EL-387070-2016 | 7/7/2016 12:06:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumer service cabling exceeds 1.5m of unprotected portion inside structure before terminating in an overcurrent device. This poses a serious risk of personal injury (shock) or property damage (thermal event) due to mechanical damage to unprotected portions of cabling. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View01_suite__cabling.png | file://x:/photopub/docs/0000000453/d15ae487-cb4c-434d-aff2-33f4beef02e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1db2a46_278b_4446_b534_02cca565d5e9
ELIN-603002-2016 | EL-353223-2016 | 7/6/2016 12:56:17 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumer service cabling exceeds 1.5m of unprotected portion inside structure before terminating in an overcurrent device. This poses a serious risk of personal injury (shock) or property damage (thermal event) due to mechanical damage to unprotected portions of cabling. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View01_suite_cabling.png | file://x:/photopub/docs/0000000453/033818b3-3c2b-40db-8e72-7f3918195fde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7623569a_a062_41cb_a1c0_09717bea6408
BPVIN-641392-2016 | BPV-429087-2016 | 9/7/2016 12:41:05 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP184 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | 3 | 3 | All flammables and combustibles materials should be properly stored. Found combustibles(wood 2x4's) behind the boiler. This could result in a boiler room fire. | 3 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | Behind_DHWB.png | file://x:/photopub/docs/0000000482/8b22a7ae-1b5f-4c50-af6f-ba69ba1973be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4e74ff0_7e44_425d_b955_2e45b5813443
BPVOP-645205-2016 | 2299778 | 9/8/2016 9:29:47 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP046 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness and the vessel has to be de-rated | 4 | 4 | The 2012 Ultrasonic Testing of air receiver (1.78m long and .51m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, determined that vessel shell has corroded externally 0.070-0.080". This extent it requires repair to restore to original condition or recalculation to determine MAWP. | 4 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness and the vessel has to be de-rated | NDE_Report.png | file://x:/photopub/docs/0000000482/a150fccb-5dc7-4cf5-8e7c-01805a371fb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd0272e2_98ae_4eb6_bf9f_e6d5c96dc61b
ELIN-644491-2016 | EL-422552-2016 | 9/6/2016 12:21:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | The service conduit is not bonded with the use of a bond bushing. During fault conditions large fault currents can damage the service panel or create a shock hazard until the over current device opens. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Service_entrance_.png | file://x:/photopub/docs/0000000480/cb15a9f7-ead9-44d6-aa07-456020f9f785.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21205207_e356_48b1_9f9d_bc3e29ca5b3c
ELIN-629182-2016 | EL-380678-2016 | 8/11/2016 11:48:14 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Non metallic sheathed cable has been installed on service pole for future light, cable has not been terminated in an approved box , but left coiled in an energized state. Splices, joints and terminations of non metallic sheathed cable are required to be made in an approved box. Energized conductors pose a risk of shock and fire to persons and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Armoured_cable_not_terminated_in_box.png | file://x:/photopub/docs/0000000469/cbb31ae0-1f59-433f-b07e-d2480b240495.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3408b450_c87c_420c_8ff2_f83c80495764
GAOP-623709-2016 | 2171725 | 8/26/2016 10:14:57 AM | ASSESS: GA OP: Periodic | png | #asFound | GA162 | Defective appliance accessory or component with imminent risk of injury or property damage | 5 | 5 | Mounting for burner is badly damaged from heat. There is a concern that the burner will become loose, causing flame impingement or flame being moved to outside of the combustion chamber | 5 | Defective appliance accessory or component with imminent risk of injury or property damage | Burner_mount2.png | file://x:/photopub/docs/0000000476/050967f2-3cf9-4f36-8fcb-d0509d77896f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54A713AB_3AA6_455F_B282_A9D21047F37E
GAOP-623709-2016 | 2171725 | 8/26/2016 10:14:57 AM | ASSESS: GA OP: Periodic | png | #asFound | GA162 | Defective appliance accessory or component with imminent risk of injury or property damage | 5 | 5 | Mounting for burner is badly damaged from heat. There is a concern that the burner will become loose, causing flame impingement or flame being moved to outside of the combustion chamber | 5 | Defective appliance accessory or component with imminent risk of injury or property damage | Burner_mount.png | file://x:/photopub/docs/0000000476/600cf586-d6b4-449d-bc59-a4dbef3b15b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54A713AB_3AA6_455F_B282_A9D21047F37E
EDMA-638010-2016 | ED-256234-2015 | 8/18/2016 9:57:31 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED033 | Operating control installed contrary to the manufacturer instructions and/ or applicable Standards Contractor is not aware Risk Reg ED-02 | 3 | 3 | The elevator car door is to apply a maximum of 30 lbs force on the door edge when closing. It was found during an acceptance inspection the door operator was incorrectly adjusted and applied in excess of 30 lbs of force on the door edge when closing. This closing force will likely injure a person standing in the way of the closing car door edge. It was found the elevator contractor was aware of the situation and failed to make the proper adjustments to the door operator. This 4 stop traction elevator is located in an existing commercial building. | 3 | Operating control installed contrary to the manufacturer instructions and/ or applicable Standards Contractor is not aware Risk Reg ED-02 | Car_door.png | file://x:/photopub/docs/0000000476/48cecbe9-0afb-4cd2-9788-22d93899a0db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1454f3f_fb48_4636_9431_da5e880d5c5e
BPVOP-641932-2016 | 2298623 | 9/1/2016 11:12:54 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP184 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | 3 | 3 | During the external inspection of an air receiver with MAWP of 150 psig many combustibles were stored near or on top of the receiver. | 3 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | Combustibles__.png | file://x:/photopub/docs/0000000479/db760f7e-67e6-41d5-b7af-2c291533d1b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c31ec2a_3c8a_45c0_8fe7_ec964b2fc808
BPVOP-641932-2016 | 2298623 | 9/1/2016 11:12:54 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP184 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | 3 | 3 | During the external inspection of an air receiver with MAWP of 150 psig many combustibles were stored near or on top of the receiver. | 3 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | More_combustibles_.png | file://x:/photopub/docs/0000000479/171b92ec-d321-4075-a31c-c43a8244a94a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c31ec2a_3c8a_45c0_8fe7_ec964b2fc808
ELIN-636551-2016 | EL-398840-2016 | 8/24/2016 8:29:03 AM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Outdoor_location_dry_type_connector.png | file://x:/photopub/docs/0000000475/cb044998-ff95-462b-9c21-db7f6388b1f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__088904c8_1486_4ea5_b53b_aa1f05314678
ELIN-636551-2016 | EL-398840-2016 | 8/24/2016 8:29:03 AM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Bending_radius_exceeded.png | file://x:/photopub/docs/0000000475/c9dac7a3-4260-445c-90cd-2f20f990a652.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__088904c8_1486_4ea5_b53b_aa1f05314678
ELIN-636551-2016 | EL-398840-2016 | 8/24/2016 8:29:03 AM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Location_of_disconnect.png | file://x:/photopub/docs/0000000475/c90bdb42-d498-4b72-8224-4142a9ae2ab6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__088904c8_1486_4ea5_b53b_aa1f05314678
ELIN-636551-2016 | EL-398840-2016 | 8/24/2016 8:29:03 AM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Cable_run_without_support.png | file://x:/photopub/docs/0000000475/47de3c18-5d1b-469c-8e6a-5c1e5a0f4a9e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__088904c8_1486_4ea5_b53b_aa1f05314678
ELIN-636523-2016 | EL-427733-2016 | 8/24/2016 1:20:54 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | An existing 600 volt 100 amp irrigation service was damaged by a storm. The service was repaired but left accessible to the general public very close to a public entertainment venue. Injury to persons can occur when electrical equipment of this nature is not installed to restrict access to only qualified persons | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Open_to_public_not_lockable_600_volt_service_public_park_within_10_meters.png | file://x:/photopub/docs/0000000475/50720dca-8fd1-4ace-8d7f-232bbb1b023f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__807897ec_781c_45b2_9147_d8e7a2b1fa90
ELIN-630889-2016 | EL-383582-2016 | 8/24/2016 10:46:44 AM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | A dry location rated 200 amp 240 volt combination service panel has been installed outdoors in a homemade wooden enclosure. Wooden enclosures are not approved for protection of electrical equipment outdoors and can allow ingress of water into electrical equipment. They also deteriorate at unpredictable rates. Either condition can lead to potential failure of safety equipment and cause property damage or injury to persons. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Dry_location_panel_service_upgrade_in_homemade_wooden_.png | file://x:/photopub/docs/0000000475/743deb28-b73a-42a0-a25d-02ca7c78827c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__80ee7b08_b8cd_4402_9e3b_5e62f234ba43
BPVIN-605090-2016 | BPV-359905-2016 | 7/6/2016 10:22:47 AM | ASSESS: BPV IN: Construction REF/PV | png | #asFound | BP025 | 1.0.2 Clearances/Maintenance - Failed visual welding inspection. | 3 | 3 | The visual inspection of 2 welds in new ammonia piping failed due to undercut and voids. I was repaired next day. | 3 | 1.0.2 Clearances/Maintenance - Failed visual welding inspection. | Porosity.png | file://x:/photopub/docs/0000000453/77ac63ae-1226-4f9d-aafe-e577638da39b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7df5576f_8798_483b_b150_33891f24099b
BPVIN-605090-2016 | BPV-359905-2016 | 7/6/2016 10:22:47 AM | ASSESS: BPV IN: Construction REF/PV | png | #asFound | BP025 | 1.0.2 Clearances/Maintenance - Failed visual welding inspection. | 3 | 3 | The visual inspection of 2 welds in new ammonia piping failed due to undercut and voids. I was repaired next day. | 3 | 1.0.2 Clearances/Maintenance - Failed visual welding inspection. | Undercut.png | file://x:/photopub/docs/0000000453/618abed0-cde3-4f96-aac1-b682c07a30ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7df5576f_8798_483b_b150_33891f24099b
BPVOP-638832-2016 | 2266408 | 7/5/2016 2:03:53 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 4 | Welded joints or shell may fail due to repetitive loading and/or corrosion. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Overall_View.png | file://x:/photopub/docs/0000000475/a1a7f6a5-f978-4387-bb29-564b88bcf551.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6a1630a_cc2a_48f7_a1c1_88113a05d91a
BPVOP-638832-2016 | 2266408 | 7/5/2016 2:03:53 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 4 | Welded joints or shell may fail due to repetitive loading and/or corrosion. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | ASME_Nameplate.png | file://x:/photopub/docs/0000000475/4c599a98-b68a-4aad-bcf1-ed78afcaa0a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6a1630a_cc2a_48f7_a1c1_88113a05d91a
GAIN-633405-2016 | GA-422008-2016 | 8/25/2016 11:28:07 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | Vent connector over 8" must be min 24 gauge. Too light of vent connector could result in failure causing fire and flue products entering occupied space | 3 | Unapproved venting material | 26_gauge_vent.png | file://x:/photopub/docs/0000000477/9bee483d-b8d3-4f12-b369-f1f8f7bc98b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfa59c56_a598_4961_a349_2a391fd3a614
ELIN-601438-2016 | EL-391758-2016 | 7/5/2016 11:36:21 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 2 | A homeowner had installed branch circuit breakers at the time of the rough wiring assessment. No arc fault breakers, nor any other form of arc fault protection for the receptacle circuits had been provided. This presents a fire hazard should arcing occur in these circuits. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_AFCI_branch_circuit_protection_for_receptacle_circuits.png | file://x:/photopub/docs/0000000451/ecb3d8c9-8a20-4614-980d-65df48a1bc62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a4bef8b_2984_4871_9ff4_1c4269f7cb7f
ELIN-639210-2016 | UW-429069-2016 | 8/26/2016 3:05:26 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Multiple locations throughout facility have had protective covers removed from panel's, junction box's and electrical equipment to accommodate moving of wires. Covers not installed, expose energized terminals, conductors, and bussing. Exposed equipment is in a restricted area not accessible to the public if left in this manner, wiring would pose a risk of fire and shock to persons and property. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Open_electrical_equipment_.png | file://x:/photopub/docs/0000000476/22c26cbb-58e1-483e-b3fd-6b5591312d88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c544498_3fa5_4fb6_ae53_f3c45bbb5cb3
ELIN-596651-2016 | EL-399127-2016 | 6/27/2016 2:13:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 2 | Outdoor mounted sewage lift equip rent operating at 30 amps 240 volt is mounted as a permanent installation outdoors on plywood. Treated plywood has been de,on strayed to be unreliable and deteriorates at unpredictable rates. This can leave electrical equipment loose and cause damage to equipment, property or injury to persons. | 3 | General Equipment is not approved for the specific use | Electrical_equipment_mounted_to_plywood_outdoors.png | file://x:/photopub/docs/0000000449/8fd8d84d-6771-4cee-9914-15519ba5e555.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ead8769b_1ea9_4a22_9f61_6dae58a9b02e
BPVIN-643353-2016 | BPV-426305-2016 | 9/2/2016 1:23:25 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Boiler_Nameplate_data.png | file://x:/photopub/docs/0000000480/13460a02-d226-4f65-9634-88f2a141839f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef56f09f_f9be_4986_83d1_ba4ed204be98
BPVIN-643353-2016 | BPV-426305-2016 | 9/2/2016 1:23:25 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Pressure_relief_valves_nameplate_data.png | file://x:/photopub/docs/0000000480/387a40b6-fa00-4542-8b3f-a61d39577feb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef56f09f_f9be_4986_83d1_ba4ed204be98
GAUP-635908-2016 | UW-427445-2016 | 8/26/2016 5:36:17 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | ISC found open and dispenser unattended, shut down on tank jammed, and ISC in open position. In the event of a leak, propane could be released when unattended. | 4 | Missing mandatory safety controls | Isc.png | file://x:/photopub/docs/0000000476/5c84a16d-28d8-421b-9009-92312ea76db0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08a5d5cf_9d20_4ca3_8268_5ccd585b9759
ELIN-602458-2016 | EL-401498-2016 | 6/28/2016 12:28:15 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | In an existing agricultural facility, the 15amp 120volt lighting cabtyre cables are permanent fixed to the structure. This could lead to a thermal effect. | 4 | Conductors, Misuse of flexible cords. | Flexible_wiring_permanent_connected.png | file://x:/photopub/docs/0000000450/a27c2ca0-3f31-4412-91d1-05d9f76d457f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4dc950b7_c9aa_4d9a_bdcf_8800d1e3a3d8
BPVOP-604229-2016 | 2291938 | 8/24/2016 4:13:13 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | The safety valve capacities on this glycol hot water boiler are lower than the minimum required as listed on the nameplate. This may not allow the safety valves to provide adequate relief in the event of an overpressure situation which may result in an incident. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | H-303_NP_PRD_Min_requirement.png | file://x:/photopub/docs/0000000476/84966ddc-dcd3-4117-bebc-8994312231d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1B059B63_47E2_412F_A1DB_301E9DD9507F
ELIN-631416-2016 | EL-377533-2016 | 8/19/2016 9:16:13 AM | ASSESS: EL: Final | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | 17 amps on a 15 amp breaker. | 3 | Protection and control Loading of distribution equipment exceeded | Meter_reading.png | file://x:/photopub/docs/0000000473/8ea36ded-7cb4-408a-bb69-1b21f0e441e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65357255_c6b6_4baa_ab60_ccc27574f02c
BPVOP-592515-2016 | 2279159 | 7/28/2016 1:22:40 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | No evidence of regular maintenance on this machine-mounted air receiver. Broken pressure indicator dials. Safety Valve appears damaged. Air receiver tank is more than 20 years old. Compliance with Safety Order required; failure to do so may result in an incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | machine_mounted_air_receiver_unplugged_no_lockout.png | file://x:/photopub/docs/0000000466/b319ac6e-77f9-4826-b156-8f8891fb11ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__36a5a43d_05b0_4307_83ce_962a2c0a25a5
BPVOP-592515-2016 | 2279159 | 7/28/2016 1:22:40 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | No evidence of regular maintenance on this machine-mounted air receiver. Broken pressure indicator dials. Safety Valve appears damaged. Air receiver tank is more than 20 years old. Compliance with Safety Order required; failure to do so may result in an incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_relief_key_ring_damaged.png | file://x:/photopub/docs/0000000466/08266072-9d7f-4757-b28b-3fb78853c5a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__36a5a43d_05b0_4307_83ce_962a2c0a25a5
BPVOP-592515-2016 | 2279159 | 7/28/2016 1:22:40 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | No evidence of regular maintenance on this machine-mounted air receiver. Broken pressure indicator dials. Safety Valve appears damaged. Air receiver tank is more than 20 years old. Compliance with Safety Order required; failure to do so may result in an incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Note_posted_on_air_receiver_breaker_panel.png | file://x:/photopub/docs/0000000466/9e76eac1-4193-4754-af9c-239582d81ba4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__36a5a43d_05b0_4307_83ce_962a2c0a25a5
BPVOP-592515-2016 | 2279159 | 7/28/2016 1:22:40 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | No evidence of regular maintenance on this machine-mounted air receiver. Broken pressure indicator dials. Safety Valve appears damaged. Air receiver tank is more than 20 years old. Compliance with Safety Order required; failure to do so may result in an incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | No_lockout_photo2.png | file://x:/photopub/docs/0000000466/2bcf7125-5ff9-4e06-a58d-599c977cf582.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__36a5a43d_05b0_4307_83ce_962a2c0a25a5
ELIN-633500-2016 | EL-381745-2016 | 8/18/2016 12:05:34 PM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Various non-compliances including but not limited to over sized over current protection supplying sub panel. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Lark.png | file://x:/photopub/docs/0000000472/03c7cdec-9e2f-482c-8847-d6e30cf738e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c52eb452_d810_4249_9139_d47b8cb449e9
ELIN-614056-2016 | EL-406658-2016 | 7/20/2016 11:21:53 AM | ASSESS: EL: Service Connection | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 4 | A new 200 amp 240 volt residential service has been interconnected to a separate service at an adjacent building. No permit was obtained and no authorization submitted. Persons can be injured where temporary power is interconnected with permanent installations and in only rare circumstances is special permission to do this granted. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | New_service_unsafely_energized.png | file://x:/photopub/docs/0000000459/78b7041c-9fb9-4f7f-a744-994e8e185e4c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf55a2c3_2839_4852_84fd_2ec288a12a60
ELIN-612128-2016 | EL-411687-2016 | 7/21/2016 7:15:26 AM | ASSESS: EL: Service Connection | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | A new commercial 200 amp 240 volt 1 phase service panel has been temporarily energized by interconnecting the new separate service main panel to a different source of supply. The service had been authorized for connection to the utility at this time. Permanent installations are to be constructed separately from temporary power, and when done this way can lead to injury to electrical workers and equipment due to potential back feed, and unwary workers that are unable to determine that equipment is energized | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Flexible_feeder_into_existing_separate_service_then_enters_new_main_panel_separate_service_to_main_breaker.png | file://x:/photopub/docs/0000000459/c1d39294-3e12-4031-90d2-467119561b52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f23f1ca7_04c4_476a_8595_e730367bf513
ELIN-644437-2016 | EL-433652-2016 | 9/8/2016 3:06:22 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 2x 200 amp 120/240 volt services are not properly protected from weather and damage protection. This is both a shock and equipment damage issue | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_816-1.png | file://x:/photopub/docs/0000000482/2f87e070-0677-44e7-8fbf-3c269fdd4916.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__876e0192_6fc7_4105_990f_5d61c85426aa
ELIN-644437-2016 | EL-433652-2016 | 9/8/2016 3:06:22 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 2x 200 amp 120/240 volt services are not properly protected from weather and damage protection. This is both a shock and equipment damage issue | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_818-2.png | file://x:/photopub/docs/0000000482/ebc59f55-3344-47a0-ae1c-d6bb06652f36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__876e0192_6fc7_4105_990f_5d61c85426aa
ELIN-644437-2016 | EL-433652-2016 | 9/8/2016 3:06:22 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 2x 200 amp 120/240 volt services are not properly protected from weather and damage protection. This is both a shock and equipment damage issue | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_818-1.png | file://x:/photopub/docs/0000000482/0d70ba18-944d-4e78-86d8-a281c2507733.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__876e0192_6fc7_4105_990f_5d61c85426aa
ELIN-644437-2016 | EL-433652-2016 | 9/8/2016 3:06:22 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 2x 200 amp 120/240 volt services are not properly protected from weather and damage protection. This is both a shock and equipment damage issue | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_816-2.png | file://x:/photopub/docs/0000000482/f62145e3-5533-4de0-8768-e8d004c22d01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__876e0192_6fc7_4105_990f_5d61c85426aa
GAUP-600844-2016 | UW-402385-2016 | 6/28/2016 11:37:05 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | Appliance air intake was less than 10 feet from regulator relief opening. | 3 | insufficient mechanical air intake clearance to gas regulator relief | Appliance_air_intake.png | file://x:/photopub/docs/0000000449/a4b407c5-6440-40a3-bf61-ca9e2659a4e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ef20967_825f_42f0_86ab_be368a5a61a2
ELIN-626695-2016 | EL-175384-2014 | 8/9/2016 12:32:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 2 | The raceway for the service conductors entering the building are required to be adequately bonded. In this installation of an overhead service, the conduit from the meter base to the service disconnect switch did not have a bonding bushing installed. This could result in a shock hazard if the metal became energized and did not have a good path to ground. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | No_Ground_Bushing_on_Service_Raceway_.png | file://x:/photopub/docs/0000000468/6b36cd4f-928a-4e49-b919-099ed9d497a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9963ef0a_6186_4d96_bea9_aa90263e3acd
ELIN-618992-2016 | EL-409698-2016 | 8/2/2016 2:59:50 PM | ASSESS: EL: Final | png | #asFound | EL039 | Equipment is not marked / identified Multiple service boxes not marked. | 2 | 3 | Interactive photovoltaic system. Breaker feeding panel is not labelled or suitably marked, this is a shock hazard as an individual may not realize the panel is being back fed by the solar system. | 2 | Equipment is not marked / identified Multiple service boxes not marked. | A.png | file://x:/photopub/docs/0000000464/f4f5dfb4-f4c8-4678-ae0c-3479fb327f46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee1ef035_489b_431b_b09d_5a478e3d61dc
ELIN-606340-2016 | EL-249208-2015 | 8/5/2016 11:16:30 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeder cabling subject to mechanical damage due to manner in which it had been installed. This poses are serious risk of personal injury (shock) and property damage (thermal event/ interface fire). | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | View04_feeder.png | file://x:/photopub/docs/0000000466/b670ad28-5783-4431-8282-6a12395c94e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__778252a2_4f7c_4c0f_9096_4500c4cb89f9
ELIN-606340-2016 | EL-249208-2015 | 8/5/2016 11:16:30 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeder cabling subject to mechanical damage due to manner in which it had been installed. This poses are serious risk of personal injury (shock) and property damage (thermal event/ interface fire). | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | View02_feeder_.png | file://x:/photopub/docs/0000000466/437de9cd-c2a0-4601-8874-5f2efd64f622.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__778252a2_4f7c_4c0f_9096_4500c4cb89f9
ELIN-606340-2016 | EL-249208-2015 | 8/5/2016 11:16:30 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeder cabling subject to mechanical damage due to manner in which it had been installed. This poses are serious risk of personal injury (shock) and property damage (thermal event/ interface fire). | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | View03_feeder.png | file://x:/photopub/docs/0000000466/140a8eb7-b49d-434d-bc5c-22ad94f5192f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__778252a2_4f7c_4c0f_9096_4500c4cb89f9
ELIN-606340-2016 | EL-249208-2015 | 8/5/2016 11:16:30 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeder cabling subject to mechanical damage due to manner in which it had been installed. This poses are serious risk of personal injury (shock) and property damage (thermal event/ interface fire). | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | View01_vertical_run_.png | file://x:/photopub/docs/0000000466/24985ea4-d325-4070-a739-efd6e6712241.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__778252a2_4f7c_4c0f_9096_4500c4cb89f9
GAOP-511855-2016 | GRP-335582-2016 | 8/29/2016 10:48:24 AM | ASSESS: Propane PV Operating: Periodic | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 2 | Minor gas leak found and isolated | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Propane_tank_paint_.png | file://x:/photopub/docs/0000000477/12a2b74d-ffe0-468a-9132-b9e03439f662.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a46972b_877c_4ef2_a37d_d8158e51c0e6
GAOP-511855-2016 | GRP-335582-2016 | 8/29/2016 10:48:24 AM | ASSESS: Propane PV Operating: Periodic | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 2 | Minor gas leak found and isolated | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Relief_valve_and_rain_cap.png | file://x:/photopub/docs/0000000477/63cf915e-ff3f-4b92-b6a6-2067d367c969.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a46972b_877c_4ef2_a37d_d8158e51c0e6
GAOP-511855-2016 | GRP-335582-2016 | 8/29/2016 10:48:24 AM | ASSESS: Propane PV Operating: Periodic | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 2 | Minor gas leak found and isolated | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Propane_Leak_detected.png | file://x:/photopub/docs/0000000477/2bfb6869-9086-48ef-b39d-516d0ddfaa7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a46972b_877c_4ef2_a37d_d8158e51c0e6
BPVIN-628526-2016 | BPV-422764-2016 | 8/10/2016 12:17:05 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for pressure relief valves on an air receiver mounted with a machine for the last 10 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_valve_.png | file://x:/photopub/docs/0000000468/1c646587-a1ac-4e49-adfe-d498be8fb29b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bffe60b_ea42_41ea_8fe8_9314851c39c4
BPVIN-628526-2016 | BPV-422764-2016 | 8/10/2016 12:17:05 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for pressure relief valves on an air receiver mounted with a machine for the last 10 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Air_compressor.png | file://x:/photopub/docs/0000000468/baa42836-7c02-4a70-90eb-a3b744448c9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bffe60b_ea42_41ea_8fe8_9314851c39c4
ELIN-628749-2016 | EL-417705-2016 | 8/11/2016 12:17:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 4 | 15 amp, 120 volt ground fault receptacle has a 20 amp overcurrent device protecting it. This is a thermal issue. | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | 1772_main_distribution.png | file://x:/photopub/docs/0000000469/79dad5a4-cc36-4a57-bec7-1cd1773d62b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a219dcf9_3bf4_47f4_b9bc_6ba3de835ed3
BPVOP-621894-2016 | 2273576 | 8/2/2016 9:34:45 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon the assessment of a Ammonia Receiver with MAWP of 250 psig, was found that the PRD was installed in July 2010 and was overdue as per CSA B52. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Overdue_PRD.png | file://x:/photopub/docs/0000000464/cc827a12-0b50-4a54-bb79-01155487a1f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9ca08cb_64e1_4b0c_a396_a22fc6e4a9d0
ELIN-624856-2016 | EL-417409-2016 | 8/9/2016 3:23:33 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Consumer service pole has deteriorated base and not adequately supported for length of secondary overhead conductors from utility supply. This poses a serious risk of personal injury (shock) or property damage (thermal event/interface fire) due to infrastructure failure. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | View02_service_pole.png | file://x:/photopub/docs/0000000468/5288c949-e9b3-49c2-974f-3053776a7438.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12c9db6e_e75a_4ee0_9eaf_a6d5f4772ec2
ELIN-624856-2016 | EL-417409-2016 | 8/9/2016 3:23:33 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Consumer service pole has deteriorated base and not adequately supported for length of secondary overhead conductors from utility supply. This poses a serious risk of personal injury (shock) or property damage (thermal event/interface fire) due to infrastructure failure. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Detail03_service_pole_base.png | file://x:/photopub/docs/0000000468/08ea0dc5-1fe8-43a8-95aa-c7254f81d564.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12c9db6e_e75a_4ee0_9eaf_a6d5f4772ec2
ELIN-624856-2016 | EL-417409-2016 | 8/9/2016 3:23:33 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Consumer service pole has deteriorated base and not adequately supported for length of secondary overhead conductors from utility supply. This poses a serious risk of personal injury (shock) or property damage (thermal event/interface fire) due to infrastructure failure. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | View01_service_pole.png | file://x:/photopub/docs/0000000468/44516959-5ec2-4335-9c19-aedfadd27992.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12c9db6e_e75a_4ee0_9eaf_a6d5f4772ec2
GAOP-615427-2016 | GA-414135-2016 | 8/26/2016 9:24:11 AM | ASSESS: GA OP: Periodic | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | Uncapped gas line on liquid line from propane tank in a building. If the unapproved gate valve was to fail, there would be dangerous amounts of liquid propane released and if it found an ignition source would cause fire or possible explosion. | 5 | Open gas line connected to fuel supply (no cap/plug) | No_ISC_valve.png | file://x:/photopub/docs/0000000478/7e4137b4-c1eb-4f9a-a4d7-05b277d3bad3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__775a91dd_af35_4666_8667_f9f248b161fc
GAOP-200081-2014 | 2170702 | 8/31/2016 11:12:42 AM | ASSESS: GA OP: Periodic | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Hose could become damaged and leak, leading to possible fire or explosion. | 3 | Non-compliant material/fittings installed | Hose1.png | file://x:/photopub/docs/0000000478/65dff816-59d5-46e4-8a85-9238427aba32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f71c5170_c72c_4aff_9e03_b9acae28f648
BPVOP-583665-2016 | 2273575 | 8/2/2016 12:04:54 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP149 | 4.1.1 Incorrect readings/alarms - Refrigerant vapour detector out of calibration | 3 | 3 | During the inspection of an Ammonia refrigeration system with 146 KW prime mover rating and 1000 lbs charge was found that the leak detector system was out of calibration. | 3 | 4.1.1 Incorrect readings/alarms - Refrigerant vapour detector out of calibration | Leak_detector_.png | file://x:/photopub/docs/0000000464/ce99dce6-2162-4fa2-8c06-a2c614711722.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8cf512b1_8004_44ca_8112_599a5c012003
BPVOP-621896-2016 | 2301381 | 8/2/2016 10:49:12 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon the assessment of a Ammonia Chiller with MAWP of 200 psig, the PRD's were overdue as per CSA B52. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRDs.png | file://x:/photopub/docs/0000000464/5d10f049-d3c9-4573-bdb6-a9b742a6e513.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__549ef40f_82fe_4776_a3ca_3c8063462c2c
ELIN-624884-2016 | EL-419272-2016 | 8/9/2016 7:59:13 AM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #6 Ground conductor from the grounding electrode has been terminated at a bonding lug in the Meterbase instead of at the neutral point in the main switch. This could result in a shock hazard or equipment damage has the proper grounding path has not been established. Overcurrent devices such as breakers may also fail to operate as intended. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Ground.png | file://x:/photopub/docs/0000000468/06514781-c499-49c9-9c46-4a7f7a544a4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fdad7d17_4925_47e7_a94d_cfece07946b8
ELIN-602997-2016 | EL-353219-2016 | 7/7/2016 6:34:55 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumer service cabling exceeds 1.5m of unprotected portion inside structure before terminating in an overcurrent device. This poses a serious risk of personal injury (shock) or property damage (thermal event) due to mechanical damage to unprotected portions of cabling. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View01_service_cabling.png | file://x:/photopub/docs/0000000453/b1d8fc40-8b96-4b41-8db9-1bdafbf102bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96ea087a_9e18_4e8f_bbf1_13c58dacbb75
GAIN-638833-2016 | GA-428566-2016 | 9/6/2016 1:31:57 PM | ASSESS: GA: Final | png | #asFound | GA117 | Non compliant system ex: incorrect appliance connection, incorrect glue/ fasteners | 2 | 2 | Combustion air not installed as per manufacturers installation instructions. Low spot in piping arrangement allows for moisture to accumulate which could obstruct the combustion air supply. | 2 | Non compliant system ex: incorrect appliance connection, incorrect glue/ fasteners | Combustion_air_piping_with_low_spot_for_moisture_to_accumulate_.png | file://x:/photopub/docs/0000000481/41e08e5b-ba62-40f5-99b3-806f5ee76166.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfb89128_dc01_4186_a127_623dd6ee32df
ELIN-603625-2016 | EL-234501-2015 | 7/21/2016 5:51:04 PM | ASSESS: EL: Final | png | #asFound | EL197 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no PPE in place. | 5 | 5 | Certified individual observed performing regulated work to energized consumer supply service metering equipment without PPE, procedures in place and prior authorization from utility. This presented a serious and immediate hazard to certified individual and assistant on site of personal injury (shock) or catastrophic property damage (thermal event/interface fire). | 5 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no PPE in place. | View02_energized_supply_transformer.png | file://x:/photopub/docs/0000000460/83aefa31-6edf-4afe-a36f-a10336af364c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__afdad9f3_25f1_4820_9427_26872e4b9e25
BPOP-635724-2016 | BPV-334080-2016 | 8/30/2016 8:41:14 AM | ASSESS: Propane PV: Periodic | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 2 | Valve has excesses maximum servicing interval. Valve may fail to open in over pressure condition. Vessel rupture could occur. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Viper_1000.png | file://x:/photopub/docs/0000000477/5bac76c1-2e7f-4c7c-b3af-9d2fd881d1f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c13082e8_e37e_4e0f_828a_dce63cf4f02e
BPOP-635724-2016 | BPV-334080-2016 | 8/30/2016 8:41:14 AM | ASSESS: Propane PV: Periodic | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 2 | Valve has excesses maximum servicing interval. Valve may fail to open in over pressure condition. Vessel rupture could occur. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Viper_1000_rating.png | file://x:/photopub/docs/0000000477/6cd3b455-be6e-4e99-8f53-0d7da9f32fbb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c13082e8_e37e_4e0f_828a_dce63cf4f02e
ELIN-623207-2016 | EL-011029-2013 | 8/5/2016 12:36:44 PM | ASSESS: EL: Final | png | #asFound | EL133 | Installation of electrical equipment General: improper polarity at receptacle. | 3 | 3 | When the polarity is reversed the circuitry is electrically charged all the time, this potentially could become a shock hazard. | 3 | Installation of electrical equipment General: improper polarity at receptacle. | Reverse_polarity__.png | file://x:/photopub/docs/0000000467/05ff47a1-9800-4eae-b9ff-24cf48373991.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c23817a1_d133_4c8a_a52a_9dda5e421dce
GAIN-628973-2016 | GA-416833-2016 | 8/15/2016 11:28:17 AM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | A certified connector connected to unsupported piping. Piping or tubing must be supported to prevent damage when appliances are moved. | 2 | Physical protection of piping and tubing absent. | Connector_connected_to_unsupported_piping.png | file://x:/photopub/docs/0000000470/f0ac830b-e859-4e51-abe8-bdd069dfd43a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0fcb39c3_a775_40e3_87af_b327e0e9f76f
GAIN-628804-2016 | GA-399465-2016 | 8/16/2016 11:21:55 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | Sidewall venting termination not installed as per installation instructions. Clearance to combustible material not met when installation instructions not followed. | 2 | Side wall vent termination not compliant with installation instructions | Sidewall_venting_termination_not_installed_as_per_installation_instructions.png | file://x:/photopub/docs/0000000471/e42c3415-95f8-49d7-a3ff-df1090c0e1ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58215c1e_fa27_4339_ad27_6e85f09cd595
ELIN-629636-2016 | EL-419479-2016 | 8/29/2016 10:45:23 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Service neutral conductors are required to be bonded (connected) to the service box enclosure. This is required to provide a bonding path back to the source of the service to allow over current devices to operate and prevent metal equipment from becoming energized. This installation of a 100A 120\240V service to an existing mobile home does not have the service neutral bonded to the enclosure as required. Left uncorrected this is a potential shock hazard if a fault on the system energizes the metal parts of the electrical service equipment and the branch circuits and equipment connected to it. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Service_neutral_bonding_screw_is_missing.png | file://x:/photopub/docs/0000000476/849f4166-a6be-4c37-a224-29acbc4d0062.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e6cd573_facb_491e_b427_cf72ee8706f5
ELIN-629636-2016 | EL-419479-2016 | 8/29/2016 10:45:23 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Service neutral conductors are required to be bonded (connected) to the service box enclosure. This is required to provide a bonding path back to the source of the service to allow over current devices to operate and prevent metal equipment from becoming energized. This installation of a 100A 120\240V service to an existing mobile home does not have the service neutral bonded to the enclosure as required. Left uncorrected this is a potential shock hazard if a fault on the system energizes the metal parts of the electrical service equipment and the branch circuits and equipment connected to it. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Exterior_of_mobile_home_.png | file://x:/photopub/docs/0000000476/ce6affa6-0d59-42d5-ab26-e694912174dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e6cd573_facb_491e_b427_cf72ee8706f5
ELIN-629636-2016 | EL-419479-2016 | 8/29/2016 10:45:23 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Service neutral conductors are required to be bonded (connected) to the service box enclosure. This is required to provide a bonding path back to the source of the service to allow over current devices to operate and prevent metal equipment from becoming energized. This installation of a 100A 120\240V service to an existing mobile home does not have the service neutral bonded to the enclosure as required. Left uncorrected this is a potential shock hazard if a fault on the system energizes the metal parts of the electrical service equipment and the branch circuits and equipment connected to it. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Interior_of_service_panel.png | file://x:/photopub/docs/0000000476/4b141de4-d970-4341-8a69-e1105df639ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e6cd573_facb_491e_b427_cf72ee8706f5
ELIN-629636-2016 | EL-419479-2016 | 8/29/2016 10:45:23 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Service neutral conductors are required to be bonded (connected) to the service box enclosure. This is required to provide a bonding path back to the source of the service to allow over current devices to operate and prevent metal equipment from becoming energized. This installation of a 100A 120\240V service to an existing mobile home does not have the service neutral bonded to the enclosure as required. Left uncorrected this is a potential shock hazard if a fault on the system energizes the metal parts of the electrical service equipment and the branch circuits and equipment connected to it. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Exterior_of_mobile_home__.png | file://x:/photopub/docs/0000000476/e6e684f9-c249-4615-814a-7b284a75d671.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e6cd573_facb_491e_b427_cf72ee8706f5
GAWP-659504-2016 | GA-375324-2016 | 9/11/2016 11:12:59 AM | ASSESS: GA Work In Progress | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Steel gas riser installed in concrete sidewalk | 2 | Physical protection of piping and tubing absent. | 2.png | file://x:/photopub/docs/0000000483/92926a9d-f756-425f-a060-c1df47234206.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b570613c_6e31_4eec_9dc0_1f5bf8a58631
ELIN-648358-2016 | EL-382332-2016 | 9/9/2016 1:37:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL191 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | 3 | 4 | 120/240 volt circuits under breakers and some circuits energized and not labelled: inadvertant energizing of circuits can lead to shock hazards. | 3 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | B4_access.png | file://x:/photopub/docs/0000000483/74e19170-9da9-4758-920f-70ad23725885.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f2cb5b8_7f3b_4bc5_b0b7_5895d1372c78
ELIN-648358-2016 | EL-382332-2016 | 9/9/2016 1:37:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL191 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | 3 | 4 | 120/240 volt circuits under breakers and some circuits energized and not labelled: inadvertant energizing of circuits can lead to shock hazards. | 3 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | B3.png | file://x:/photopub/docs/0000000483/d4b27c0d-e98a-465d-8730-a73f38c74844.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f2cb5b8_7f3b_4bc5_b0b7_5895d1372c78
ELIN-648358-2016 | EL-382332-2016 | 9/9/2016 1:37:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL191 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | 3 | 4 | 120/240 volt circuits under breakers and some circuits energized and not labelled: inadvertant energizing of circuits can lead to shock hazards. | 3 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | B5.png | file://x:/photopub/docs/0000000483/ac1cb351-3870-45fd-9e16-10e361a0d6f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f2cb5b8_7f3b_4bc5_b0b7_5895d1372c78
ELIN-648358-2016 | EL-382332-2016 | 9/9/2016 1:37:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL191 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | 3 | 4 | 120/240 volt circuits under breakers and some circuits energized and not labelled: inadvertant energizing of circuits can lead to shock hazards. | 3 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | B6.png | file://x:/photopub/docs/0000000483/df36a22d-ae5a-4d15-b013-05d0bd411599.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f2cb5b8_7f3b_4bc5_b0b7_5895d1372c78
ELIN-648358-2016 | EL-382332-2016 | 9/9/2016 1:37:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL191 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | 3 | 4 | 120/240 volt circuits under breakers and some circuits energized and not labelled: inadvertant energizing of circuits can lead to shock hazards. | 3 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | Brent1.png | file://x:/photopub/docs/0000000483/2ad1587f-607b-4017-bd6a-1e8039dc0aaa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f2cb5b8_7f3b_4bc5_b0b7_5895d1372c78
ELIN-648358-2016 | EL-382332-2016 | 9/9/2016 1:37:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL191 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | 3 | 4 | 120/240 volt circuits under breakers and some circuits energized and not labelled: inadvertant energizing of circuits can lead to shock hazards. | 3 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | B2.png | file://x:/photopub/docs/0000000483/e0e9243e-a74c-4f4e-a971-a43067e825ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f2cb5b8_7f3b_4bc5_b0b7_5895d1372c78
ELIN-603317-2016 | EL-279577-2015 | 7/8/2016 12:31:12 PM | ASSESS: EL: Final | png | #asFound | EL125 | Installation of electrical equipment Covers or canopies - metal coverplate is not recessed from receptacle. | 4 | 4 | 15 amp, 120 volt general use receptacle missing finishing faceplate. This is a shock hazard. | 4 | Installation of electrical equipment Covers or canopies - metal coverplate is not recessed from receptacle. | Missing_faceplate.png | file://x:/photopub/docs/0000000453/43f6eb2b-1453-442f-a26e-3db2e2b3fc55.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac16fdc1_51a8_4d67_ae6b_5d5216ae2cf3
ELIN-612713-2016 | EL-347428-2016 | 7/22/2016 4:11:59 PM | ASSESS: EL: Service Connection | png | #asFound | EL038 | Number of supply or consumer's services has been exceeded Number of Consumer services have been exceeded. | 3 | 2 | Found two dwelling unit residential house has main 120/240 volt 200 amp consumer's service panelboard located in a garage which is not a common area of the house so that all occupants in the house have access at all times without permission to access main service breaker. When main service is not sub-divided and main breaker above is not fully accessible by all occupants at all times as required by code, there are risk of hazards in the event an electrical shock or fire fault condition happens if all occupants don't have access to main breaker to turn of breakers. | 3 | Number of supply or consumer's services has been exceeded Number of Consumer services have been exceeded. | 2.png | file://x:/photopub/docs/0000000461/d77eb9e2-39ea-48a2-b5cb-419aac09835b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__274b2ec8_7107_4b71_924b_bc2f3b4880dc
ELIN-612713-2016 | EL-347428-2016 | 7/22/2016 4:11:59 PM | ASSESS: EL: Service Connection | png | #asFound | EL038 | Number of supply or consumer's services has been exceeded Number of Consumer services have been exceeded. | 3 | 2 | Found two dwelling unit residential house has main 120/240 volt 200 amp consumer's service panelboard located in a garage which is not a common area of the house so that all occupants in the house have access at all times without permission to access main service breaker. When main service is not sub-divided and main breaker above is not fully accessible by all occupants at all times as required by code, there are risk of hazards in the event an electrical shock or fire fault condition happens if all occupants don't have access to main breaker to turn of breakers. | 3 | Number of supply or consumer's services has been exceeded Number of Consumer services have been exceeded. | 3.png | file://x:/photopub/docs/0000000461/bbe88c15-4fb7-4ed6-b3e2-4b3826265fac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__274b2ec8_7107_4b71_924b_bc2f3b4880dc
ELIN-612713-2016 | EL-347428-2016 | 7/22/2016 4:11:59 PM | ASSESS: EL: Service Connection | png | #asFound | EL038 | Number of supply or consumer's services has been exceeded Number of Consumer services have been exceeded. | 3 | 2 | Found two dwelling unit residential house has main 120/240 volt 200 amp consumer's service panelboard located in a garage which is not a common area of the house so that all occupants in the house have access at all times without permission to access main service breaker. When main service is not sub-divided and main breaker above is not fully accessible by all occupants at all times as required by code, there are risk of hazards in the event an electrical shock or fire fault condition happens if all occupants don't have access to main breaker to turn of breakers. | 3 | Number of supply or consumer's services has been exceeded Number of Consumer services have been exceeded. | 1.png | file://x:/photopub/docs/0000000461/947a934c-5a26-409e-a778-0c89a9b527c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__274b2ec8_7107_4b71_924b_bc2f3b4880dc
GAIN-634068-2016 | GA-278085-2015 | 8/19/2016 11:31:13 AM | ASSESS: GA: Commissioning Approval | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | CPVC potable water pipe is not approved for boiler vent material. The use of the incorrect vent material could lead to vent failure and products of combustion entering the occupied area of the building. | 3 | Unapproved venting material | Wrong_vent_material_.png | file://x:/photopub/docs/0000000475/5f78e080-b4a4-481b-b8f8-7fb925df20b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e54903ad_df7c_4973_921f_c1333cb66794
GAIN-634068-2016 | GA-278085-2015 | 8/19/2016 11:31:13 AM | ASSESS: GA: Commissioning Approval | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | CPVC potable water pipe is not approved for boiler vent material. The use of the incorrect vent material could lead to vent failure and products of combustion entering the occupied area of the building. | 3 | Unapproved venting material | Wrong_vent_material_used.png | file://x:/photopub/docs/0000000475/b891c558-31db-4d50-a032-9eac3aa1d6f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e54903ad_df7c_4973_921f_c1333cb66794
GAIN-635401-2016 | GA-427098-2016 | 8/31/2016 1:17:36 PM | ASSESS: GA: Final | png | #asFound | GA096 | Supports in place but not in compliance with certified instructions | 1 | 1 | Unsupported vertical venting from outlet of furnace. | 1 | Supports in place but not in compliance with certified instructions | Unsupported_venting.png | file://x:/photopub/docs/0000000478/cd2e507b-d9dd-4555-9a83-138d7e50f8aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e3d3cd8_c2a0_4da9_9f8c_27287bf37942
ELIN-602834-2016 | EL-226852-2015 | 7/12/2016 8:49:54 AM | ASSESS: EL: Final | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | Sewer pump leads are subject to mechanical damage. This could be a hazard to persons/property if the leads of the sewer pump were to be damaged. Persons could get shocked if they were exposed to a live wire. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Mechanical_protection_is_needed.png | file://x:/photopub/docs/0000000455/b0a52ab4-0f5a-44ef-9697-d257d7e57bd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ec95f6d_4fcc_463a_b55b_e13207c738b7
ELIN-639553-2016 | EL-394882-2016 | 8/29/2016 1:05:24 PM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Attachment_point.png | file://x:/photopub/docs/0000000477/24e36797-5fe9-49a6-9a95-575c2f19aa6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b690d4e2_5f7d_4282_b4f8_59b4c846a9c6
ELIN-639553-2016 | EL-394882-2016 | 8/29/2016 1:05:24 PM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | New_200A_panel.png | file://x:/photopub/docs/0000000477/1f997b84-aa26-4de3-b391-65df8bef8293.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b690d4e2_5f7d_4282_b4f8_59b4c846a9c6
ELIN-639553-2016 | EL-394882-2016 | 8/29/2016 1:05:24 PM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Panel_location.png | file://x:/photopub/docs/0000000477/879d4a93-d521-4e59-a59a-721b308417a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b690d4e2_5f7d_4282_b4f8_59b4c846a9c6
ELIN-604473-2016 | EL-403760-2016 | 7/7/2016 9:40:33 AM | ASSESS: EL: Final | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | Branch circuit entering the main breaker compartment for service conductors. 240 Volt. 30 Amp. This is an equipment damage condition. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Branch_circuit_for_A_C_unit_entering_main_service_conductor_compartment.png | file://x:/photopub/docs/0000000453/610541dd-ee3f-4eb7-8967-9c9b9222a138.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91a232e7_f2b3_4148_9f19_c74bd81e9b7d
ELIN-639319-2016 | EL-429082-2016 | 8/31/2016 12:36:30 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | This assessment found an indoor fixture installed on the exterior of the building. Water accumulating in the fixture poses a shock and fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Fixture.png | file://x:/photopub/docs/0000000478/862da3f4-ace6-424a-af3e-0dedee0fecc4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658c2c0a_12cd_4248_ba07_402e590d8343
ELIN-639319-2016 | EL-429082-2016 | 8/31/2016 12:36:30 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | This assessment found an indoor fixture installed on the exterior of the building. Water accumulating in the fixture poses a shock and fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Flex_bare_conductor.png | file://x:/photopub/docs/0000000478/8d6689e7-3198-4fc2-bd07-2fb445b4ebd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658c2c0a_12cd_4248_ba07_402e590d8343
ELIN-639319-2016 | EL-429082-2016 | 8/31/2016 12:36:30 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | This assessment found an indoor fixture installed on the exterior of the building. Water accumulating in the fixture poses a shock and fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Shed_wiring.png | file://x:/photopub/docs/0000000478/b3d46b25-0604-4860-a09e-8e7f59233da4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658c2c0a_12cd_4248_ba07_402e590d8343
ELIN-630392-2016 | EL-423250-2016 | 8/13/2016 6:55:40 AM | ASSESS: EL: Final | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Found 120 volt branch circuits bonding conductor not terminated properly under bonding screws as required for properly bonding electrical equipment. When electrical equipment is not properly and effectively bonded as required by code and if there is a short circuit or fault condition then over-current devices might not effectively operate or trip immediately and could pose an electrical fire or shock hazard to people or property. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 102.png | file://x:/photopub/docs/0000000470/834bf117-5a2f-4226-8dee-3eabd84d8b66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49dc3f93_67f7_4e94_aa06_5abce61beb85
ELIN-630392-2016 | EL-423250-2016 | 8/13/2016 6:55:40 AM | ASSESS: EL: Final | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Found 120 volt branch circuits bonding conductor not terminated properly under bonding screws as required for properly bonding electrical equipment. When electrical equipment is not properly and effectively bonded as required by code and if there is a short circuit or fault condition then over-current devices might not effectively operate or trip immediately and could pose an electrical fire or shock hazard to people or property. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 105.png | file://x:/photopub/docs/0000000470/350b5255-10f3-4a06-bcbc-48a9327e4d45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49dc3f93_67f7_4e94_aa06_5abce61beb85
ELIN-630392-2016 | EL-423250-2016 | 8/13/2016 6:55:40 AM | ASSESS: EL: Final | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Found 120 volt branch circuits bonding conductor not terminated properly under bonding screws as required for properly bonding electrical equipment. When electrical equipment is not properly and effectively bonded as required by code and if there is a short circuit or fault condition then over-current devices might not effectively operate or trip immediately and could pose an electrical fire or shock hazard to people or property. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 103.png | file://x:/photopub/docs/0000000470/7f902433-4095-485a-8958-d0012ad8fa1e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49dc3f93_67f7_4e94_aa06_5abce61beb85
ELIN-618595-2016 | EL-416115-2016 | 8/10/2016 5:08:58 PM | ASSESS: EL: Service Connection | png | #asFound | EL049 | Protection and control Interrupt ratings are not adequate for the installation | 4 | 4 | At a new construction site, a 200amp 120/240volt construction service is found with no main Overcurrent device present. This can lead to A thermal effect. Pic attached. | 4 | Protection and control Interrupt ratings are not adequate for the installation | Loadcentre_with_no_main_breaker.png | file://x:/photopub/docs/0000000469/5cd1afed-8b85-47a0-ada4-45d7e75b1867.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc48c5cf_c68e_4012_beb1_f94b2c05a820
611381-2016 | ED-112511-2014 | 7/7/2016 | ASSESS: ED IN: Construction Use | png | #asFound | ED057 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 2 | 2 | Tripping hazards at landings | 2 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | Uneven_floor.png | file://x:/photopub/docs/0000000463/54040cb1-e919-4d55-9342-ca4562cb4904.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58cc651d_4166_4181_93e1_3492b944e1f2
ELIN-630392-2016 | EL-423250-2016 | 8/13/2016 6:55:40 AM | ASSESS: EL: Final | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Found 120 volt branch circuits bonding conductor not terminated properly under bonding screws as required for properly bonding electrical equipment. When electrical equipment is not properly and effectively bonded as required by code and if there is a short circuit or fault condition then over-current devices might not effectively operate or trip immediately and could pose an electrical fire or shock hazard to people or property. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 104.png | file://x:/photopub/docs/0000000470/3593d57e-8c08-4f37-8194-161b89015003.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49dc3f93_67f7_4e94_aa06_5abce61beb85
ELIN-630392-2016 | EL-423250-2016 | 8/13/2016 6:55:40 AM | ASSESS: EL: Final | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Found 120 volt branch circuits bonding conductor not terminated properly under bonding screws as required for properly bonding electrical equipment. When electrical equipment is not properly and effectively bonded as required by code and if there is a short circuit or fault condition then over-current devices might not effectively operate or trip immediately and could pose an electrical fire or shock hazard to people or property. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 101.png | file://x:/photopub/docs/0000000470/7963c741-d6e7-48c4-991f-0e39f9ffd3ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49dc3f93_67f7_4e94_aa06_5abce61beb85
ELIN-607083-2016 | EL-379985-2016 | 7/8/2016 9:46:00 AM | ASSESS: EL: Service Connection | png | #asFound | EL109 | Conductors Identified conductor or neutral conductor has not been properly identified | 1 | 1 | The identified conductor ( neutral) is identified the incorrect colour. | 1 | Conductors Identified conductor or neutral conductor has not been properly identified | Identified_conductor_marking.png | file://x:/photopub/docs/0000000453/847a4628-0944-4494-b593-b4fa6b6cf303.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee539ff7_703f_4f76_b333_0bd1ffa9f0f6
BPVIN-619452-2016 | BPV-416863-2016 | 7/28/2016 9:33:53 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP123 | 3.1.1 Safeties will not function - Pressure Relief Device Safety relief valve removed or bypassed | 5 | 5 | All pressure retaining equipment shall have pressure relief device in order to protect the equipment from overpressure and damage. I found no pressure relief device on this high pressure air receiver (125PSI). A potential exists for an overpressure incident. | 5 | 3.1.1 Safeties will not function - Pressure Relief Device Safety relief valve removed or bypassed | NO_PRESSURE_RELIEF_DEVICE_.png | file://x:/photopub/docs/0000000463/2bd1441f-9f01-4c1e-8deb-419059617b14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__507ccbe5_0318_41e2_9ae7_f5bbb58291cd
ELIN-609319-2016 | UW-409377-2016 | 7/11/2016 2:11:12 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Regulated work being performed without the required permits, exposed energized equipment. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Loose_wiring1.png | file://x:/photopub/docs/0000000454/2a4ac904-2368-4316-a2ff-006a8587469d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48866eb0_c2e0_4b9a_94c1_9dca1066d1f0
ELIN-609319-2016 | UW-409377-2016 | 7/11/2016 2:11:12 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Regulated work being performed without the required permits, exposed energized equipment. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Main_service.png | file://x:/photopub/docs/0000000454/de7b270b-a612-4174-85da-0a3606c4d78c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48866eb0_c2e0_4b9a_94c1_9dca1066d1f0
ELIN-609319-2016 | UW-409377-2016 | 7/11/2016 2:11:12 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Regulated work being performed without the required permits, exposed energized equipment. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Kitchen_reno.png | file://x:/photopub/docs/0000000454/e061963a-49ee-4586-9e1a-fe01971e953a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48866eb0_c2e0_4b9a_94c1_9dca1066d1f0
ELIN-631506-2016 | EL-423071-2016 | 8/16/2016 2:11:38 PM | ASSESS: EL: Service Connection | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | No receptacles provided for use by sub trades results in unauthorized temporary wiring into panel board. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Panel_with_no_temp_plugs.png | file://x:/photopub/docs/0000000471/5611c1d7-09f2-45d6-befc-b46803472fc7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2f9cd75_4dc5_476d_a134_c39c7d3c0de7
ELIN-600796-2016 | EL-389654-2016 | 8/19/2016 9:01:58 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | The hazard is if the cover was to be left open as a result of a cord being left in, the water would eventually deteriorate the receptacle. This could cause thermal or shock hazards. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Outside_receptacle__.png | file://x:/photopub/docs/0000000473/4f08f60b-9d35-4e17-a790-0a3c6a449164.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0dd1e7f_256b_44ac_8f7a_f1f73b2d1813
GAUP-602246-2016 | UW-403390-2016 | 7/6/2016 8:38:54 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA134 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | 2 | 2 |  | 2 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | Open_junction_box_.png | file://x:/photopub/docs/0000000458/b7c576a6-ab89-44db-9242-2342a1764f95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79a7d350_3d5b_43cc_86a2_0da5f51735bb
ELIN-630312-2016 | EL-422370-2016 | 8/16/2016 11:56:20 AM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Service conductors cross over roofline and grounding for service is connected to the bond of the meter base. Potential for shock. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Ground_conductor_connected_to_bond_on_meter_base.png | file://x:/photopub/docs/0000000471/6c846dbe-3174-48d4-abcf-1fe5ab08aa4c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad7c69b3_b394_491e_89ba_be8a04cb108c
ELIN-630312-2016 | EL-422370-2016 | 8/16/2016 11:56:20 AM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Service conductors cross over roofline and grounding for service is connected to the bond of the meter base. Potential for shock. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Service_conductors_will_cross_over_roofline.png | file://x:/photopub/docs/0000000471/d4b8a20f-ee9d-4061-a39a-3941d92937f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad7c69b3_b394_491e_89ba_be8a04cb108c
BPVIN-632690-2016 | BPV-425382-2016 | 8/17/2016 12:19:34 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP002 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | 5 | 5 | The name plate of every boiler and pressure vessel shall be stamped in accordance with the requirements of the appropriate section of the American Society of Mechanical Engineers Code. The stamping shall include the Canadian Registration Number, identification traceable to the manufacture and design characteristics. I found no stamping or certification markings on eight unfired pressure vessels. Potential exists for an incident due to design limits being unknown. | 5 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | Head_material_.png | file://x:/photopub/docs/0000000472/21c723ba-bc45-4363-8cd2-af1921a7b3ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e2695e9_f773_48c8_b2cd_b7065a5eab9f
ELHE-607433-2016 | HE-408489-2016 | 7/12/2016 1:32:04 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Pedestrian clearance to overhead service conductors | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Overhead_service__conductors.png | file://x:/photopub/docs/0000000455/70c76ec4-134d-451c-a1c3-89945b8f8f8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93f19e9f_c57b_4b1a_97f3_fe6b3cc4a86d
BPVOP-525545-2016 | 2295613 | 7/12/2016 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | Safety devices protect the boiler from unsafe conditions. I found that one of the safety devices was not functioning on this high pressure steam boiler (150 PSI). Potential exists for an incident because required safety device is not in order. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Lwco_.png | file://x:/photopub/docs/0000000455/e856cab1-7e4f-4aa5-96f5-5049814a359a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7dc19f6_5ab5_4727_941d_dc2ff634bee5
GAIN-609362-2016 | GA-408835-2016 | 8/16/2016 2:50:47 PM | ASSESS: GA: Final | png | #asFound | GA062 | Piping/tubing hose installed in a corrosive/hazardous location | 4 | 4 | Commercial appliance hose installed in a hazardous location. Hose can be damaged by heat when installed with in clearance to combustible area of an appliance causing damage and possible uncontrolled release of gas. | 4 | Piping/tubing hose installed in a corrosive/hazardous location | Damaged_appliance_connector_hose_due_to_installation_in_clearance_to_combustible_area_of_appliance_.png | file://x:/photopub/docs/0000000471/f19bfcce-ef44-4a35-b69f-0ce66c975b93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59103e8b_609d_4ddc_8924_67fa64c6b318
ELIN-609601-2016 | EL-406952-2016 | 7/14/2016 10:55:20 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 200 amp, 120/240 volt main distribution panel designed for indoor conditions is installed were maybe subject to outdoor environments. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_distribution_enclosure.png | file://x:/photopub/docs/0000000456/5867d704-6e69-4dc5-964b-4eb672068f67.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e39f9a1f_a18f_40e2_8f74_0911bd8c84c3
ELIN-611415-2016 | EL-386858-2016 | 7/14/2016 10:18:32 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | 125 amp, 120/240 volt service ampacity exceeds the ampacity of the service conductors. This is a thermal issue. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Size_of_conductor.png | file://x:/photopub/docs/0000000456/18ea3cff-80e4-4e8a-9dd8-9049d7eb2c51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e3186483_9d21_4fb8_bcd3_859dd199a47b
GAOP-615427-2016 | GA-414135-2016 | 8/26/2016 9:24:11 AM | ASSESS: GA OP: Periodic | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | Uncapped gas line on liquid line from propane tank in a building. If the unapproved gate valve was to fail, there would be dangerous amounts of liquid propane released and if it found an ignition source would cause fire or possible explosion. | 5 | Open gas line connected to fuel supply (no cap/plug) | Uncapped_gas_line.png | file://x:/photopub/docs/0000000478/3b4d42be-4d1d-485c-a306-d7063ef85cbc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__775a91dd_af35_4666_8667_f9f248b161fc
GAOP-200111-2014 | 5265056 | 8/31/2016 10:26:35 AM | ASSESS: GA OP: Periodic | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Liquid propane lines must be such 80. Sch 40 pipe and fittings risk the chance of failure causing leaks and possible fire. | 3 | Non-compliant material/fittings installed | Piping.png | file://x:/photopub/docs/0000000478/26ac4f15-b3fb-4c16-9719-5725d99d439d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ad9d434_7df3_4c62_aa87_aaeeb590bbad
GAOP-200111-2014 | 5265056 | 8/31/2016 10:26:35 AM | ASSESS: GA OP: Periodic | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Liquid propane lines must be such 80. Sch 40 pipe and fittings risk the chance of failure causing leaks and possible fire. | 3 | Non-compliant material/fittings installed | Hose.png | file://x:/photopub/docs/0000000478/e139f648-e426-40b7-89c5-ca215ddef009.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ad9d434_7df3_4c62_aa87_aaeeb590bbad
ELIN-643370-2016 | EL-414491-2016 | 9/9/2016 11:16:00 AM | ASSESS: EL: Service Connection | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Not_WP.png | file://x:/photopub/docs/0000000482/8c6a1a75-f66e-4431-89f1-eedffdd1a251.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17ea81a4_d31e_4b10_8aed_7eb96d8197ae
GAIN-618676-2016 | GA-416165-2016 | 7/29/2016 1:47:45 PM | ASSESS: GA: Rough-In | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | Concentric vent terminations are too close together for vent on a different plane. Could cause recirculation of flue products causing incomplete combustion and fouling of heat exchanger | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_term.png | file://x:/photopub/docs/0000000464/86990446-5f02-4c37-9a42-e352a6b480c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__436c90a0_342c_4935_bf35_7a7c73d1f865
GAIN-619345-2016 | GA-232862-2015 | 7/27/2016 | ASSESS: GA: Rough-In | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Non-compliant Poly gas transition fitting used as riser leaves plastic gas line exposed which could be subject to damage, causing leak and possible fire. | 3 | Non-compliant material/fittings installed | Trans_Ftg.png | file://x:/photopub/docs/0000000464/be7bd4ea-7984-4d42-8f38-9d23a9d998dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28826bff_2684_4fd2_aec7_5f184350c5a5
ELIN-645651-2016 | UW-434331-2016 | 9/7/2016 2:46:19 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | 8c #12awg shielded cable on a 30A breaker used to feed a 100 amp sub panel. The cable is terminated in parallel. This is a fire hazard. Electrical code only permits parallel runs of cable in sizes 1/0 and larger. The cable termination was loose upon examination, this is because th lugs were not rated for parallel number 12 awg conductors. There were hot spots developing because of this condition. There was also a 3c #8 NMD90 installed under the main lugs that fed a 100A sub panel. This is also a hazard as the lugs are not rated for this purpose. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | B.png | file://x:/photopub/docs/0000000481/4c57122d-a964-499e-b396-4641ff5526f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70b8d7c8_bf08_4278_9f15_19e207f53f9f
ELIN-645651-2016 | UW-434331-2016 | 9/7/2016 2:46:19 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | 8c #12awg shielded cable on a 30A breaker used to feed a 100 amp sub panel. The cable is terminated in parallel. This is a fire hazard. Electrical code only permits parallel runs of cable in sizes 1/0 and larger. The cable termination was loose upon examination, this is because th lugs were not rated for parallel number 12 awg conductors. There were hot spots developing because of this condition. There was also a 3c #8 NMD90 installed under the main lugs that fed a 100A sub panel. This is also a hazard as the lugs are not rated for this purpose. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | C.png | file://x:/photopub/docs/0000000481/f56e6d93-7ebc-4f45-975d-fe02a3a5cd95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70b8d7c8_bf08_4278_9f15_19e207f53f9f
ELIN-645651-2016 | UW-434331-2016 | 9/7/2016 2:46:19 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | 8c #12awg shielded cable on a 30A breaker used to feed a 100 amp sub panel. The cable is terminated in parallel. This is a fire hazard. Electrical code only permits parallel runs of cable in sizes 1/0 and larger. The cable termination was loose upon examination, this is because th lugs were not rated for parallel number 12 awg conductors. There were hot spots developing because of this condition. There was also a 3c #8 NMD90 installed under the main lugs that fed a 100A sub panel. This is also a hazard as the lugs are not rated for this purpose. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | A.png | file://x:/photopub/docs/0000000481/0aea3f34-63cc-4573-b558-ab0b6fd308c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70b8d7c8_bf08_4278_9f15_19e207f53f9f
GAHE-641724-2016 | HE-430735-2016 | 8/31/2016 12:08:37 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA154 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | 5 | 5 | The hazard was created by improperly installed equipment and a extreme lack of maintenance. This led to the burner rolling out of the combustion chamber and spilling products of combustion including carbon monoxide in to the staff work area. | 5 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | Dryer_burner_flame_roll_out.png | file://x:/photopub/docs/0000000478/6a107b5d-62b5-4f12-9f83-95e4e5d936b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ffa13ab8_a408_4749_aa8b_111c8a6e62ea
GAHE-641724-2016 | HE-430735-2016 | 8/31/2016 12:08:37 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA154 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | 5 | 5 | The hazard was created by improperly installed equipment and a extreme lack of maintenance. This led to the burner rolling out of the combustion chamber and spilling products of combustion including carbon monoxide in to the staff work area. | 5 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | Piping_not_supported.png | file://x:/photopub/docs/0000000478/9e079479-adaa-484f-90b9-ea85183d570d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ffa13ab8_a408_4749_aa8b_111c8a6e62ea
GAHE-641724-2016 | HE-430735-2016 | 8/31/2016 12:08:37 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA154 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | 5 | 5 | The hazard was created by improperly installed equipment and a extreme lack of maintenance. This led to the burner rolling out of the combustion chamber and spilling products of combustion including carbon monoxide in to the staff work area. | 5 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | Dryer_duct_clearances_not_met_.png | file://x:/photopub/docs/0000000478/64c722e3-35b8-44b9-8b7f-2c69a850d1cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ffa13ab8_a408_4749_aa8b_111c8a6e62ea
GAHE-641724-2016 | HE-430735-2016 | 8/31/2016 12:08:37 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA154 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | 5 | 5 | The hazard was created by improperly installed equipment and a extreme lack of maintenance. This led to the burner rolling out of the combustion chamber and spilling products of combustion including carbon monoxide in to the staff work area. | 5 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | Dryer_duct_size_reduced.png | file://x:/photopub/docs/0000000478/9f69143a-e3ac-472c-a5a5-64b11a236cbd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ffa13ab8_a408_4749_aa8b_111c8a6e62ea
ELIN-604035-2016 | EL-406442-2016 | 8/17/2016 12:58:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | Service neutral conductors are required to be grounded at service boxes and bonded to the service enclosure. This is required to provide grounding and bonding for the electrical equipment in the event of a fault on the system. This is intended to protect persons from shock or electrocution, and to facilitate the operation of over current devices such as fuses and breakers. This installation of a temporary construction service mounted to a pole has a service neutral that is not grounded and bonded properly. Left uncorrected this is a potential shock and fire hazard if an electrical fault occurs with the equipment not properly grounded and bonded. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Neutral_bond_removed_and_grounding_conductor_terminated_onto_panel_enclosure.png | file://x:/photopub/docs/0000000472/26cb9b1f-4b62-46ac-80e5-b331a0094ba8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__519b4fc7_8646_40f3_a686_fa45d5a62d69
ELIN-604035-2016 | EL-406442-2016 | 8/17/2016 12:58:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | Service neutral conductors are required to be grounded at service boxes and bonded to the service enclosure. This is required to provide grounding and bonding for the electrical equipment in the event of a fault on the system. This is intended to protect persons from shock or electrocution, and to facilitate the operation of over current devices such as fuses and breakers. This installation of a temporary construction service mounted to a pole has a service neutral that is not grounded and bonded properly. Left uncorrected this is a potential shock and fire hazard if an electrical fault occurs with the equipment not properly grounded and bonded. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Temporary_construction_pole_service.png | file://x:/photopub/docs/0000000472/a8a5d55d-7697-4a75-a60d-37128d98cfde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__519b4fc7_8646_40f3_a686_fa45d5a62d69
GAOP-623622-2016 | GA-411163-2016 | 9/11/2016 8:57:43 AM | ASSESS: GA OP: Periodic | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | ISC operator not mounted, fuel supply open and return spring broken. In the event of a leak or pipe breakage uncontrolled propane could be released. | 4 | Missing mandatory safety controls | Isc.png | file://x:/photopub/docs/0000000483/7cef3e7c-862b-41e7-abd9-d0fb0c344d7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4769CCF3_D033_49BC_82A8_63931F860146
ELIN-610638-2016 | EL-389885-2016 | 7/18/2016 11:15:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | PVC conduits are required to terminate into threaded metal enclosures using female threaded PVC adapters together with metal conduit nipples. This is required because PVC expands and contracts at a different rate compared to metal. Movement between PVC and metal fittings can cause PVC fittings to crack, break, or pull out of metal fittings causing damage to the conduit and allowing water to enter electrical equipment. This installation of a new service on a residential property has a PVC service conduit terminated at the top of a meter base on a service pole. The PVC conduit is terminated using a PVC male adapter threaded into a female metal hub. Left uncorrected the male PVC adapter on the service conduit may crack, break, or pull apart allowing water to enter the meter base. Over time this may rust and corrode the conductor terminations inside the meter base posing a fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_pole.png | file://x:/photopub/docs/0000000457/b52b0d84-2127-4727-87be-4359e8f8140d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e9e5b2dd_1d6f_48fb_b891_a3567e7a10a4
ELIN-610638-2016 | EL-389885-2016 | 7/18/2016 11:15:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | PVC conduits are required to terminate into threaded metal enclosures using female threaded PVC adapters together with metal conduit nipples. This is required because PVC expands and contracts at a different rate compared to metal. Movement between PVC and metal fittings can cause PVC fittings to crack, break, or pull out of metal fittings causing damage to the conduit and allowing water to enter electrical equipment. This installation of a new service on a residential property has a PVC service conduit terminated at the top of a meter base on a service pole. The PVC conduit is terminated using a PVC male adapter threaded into a female metal hub. Left uncorrected the male PVC adapter on the service conduit may crack, break, or pull apart allowing water to enter the meter base. Over time this may rust and corrode the conductor terminations inside the meter base posing a fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_to_temporary_power_shed.png | file://x:/photopub/docs/0000000457/959fdeef-f76a-4a5f-a717-aa91f87b72d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e9e5b2dd_1d6f_48fb_b891_a3567e7a10a4
ELHE-610588-2016 | HE-410757-2016 | 7/15/2016 2:23:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | The 60 amp 120/240 volt service is pulled away from the pole and the main over current device cover is open exposing energized parts to the public in the vicinity. This is both a shock and equipment damage issue | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Service.png | file://x:/photopub/docs/0000000457/7b9c836f-baf1-45ec-b04b-bcc549f354c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6c161ea_3eeb_4c50_a911_7515f9da76d1
ELHE-610588-2016 | HE-410757-2016 | 7/15/2016 2:23:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | The 60 amp 120/240 volt service is pulled away from the pole and the main over current device cover is open exposing energized parts to the public in the vicinity. This is both a shock and equipment damage issue | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Service_disconnect_open_cover.png | file://x:/photopub/docs/0000000457/628be2e3-fdc1-4eff-86b9-302faff17dea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6c161ea_3eeb_4c50_a911_7515f9da76d1
ELIN-600991-2016 | EL-311450-2015 | 7/26/2016 12:33:10 PM | ASSESS: EL: Final | png | #asFound | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 4 | 4 | A new residential service feeding 2 200 amp 240 volt one phase panels has been installed. One 200 amp panel has had shelving installed directly in front of the panel and the other panel was located high and was not readily accessible. Both panels provide for potential for injury to workers and operates of the equipment when access to the equipment is not properly provided | 4 | General Location of equipment does not allow for proper access to disconnecting means | Panel_obstructed_by_shelving.png | file://x:/photopub/docs/0000000462/c0a44f87-808e-4dcd-bfc7-987cc57c5b71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b403aac_b08a_4a88_a028_ec1f6a02ba6f
GAIN-633586-2016 | GA-425003-2016 | 9/1/2016 11:02:50 AM | ASSESS: GA: Final | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | GasTite must be properly secured to avoid damage which could cause leak and possible fire. | 3 | Code prohibited practices or materials | Gastite_termination.png | file://x:/photopub/docs/0000000479/1c67d4d6-08dc-43f7-a444-9ffc2927baa0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__745168bd_edd1_4d62_bc1d_f93843a620fe
GAIN-637704-2016 | GA-413733-2016 | 9/2/2016 11:14:44 AM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Vent_support.png | file://x:/photopub/docs/0000000479/3619d863-ccaa-4557-b07d-4318758f380e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9746848a_2fcc_46e5_b766_cbc48e7e403f
ELIN-643618-2016 | EL-414780-2016 | 9/2/2016 7:22:18 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Permanent main distribution panel being used for temporary construction purposes not protected from the effects of weather and equipment in direct contact with water (rain). This poses as risk of personal injury (shock) or property damage (thermal event) during the construction phase and afterwards due to deterioration of the service equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | View01_main_distribution_.png | file://x:/photopub/docs/0000000480/ae5d1df2-5221-44a9-9a0e-a5b9c19025d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f49b440a_b42f_4349_b4d6_54fe48d213c3
BPVOP-613508-2016 | BPV-222566-2015 | 7/18/2016 10:08:47 AM | ASSESS: BPV OP: Re-Inspection Boiler | png | #asFound | BP195 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | 3 | 3 | Boiler heat exchange surfaces should be clear from scale and other deposits that could impair thermal heat transfer. I found excessive scale and deposits on the water side of a 15psi steam boiler. This can lead to over heating and failure of the boiler tubes and controls. | 3 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | LWCO_scale_sludge.png | file://x:/photopub/docs/0000000458/8eb5c365-a109-464d-8ee1-ac95426001f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d246b8d8_3334_4d5d_a0f1_26567e4c1efe
ELHE-619434-2016 | HE-416827-2016 | 7/28/2016 2:41:03 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 5 | In an existing single family dwelling, an attached garage had a 15amp 120volt duplex receptacle and male cord end fail resulting in a fire. Not only was equipment damaged but it also resulted in a thermal condition. See pic attached. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | What_s_left_of_the_ext_cord.png | file://x:/photopub/docs/0000000464/92f28f4a-7963-4e92-b89c-8af76757813b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__484c9355_4be5_4369_b9cd_3a9335cee812
ELHE-619434-2016 | HE-416827-2016 | 7/28/2016 2:41:03 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 5 | In an existing single family dwelling, an attached garage had a 15amp 120volt duplex receptacle and male cord end fail resulting in a fire. Not only was equipment damaged but it also resulted in a thermal condition. See pic attached. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 15amp_outlet.png | file://x:/photopub/docs/0000000464/2060834a-c18d-41fa-b0ea-5f25cc90e885.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__484c9355_4be5_4369_b9cd_3a9335cee812
ELHE-619434-2016 | HE-416827-2016 | 7/28/2016 2:41:03 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 5 | In an existing single family dwelling, an attached garage had a 15amp 120volt duplex receptacle and male cord end fail resulting in a fire. Not only was equipment damaged but it also resulted in a thermal condition. See pic attached. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Main_panel.png | file://x:/photopub/docs/0000000464/e4a2311a-6591-4f43-bfe7-b351ffdec2c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__484c9355_4be5_4369_b9cd_3a9335cee812
ELIN-616095-2016 | EL-406473-2016 | 7/25/2016 8:21:41 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Main_distribution.png | file://x:/photopub/docs/0000000460/d46b1ec6-2f16-4d46-bb30-45c2e14d46a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96edae6a_bcf4_4cb4_a3b9_688db74289df
ELIN-628749-2016 | EL-417705-2016 | 8/11/2016 12:17:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 4 | 15 amp, 120 volt ground fault receptacle has a 20 amp overcurrent device protecting it. This is a thermal issue. | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | 1768_main_distribution_and_receptacles.png | file://x:/photopub/docs/0000000469/c3fa1a27-8e20-48e4-ba32-cc8ea629b851.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a219dcf9_3bf4_47f4_b9bc_6ba3de835ed3
ELIN-590343-2016 | EL-396096-2016 | 6/28/2016 8:59:55 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Having multiple bonds to ground will create difference in potential if a fault occurs. This could result in objectionable current flow creating a shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | AC_90.png | file://x:/photopub/docs/0000000449/379ecc17-1696-4bd1-a433-01afce42faa5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a5a83e49_7fe7_4c4d_a641_6f83211e4320
ELIN-590343-2016 | EL-396096-2016 | 6/28/2016 8:59:55 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Having multiple bonds to ground will create difference in potential if a fault occurs. This could result in objectionable current flow creating a shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Switch.png | file://x:/photopub/docs/0000000449/fdb5404f-1ab9-4b84-9b93-969860c334e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a5a83e49_7fe7_4c4d_a641_6f83211e4320
ELIN-590343-2016 | EL-396096-2016 | 6/28/2016 8:59:55 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Having multiple bonds to ground will create difference in potential if a fault occurs. This could result in objectionable current flow creating a shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Bonding.png | file://x:/photopub/docs/0000000449/d0e4be10-e59c-4f5b-96ab-899d35ccedf5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a5a83e49_7fe7_4c4d_a641_6f83211e4320
ELIN-590343-2016 | EL-396096-2016 | 6/28/2016 8:59:55 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Having multiple bonds to ground will create difference in potential if a fault occurs. This could result in objectionable current flow creating a shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Barn_wiring_.png | file://x:/photopub/docs/0000000449/ee47ff8f-0bdb-4366-bcae-96657f935ab2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a5a83e49_7fe7_4c4d_a641_6f83211e4320
GAOP-200097-2014 | 5265064 | 8/30/2016 11:47:11 AM | ASSESS: GA OP: Periodic | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Hose could become damaged and leak, leading to possible fire or explosion. | 3 | Non-compliant material/fittings installed | Un_approved_connector.png | file://x:/photopub/docs/0000000478/70dba4c2-79eb-4e55-97c3-e94e96ca39e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e69bbc6_3511_430d_a404_2eaf65574589
ELIN-630755-2016 | EL-401697-2016 | 8/15/2016 11:43:36 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL039 | Equipment is not marked / identified Multiple service boxes not marked. | 2 | 2 |  | 2 | Equipment is not marked / identified Multiple service boxes not marked. | Mast.png | file://x:/photopub/docs/0000000470/332a5694-3d93-4b6c-9caf-71190d16eb2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f349686f_1e17_4756_b7c0_83e178bc0982
ELIN-630755-2016 | EL-401697-2016 | 8/15/2016 11:43:36 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL039 | Equipment is not marked / identified Multiple service boxes not marked. | 2 | 2 |  | 2 | Equipment is not marked / identified Multiple service boxes not marked. | meter_installed.png | file://x:/photopub/docs/0000000470/b524640c-32f1-43c2-88d0-07f2b5dee6cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f349686f_1e17_4756_b7c0_83e178bc0982
ELIN-640639-2016 | UW-429651-2016 | 8/30/2016 7:35:41 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found main consumer's service equipment rated 800 amp 120/208 volt 3 phase equipment that is in contact with water, is rusted and is damaged. When electrical equipment is rusted or damaged the electrical equipment may not perform its functions as it is approved and designed for and could fail in the event there is a fault condition on the system and could result in an electrical fire or shock hazard to people or property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | wet_rusted_service_equiment_2.png | file://x:/photopub/docs/0000000477/7d94cdf2-75b6-412b-94da-62e2b74ccd7f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fee94ace_16d1_4faf_a1b7_16bdde4bc810
ELIN-640639-2016 | UW-429651-2016 | 8/30/2016 7:35:41 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found main consumer's service equipment rated 800 amp 120/208 volt 3 phase equipment that is in contact with water, is rusted and is damaged. When electrical equipment is rusted or damaged the electrical equipment may not perform its functions as it is approved and designed for and could fail in the event there is a fault condition on the system and could result in an electrical fire or shock hazard to people or property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | wet_rusted_service_equiment_1.png | file://x:/photopub/docs/0000000477/7b94af36-ccdc-4a76-91fb-1ca947331e88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fee94ace_16d1_4faf_a1b7_16bdde4bc810
ELIN-640639-2016 | UW-429651-2016 | 8/30/2016 7:35:41 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found main consumer's service equipment rated 800 amp 120/208 volt 3 phase equipment that is in contact with water, is rusted and is damaged. When electrical equipment is rusted or damaged the electrical equipment may not perform its functions as it is approved and designed for and could fail in the event there is a fault condition on the system and could result in an electrical fire or shock hazard to people or property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | wet_rusted_service_equiment_3.png | file://x:/photopub/docs/0000000477/78fe84da-9b05-4d23-8973-ee5ae68214ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fee94ace_16d1_4faf_a1b7_16bdde4bc810
ELIN-640639-2016 | UW-429651-2016 | 8/30/2016 7:35:41 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found main consumer's service equipment rated 800 amp 120/208 volt 3 phase equipment that is in contact with water, is rusted and is damaged. When electrical equipment is rusted or damaged the electrical equipment may not perform its functions as it is approved and designed for and could fail in the event there is a fault condition on the system and could result in an electrical fire or shock hazard to people or property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | wet_rusted_service_equiment_4.png | file://x:/photopub/docs/0000000477/532b237b-8dd5-445d-a684-09601677255d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fee94ace_16d1_4faf_a1b7_16bdde4bc810
EDIN-595448-2016 | ED-333664-2016 | 6/2/2016 | ASSESS: ED IN: Acceptance | png | #asFound | ED036 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is in operation A secondary system will detect known hazard if this monitoring is bypassed or failed Risk Reg ED-02 | 4 | 4 | The elevator controller function is to manage the safe operation of the elevator. During an acceptance inspection it was found that a critical part of the safety circuit was compromised due to a faulty logic board. The elevator was allowed to run with the elevator hall door open. This created a serious safety hazard for any potential users of the elevator. It was found the elevator contractor failed to properly pre-test the elevator. This is a 2 stop handicap platform lift located in a commercial building. | 4 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is in operation A secondary system will detect known hazard if this monitoring is bypassed or failed Risk Reg ED-02 | Running_with_door_open.png | file://x:/photopub/docs/0000000449/afd62391-c8f9-4d56-9312-a69e28d539fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eaff6146_c30e_4b2e_a1e5_0efd47d35eb8
EDIN-595074-2016 | ED-310426-2015 | 6/13/2016 | ASSESS: ED IN: Construction Use | png | #asFound | ED018 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 3 | 3 | The machine room is to be free of any water leaks. It was found during an acceptance inspection that the ventilation damper vent installation was not complete and water was leaking into the machine room by an electrical pipe. It was found the general contractor had not completed the full installation of the vent. This 36 stop overhead traction elevator is located in a new residential building. | 3 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | Machine_vent_leaking_water.png | file://x:/photopub/docs/0000000449/fc81926e-1823-4acb-85b8-e0cfcb43b50a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0223eaf1_1d5d_47e2_bffe_36a147373f17
BPVIN-615403-2016 | BPV-414117-2016 | 7/20/2016 11:07:00 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. Devices must be installed according to all applicable standards. I found a safety device installed incorrectly on a 150 psi air receiver. Potential exists for an incident to occur due to a safety device not providing intended level of control | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | Pressure_relief_device_inlet.png | file://x:/photopub/docs/0000000459/5c97db58-18a3-4b2f-9b29-ff2051031033.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4810ed20_f6a3_4393_a8fa_11f8caa76386
BPVIN-615403-2016 | BPV-414117-2016 | 7/20/2016 11:07:00 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. Devices must be installed according to all applicable standards. I found a safety device installed incorrectly on a 150 psi air receiver. Potential exists for an incident to occur due to a safety device not providing intended level of control | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | Air_Receiver_Pressure_relief_device_.png | file://x:/photopub/docs/0000000459/ad7f219d-3b89-402b-ba59-8da28c8c979a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4810ed20_f6a3_4393_a8fa_11f8caa76386
GAIN-615330-2016 | GA-391848-2016 | 7/20/2016 10:26:35 AM | ASSESS: GA: Final | png | #asFound | GA018 | Venting of pressure relief device indoors where source of ignition is present | 5 | 5 | The gas regulator has been mounted next to the burner of the water heater inside of the occupied building. The regulator has been installed without a dirt pocket ahead of the regulator to protect it from contamination that could cause the regulator to fail. If the regulator failed and vented gas next to the burner it could start a fire. | 5 | Venting of pressure relief device indoors where source of ignition is present | Water_heater_regulator_vent_.png | file://x:/photopub/docs/0000000459/5aba5313-ed7a-4b8a-ac86-1b3dee3c5c83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15b3df04_86ea_47a8_876e_c939a4f239e0
BPVOP-622787-2016 | 2295976 | 8/3/2016 10:05:45 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 |  | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | Scale_caused_from_insulation.png | file://x:/photopub/docs/0000000465/a3742159-999e-47aa-ab39-f155111926d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__675b7aeb_f275_4fbe_8062_97e7ffe68af1
GAIN-645499-2016 | GA-257266-2015 | 9/9/2016 4:26:04 PM | ASSESS: GA: Final | png | #asFound | GA115 | Vent sizing causing spillage | 5 | 4 | Under sized common vent causes spillage of product of combustion. | 5 | Vent sizing causing spillage | Under_sized_common_vent.png | file://x:/photopub/docs/0000000483/404b0c5b-7cc9-40d2-b8f3-b53a5d6ceb0a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28090f01_158d_4719_a08f_7380483090e3
GAIN-645475-2016 | GA-257257-2015 | 9/9/2016 4:48:34 PM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | Lack of proper c vent clearance causes a fire hazard. | 3 | Non compliant Type C Vent clearance | 1__c_vent_clearance.png | file://x:/photopub/docs/0000000483/5971bc48-2eae-4095-aeda-d011dfd45df0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a641335d_2727_460a_a24a_a3a6be5a1cb0
GAIN-616773-2016 | GA-369382-2016 | 8/4/2016 3:46:45 PM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | Liquid propane could enter regulator which has a vapour rating only resulting in damage. Possible over pressure condition resulting in over fire condition. Fire and or carbon monoxide risk. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Regs.png | file://x:/photopub/docs/0000000466/b6b147da-18eb-440a-a1c0-fb2b6b533dd1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcd295ff_64ca_4575_9166_735e36eb4103
ELIN-631532-2016 | EL-354072-2016 | 8/17/2016 7:20:30 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Electrical equipment that is damaged during installation is required to be replaced. This requirement is to protect persons and property from potential electrical hazards. In this installation at a new single family home, the safety officer observed the cable for the dryer receptacle had been damaged. At the damaged portion of the cable, a small area of the outer sheath was missing and bare copper was showing through the insulation of two of the internal conductors. When energized, there is a potential for a parallel arc fault between the damaged conductors which could create a fire hazard within the walls of this home. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Damaged_Cable.png | file://x:/photopub/docs/0000000471/4042d2b4-280a-4f5b-96d4-47582c70b45c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0532302f_aab9_4065_9355_48f64d9e1574
ELIN-631532-2016 | EL-354072-2016 | 8/17/2016 7:20:30 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Electrical equipment that is damaged during installation is required to be replaced. This requirement is to protect persons and property from potential electrical hazards. In this installation at a new single family home, the safety officer observed the cable for the dryer receptacle had been damaged. At the damaged portion of the cable, a small area of the outer sheath was missing and bare copper was showing through the insulation of two of the internal conductors. When energized, there is a potential for a parallel arc fault between the damaged conductors which could create a fire hazard within the walls of this home. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Location_of_damaged_cable.png | file://x:/photopub/docs/0000000471/dce6effc-b5d3-457b-b633-d6fdc92a9bbf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0532302f_aab9_4065_9355_48f64d9e1574
BPVOP-622787-2016 | 2295976 | 8/3/2016 10:05:45 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 |  | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | Insulation.png | file://x:/photopub/docs/0000000465/5bc97448-f47d-4549-8ef7-524e05a971ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__675b7aeb_f275_4fbe_8062_97e7ffe68af1
ELIN-619893-2016 | UW-417164-2016 | 7/28/2016 9:12:13 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found 250 KCM sized conductors terminated directly onto 200 amp panelboard distribution bus bars without use of over-current device to protect conductors. When over-current device is not installed for protecting conductors, the system is an electrical fire or shock hazard. | 4 | Protection and control Switching is not done in an ungrounded conductor | 102.png | file://x:/photopub/docs/0000000462/6afcf88b-2b5a-4af4-be28-2f8d1c659fc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc8d84a6_86b8_446d_8940_7f3e2e940e74
ELIN-619893-2016 | UW-417164-2016 | 7/28/2016 9:12:13 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found 250 KCM sized conductors terminated directly onto 200 amp panelboard distribution bus bars without use of over-current device to protect conductors. When over-current device is not installed for protecting conductors, the system is an electrical fire or shock hazard. | 4 | Protection and control Switching is not done in an ungrounded conductor | 103.png | file://x:/photopub/docs/0000000462/96e345b1-8fff-4255-9579-476f865addbd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc8d84a6_86b8_446d_8940_7f3e2e940e74
ELIN-619893-2016 | UW-417164-2016 | 7/28/2016 9:12:13 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found 250 KCM sized conductors terminated directly onto 200 amp panelboard distribution bus bars without use of over-current device to protect conductors. When over-current device is not installed for protecting conductors, the system is an electrical fire or shock hazard. | 4 | Protection and control Switching is not done in an ungrounded conductor | 105.png | file://x:/photopub/docs/0000000462/23d0a7d6-1e61-42ed-b070-b87c4c577a85.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc8d84a6_86b8_446d_8940_7f3e2e940e74
ELIN-619893-2016 | UW-417164-2016 | 7/28/2016 9:12:13 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found 250 KCM sized conductors terminated directly onto 200 amp panelboard distribution bus bars without use of over-current device to protect conductors. When over-current device is not installed for protecting conductors, the system is an electrical fire or shock hazard. | 4 | Protection and control Switching is not done in an ungrounded conductor | 104.png | file://x:/photopub/docs/0000000462/5b10d0c1-0ad3-45bf-a1f7-71de337646f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc8d84a6_86b8_446d_8940_7f3e2e940e74
ELIN-619893-2016 | UW-417164-2016 | 7/28/2016 9:12:13 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found 250 KCM sized conductors terminated directly onto 200 amp panelboard distribution bus bars without use of over-current device to protect conductors. When over-current device is not installed for protecting conductors, the system is an electrical fire or shock hazard. | 4 | Protection and control Switching is not done in an ungrounded conductor | 100.png | file://x:/photopub/docs/0000000462/fc25a5f4-2b16-4701-8933-90b492d54f44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc8d84a6_86b8_446d_8940_7f3e2e940e74
ELIN-619893-2016 | UW-417164-2016 | 7/28/2016 9:12:13 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found 250 KCM sized conductors terminated directly onto 200 amp panelboard distribution bus bars without use of over-current device to protect conductors. When over-current device is not installed for protecting conductors, the system is an electrical fire or shock hazard. | 4 | Protection and control Switching is not done in an ungrounded conductor | 101.png | file://x:/photopub/docs/0000000462/55480b62-5cb8-41f4-a55a-55cafdbafeb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc8d84a6_86b8_446d_8940_7f3e2e940e74
ELIN-619299-2016 | EL-401142-2016 | 8/24/2016 1:45:42 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | In an existing single family dwelling mobile home, a 120volt 15amp household extension cord plugged into a bedroom outlet is used to power a full sized fridge in back corridor. This can lead to a thermal effect. Pic. Attached. | 4 | Conductors, Misuse of flexible cords. | Ext_cord_.png | file://x:/photopub/docs/0000000475/3a21fcc5-1772-454a-991f-7a5364b1a12d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d3843ac_3ed8_47d4_a70c_4bb6fdc9f984
ELIN-619299-2016 | EL-401142-2016 | 8/24/2016 1:45:42 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | In an existing single family dwelling mobile home, a 120volt 15amp household extension cord plugged into a bedroom outlet is used to power a full sized fridge in back corridor. This can lead to a thermal effect. Pic. Attached. | 4 | Conductors, Misuse of flexible cords. | Fridge_and_extension_cord.png | file://x:/photopub/docs/0000000475/1ae94483-acb9-4391-b1a1-138589ace4b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d3843ac_3ed8_47d4_a70c_4bb6fdc9f984
ELIN-627819-2016 | EL-231161-2015 | 8/16/2016 8:50:06 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | __unsupported_service_conduit.png | file://x:/photopub/docs/0000000471/44dc480e-6a04-4cbd-8c84-afb4836cd24a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6c42dfc_c626_4dcb_aa01_6d4497eacc1a
ELIN-627819-2016 | EL-231161-2015 | 8/16/2016 8:50:06 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Upper_service__upper_service_conduit_with_no_support.png | file://x:/photopub/docs/0000000471/607177c7-d455-46e2-a8c0-9b03156d5028.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6c42dfc_c626_4dcb_aa01_6d4497eacc1a
ELIN-643095-2016 | EL-425408-2016 | 9/6/2016 10:43:29 AM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | In a residential electrical service the grounded service conductor is required to be connected to a ground electrode at the supply side of the service disconnect only. This is to prevent neutral currents from circulating through the bonding system and to carry any unbalanced fault currents back to the source. In this installation, two 100 amp panel where replaced in a residential duplex. The ground conductor for each of the new panels was connected to the bond terminal on the load side of the panel. If an electrical fault was to occur, there is the potential for unbalanced fault currents to flow through the metal of the service panel and create a shock hazard for any persons in contact with the panel. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Panel_unit_2010.png | file://x:/photopub/docs/0000000481/70eb8787-f1dc-4781-92ea-da1a5d0b4da4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bc51c36_4574_4002_b5ec_558f7d8434e7
ELIN-643095-2016 | EL-425408-2016 | 9/6/2016 10:43:29 AM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | In a residential electrical service the grounded service conductor is required to be connected to a ground electrode at the supply side of the service disconnect only. This is to prevent neutral currents from circulating through the bonding system and to carry any unbalanced fault currents back to the source. In this installation, two 100 amp panel where replaced in a residential duplex. The ground conductor for each of the new panels was connected to the bond terminal on the load side of the panel. If an electrical fault was to occur, there is the potential for unbalanced fault currents to flow through the metal of the service panel and create a shock hazard for any persons in contact with the panel. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Panel_unit_2012.png | file://x:/photopub/docs/0000000481/9c5d3d00-ce71-45de-abf2-28aea8022382.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bc51c36_4574_4002_b5ec_558f7d8434e7
ELIN-616526-2016 | UW-414925-2016 | 7/22/2016 12:49:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Private high voltage overhead transformer mounted on a pole set in 1958, feeding a submarine cable. The pole and cross arm have visible signs of rot and require maintenance. The 600V 400A switch supports have rotted off. This is a shock and fire hazard. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | F.png | file://x:/photopub/docs/0000000462/baa79b8f-2e58-484c-a678-c6a691a55ca6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01a33ad3_6e3b_4c5f_87bc_68a65e69c255
ELIN-616526-2016 | UW-414925-2016 | 7/22/2016 12:49:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Private high voltage overhead transformer mounted on a pole set in 1958, feeding a submarine cable. The pole and cross arm have visible signs of rot and require maintenance. The 600V 400A switch supports have rotted off. This is a shock and fire hazard. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | H.png | file://x:/photopub/docs/0000000462/626d60ad-228d-4e79-babf-315db9a90add.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01a33ad3_6e3b_4c5f_87bc_68a65e69c255
ELIN-616526-2016 | UW-414925-2016 | 7/22/2016 12:49:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Private high voltage overhead transformer mounted on a pole set in 1958, feeding a submarine cable. The pole and cross arm have visible signs of rot and require maintenance. The 600V 400A switch supports have rotted off. This is a shock and fire hazard. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | E.png | file://x:/photopub/docs/0000000462/d8a42de6-136d-4b6d-8ced-7793f4c13fc0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01a33ad3_6e3b_4c5f_87bc_68a65e69c255
ELIN-616526-2016 | UW-414925-2016 | 7/22/2016 12:49:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Private high voltage overhead transformer mounted on a pole set in 1958, feeding a submarine cable. The pole and cross arm have visible signs of rot and require maintenance. The 600V 400A switch supports have rotted off. This is a shock and fire hazard. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | J.png | file://x:/photopub/docs/0000000462/a6499a89-d658-4ab8-8fa0-6e14c42cf9d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01a33ad3_6e3b_4c5f_87bc_68a65e69c255
ELIN-616526-2016 | UW-414925-2016 | 7/22/2016 12:49:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Private high voltage overhead transformer mounted on a pole set in 1958, feeding a submarine cable. The pole and cross arm have visible signs of rot and require maintenance. The 600V 400A switch supports have rotted off. This is a shock and fire hazard. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | G.png | file://x:/photopub/docs/0000000462/e6d44bcd-1011-47bd-a043-360d5b17fd35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01a33ad3_6e3b_4c5f_87bc_68a65e69c255
ELOP-607186-2016 | 5140949 | 8/8/2016 10:11:20 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL231 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | 3 | 3 | Follow-up assessment for pilot parts mill. Saw dust buildup on conveyor motors under platform at rear of mill is not addressed in the dust mitigation plan. Cleaning in this area is not effective. Build up of combustible sawdust on motor and conveyor pulleys can lead to overheated bearings and cause a fire. | 3 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | Dust_on_motor.png | file://x:/photopub/docs/0000000467/6dd213eb-3ea3-484b-9fdd-699f1bf7e4e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a96fec85_3009_410d_9544_92b00d1b9b4e
ELOP-626333-2016 | EL-057955-2013 | 8/8/2016 2:02:22 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL179 | General Construction Indoor: Inadequate spacing from walls for transformer. | 4 | 3 | Electrical operating permit assessment of grocery store. An inadequate and reduced clearance from an electrical transformer to the combustible wall behind this transformer has caused charring of the wall over the years. As the charring progresses, it becomes a bigger fire risk with time. Fire hazard. | 4 | General Construction Indoor: Inadequate spacing from walls for transformer. | Charring.png | file://x:/photopub/docs/0000000467/b38939f6-7677-4a2f-81c4-01899e0dae91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8e29f0d_40d1_4ca4_b09c_adfeff8df393
ELIN-615844-2016 | EL-368429-2016 | 7/21/2016 9:59:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 200 amp, 120/240 volt main distribution of a type 1 rating installed where maybe exposed to outdoor elements. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Temp_main_distribution.png | file://x:/photopub/docs/0000000459/47ba4ebd-e1c7-4e08-ad6f-328c6549e41f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d5d705f_c092_4aae_a07d_92c5f618fa84
ELIN-615560-2016 | EL-302238-2015 | 7/25/2016 10:37:03 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | A 20A GFCI receptacle has been installed on a 15A 120V branch circuit. This poses a hazard to the electrical equipment as the branch circuit could be overloaded, this could also damage equipment connected to the receptacle that require a 20A power supply. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | GFCI.png | file://x:/photopub/docs/0000000461/ce317194-4d24-4f51-829e-8f9ee82b23a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b080ceb5_7e11_47ae_9b65_d8d9d83cfe1b
584937-2016 | GA-153387-2014 | 8/22/2016 1:40:29 PM | ASSESS: GA: Rough-In | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | The hazard is that if the regulator relief valve vents gas the vented gas can be readily ignited by the RTUs burner. This uncontrolled burning gas could catch the building on fire risking property and life. | 4 | Ignition sources present with-in minimum distance required | RTU_reg_vent_location_times_8.png | file://x:/photopub/docs/0000000474/17e154ab-1d23-4f30-b22a-c1cf4da64e8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d53ebc5_45e2_455c_ae10_e8941012e6ba
584937-2016 | GA-153387-2014 | 8/22/2016 1:40:29 PM | ASSESS: GA: Rough-In | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | The hazard is that if the regulator relief valve vents gas the vented gas can be readily ignited by the RTUs burner. This uncontrolled burning gas could catch the building on fire risking property and life. | 4 | Ignition sources present with-in minimum distance required | B-vent_no_clearances.png | file://x:/photopub/docs/0000000474/ba4d89be-4dbf-4172-903f-007f20d15f30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d53ebc5_45e2_455c_ae10_e8941012e6ba
ELIN-640540-2016 | UW-429879-2016 | 8/30/2016 12:23:47 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL148 | Installation of electrical equipment Visible charring of combustible material | 5 | 5 | Overloaded lighting circuit. The overloaded conductors caught fire. Maximum over current protection for 14awg wire is not to exceed 15 amps. This installation had a load of 18 amps protected by a 20 amp breaker on 14awg wire. The heating was further exacerbated by the length of the run. Conductors have their own inherent resistance which increases with the length of the run. As the resistance of the cable increases so does the heating. This is called voltage drop. The allowable voltage drop on a cable feeding a lighting branch circuit is 3% or 3.6v on a 120v circuit. A 14awg cable loaded to 18 amps will drop 3.6v by the time it hits 37'. It is estimated that the length of the run that caught fire was in excess of 60 feet. | 5 | Installation of electrical equipment Visible charring of combustible material | A.png | file://x:/photopub/docs/0000000478/4e319e90-72f5-4d0c-9797-d275fdb07636.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fcc4ea6a_46c4_4d14_8732_2d4e4322150d
ELIN-640540-2016 | UW-429879-2016 | 8/30/2016 12:23:47 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL148 | Installation of electrical equipment Visible charring of combustible material | 5 | 5 | Overloaded lighting circuit. The overloaded conductors caught fire. Maximum over current protection for 14awg wire is not to exceed 15 amps. This installation had a load of 18 amps protected by a 20 amp breaker on 14awg wire. The heating was further exacerbated by the length of the run. Conductors have their own inherent resistance which increases with the length of the run. As the resistance of the cable increases so does the heating. This is called voltage drop. The allowable voltage drop on a cable feeding a lighting branch circuit is 3% or 3.6v on a 120v circuit. A 14awg cable loaded to 18 amps will drop 3.6v by the time it hits 37'. It is estimated that the length of the run that caught fire was in excess of 60 feet. | 5 | Installation of electrical equipment Visible charring of combustible material | B.png | file://x:/photopub/docs/0000000478/71e928df-89fb-46fb-a102-1f1de945d81b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fcc4ea6a_46c4_4d14_8732_2d4e4322150d
ELIN-640540-2016 | UW-429879-2016 | 8/30/2016 12:23:47 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL148 | Installation of electrical equipment Visible charring of combustible material | 5 | 5 | Overloaded lighting circuit. The overloaded conductors caught fire. Maximum over current protection for 14awg wire is not to exceed 15 amps. This installation had a load of 18 amps protected by a 20 amp breaker on 14awg wire. The heating was further exacerbated by the length of the run. Conductors have their own inherent resistance which increases with the length of the run. As the resistance of the cable increases so does the heating. This is called voltage drop. The allowable voltage drop on a cable feeding a lighting branch circuit is 3% or 3.6v on a 120v circuit. A 14awg cable loaded to 18 amps will drop 3.6v by the time it hits 37'. It is estimated that the length of the run that caught fire was in excess of 60 feet. | 5 | Installation of electrical equipment Visible charring of combustible material | C.png | file://x:/photopub/docs/0000000478/a0eb2dfa-6182-4e88-8d59-ca1c871144e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fcc4ea6a_46c4_4d14_8732_2d4e4322150d
ELIN-661960-2016 | EL-352549-2016 | 9/13/2016 11:55:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL118 | Conductors Identified conductor or neutral conductor has not been properly identified | 1 | 1 | The main consumer service neutral conductor has not been identified and therefore this could lead to a shock hazard for electrical worker personal by mistakenly assuming no voltage is present on a conductor. | 1 | Conductors Identified conductor or neutral conductor has not been properly identified | Neutral_not_identified.png | file://x:/photopub/docs/0000000484/34e7a747-efee-44d7-855d-746128a3940d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7f0345b_247a_4fbf_b61b_677d6221324e
ELHE-617115-2016 | HE-415294-2016 | 7/22/2016 1:47:22 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Service mast is damaged. Conductors inside are not adequately protected. Fault may occur resulting in fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Damaged_mast.png | file://x:/photopub/docs/0000000460/914879f7-b8ef-4c62-b626-754712aeea8e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1b1d80f_6867_4b36_9ff4_005b3e1fa38f
ELIN-601800-2016 | EL-382216-2016 | 6/30/2016 12:48:28 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | No_duct_seal_installed.png | file://x:/photopub/docs/0000000450/1ef90901-e2bb-4ab1-8924-bfddaeface84.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6fcc21c8_aa11_455a_84ef_d8e8fed05353
BPVIN-615499-2016 | BPV-414215-2016 | 7/20/2016 12:38:08 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve on an air receiver must match or exceed capacity of all attached compressors. I found the relieving capacity of the safety valve was less than that what's required. The air receiver may rupture due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Air_receiver_.png | file://x:/photopub/docs/0000000459/8a19840d-8e6e-4047-82b8-4a3579655638.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59f0130c_244d_4ee7_88f6_940de1545f9d
BPVIN-615499-2016 | BPV-414215-2016 | 7/20/2016 12:38:08 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve on an air receiver must match or exceed capacity of all attached compressors. I found the relieving capacity of the safety valve was less than that what's required. The air receiver may rupture due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | PV_Data_label.png | file://x:/photopub/docs/0000000459/e65ea82e-7d33-4b51-ad4c-3769f3c9512a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59f0130c_244d_4ee7_88f6_940de1545f9d
BPVIN-615499-2016 | BPV-414215-2016 | 7/20/2016 12:38:08 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve on an air receiver must match or exceed capacity of all attached compressors. I found the relieving capacity of the safety valve was less than that what's required. The air receiver may rupture due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Atlas_motor_data_label_capacity_.png | file://x:/photopub/docs/0000000459/94997311-3526-40c5-a96a-462678dc559f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59f0130c_244d_4ee7_88f6_940de1545f9d
584937-2016 | GA-153387-2014 | 8/22/2016 1:40:29 PM | ASSESS: GA: Rough-In | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | The hazard is that if the regulator relief valve vents gas the vented gas can be readily ignited by the RTUs burner. This uncontrolled burning gas could catch the building on fire risking property and life. | 4 | Ignition sources present with-in minimum distance required | B-vent_not_supported.png | file://x:/photopub/docs/0000000474/d846d061-81b1-4413-bcc1-88d9ee62f5da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d53ebc5_45e2_455c_ae10_e8941012e6ba
584937-2016 | GA-153387-2014 | 8/22/2016 1:40:29 PM | ASSESS: GA: Rough-In | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | The hazard is that if the regulator relief valve vents gas the vented gas can be readily ignited by the RTUs burner. This uncontrolled burning gas could catch the building on fire risking property and life. | 4 | Ignition sources present with-in minimum distance required | Water_heater_draft_hood_not_attached.png | file://x:/photopub/docs/0000000474/64b6b201-b4e9-45b9-ab05-a59b12311a96.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d53ebc5_45e2_455c_ae10_e8941012e6ba
584937-2016 | GA-153387-2014 | 8/22/2016 1:40:29 PM | ASSESS: GA: Rough-In | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | The hazard is that if the regulator relief valve vents gas the vented gas can be readily ignited by the RTUs burner. This uncontrolled burning gas could catch the building on fire risking property and life. | 4 | Ignition sources present with-in minimum distance required | Unit_heater_under_sized_gas_piping.png | file://x:/photopub/docs/0000000474/133b8263-14de-4b75-a089-09b4b7b00c13.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d53ebc5_45e2_455c_ae10_e8941012e6ba
584937-2016 | GA-153387-2014 | 8/22/2016 1:40:29 PM | ASSESS: GA: Rough-In | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | The hazard is that if the regulator relief valve vents gas the vented gas can be readily ignited by the RTUs burner. This uncontrolled burning gas could catch the building on fire risking property and life. | 4 | Ignition sources present with-in minimum distance required | Appliance_connector_kinked_and_run_through_cabinet.png | file://x:/photopub/docs/0000000474/8bddff16-7441-4bda-b0a9-ef8dd72c34d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d53ebc5_45e2_455c_ae10_e8941012e6ba
GAIN-628493-2016 | GA-375059-2016 | 8/22/2016 2:01:31 PM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | 1) All gas lines are required to be tested and leak tight. 2) The black steel Union at the furnace was left loose by installer. 3) Natural gas may leak undetected and collect in a area and be ignited by a source of ignition leading to possible fire and damage to property and persons. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Loose__pipe_union_at_furnace_.png | file://x:/photopub/docs/0000000474/4e05797c-c8f9-47da-8b68-fbfe574acc90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f3db162_1f9e_4a46_9af3_2b639e307fba
GAIN-628493-2016 | GA-375059-2016 | 8/22/2016 2:01:31 PM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | 1) All gas lines are required to be tested and leak tight. 2) The black steel Union at the furnace was left loose by installer. 3) Natural gas may leak undetected and collect in a area and be ignited by a source of ignition leading to possible fire and damage to property and persons. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Gas_regulator_undersized_for_appliance_load.png | file://x:/photopub/docs/0000000474/01828b13-3431-4240-a793-8505430fc03b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f3db162_1f9e_4a46_9af3_2b639e307fba
ELIN-603421-2016 | EL-356637-2016 | 7/7/2016 12:17:31 PM | ASSESS: EL: Final | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 3 | In a new water park facility, a 120/240volt (unknown amperage) liquidtite conduit is used for general purpose raceway and is unprotected. This could lead to a power system interruption as well as equipment damage. (Picture attached) | 3 | Protection and control Low voltage protection damaged or not provided. | Liquidtite_.png | file://x:/photopub/docs/0000000453/33b1b441-6c69-4766-b348-99f7c3547015.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f496d782_3a48_4698_ab76_d47164cbf7ab
ELIN-598837-2016 | EL-368982-2016 | 6/30/2016 10:29:17 AM | ASSESS: EL: Final | png | #asFound | EL138 | Installation of electrical equipment General: boxes are not accessible. | 3 | 3 | The 30 amp 120/240 volt dryer receptacle is not accessible and hidden behind a cabinet, the dryer cord is run though the cabinet , this is a thermal hazard | 3 | Installation of electrical equipment General: boxes are not accessible. | Dryer_outlet.png | file://x:/photopub/docs/0000000452/fd0d9112-5467-4091-a41e-f59f3fa1d2bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b1bff1e_cfec_4dc2_bdf5_5f6073406c2c
EDMA-620990-2016 | ED-340353-2016 | 8/2/2016 3:05:44 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | A hydraulic elevator motor must be able to operate within the motor data nameplate rating. Some motor manufactures do allow a 15 to 30 percent over load situation for oil submerged motors. During my inspection I found a Leroy Somer 208V 3 Phase 20 Hp. Electric motor rated for 69 Full Load Amps. This motor with no load was operating at 86A amps 20% over motor data name plate. When the motor was tested with a full load of 2000lbs ,the amperage exceeded motor data nameplate by 58.4% with a reading of 118A. This could potentially cause an entrapment and or a fire situation. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | Data_sheet_with_readings.png | file://x:/photopub/docs/0000000465/242c52f8-c579-4419-af5e-3db0d0930a31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac6fa9fa_697d_4997_9bcd_fe499ca89db6
ELIN-599390-2016 | EL-399984-2016 | 7/7/2016 10:40:58 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Weather_head_and_point_of_attachment.png | file://x:/photopub/docs/0000000453/308ca69c-0789-4847-b931-3991091c7fcd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8b73568_a5d5_4301_9b92_525cc6dc4fa1
BPVOP-629888-2016 | 2269928 | 8/12/2016 9:02:03 AM | ASSESS: BPV OP: Re-Inspection Boiler | png | #asFound | BP137 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | 4 | 4 | Upon assessment of low pressure steam heating boiler with 40 square meters heating surface it is determined that safety valve popping pressure is higher than tolerance allowed by the code. Higher popping pressure is an indication of sticky moving parts of safety valve and valve may fail completely to operate in the event of overpressure in the boiler, if valve is not replaced or serviced, resulting in failure of pressure boundary of boiler with likelihood of severe incident. | 4 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | Safety_valve.png | file://x:/photopub/docs/0000000470/8663ad58-9529-4ec4-9309-9e222c8a992d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d22e9b76_44f8_44e3_a4f2_48a6989cda4c
GAHE-607773-2016 | HE-408656-2016 | 7/8/2016 6:31:40 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | At time of inspection on propane filling dispenser, emergency shut down systems missing, no scale and power to dispenser. In the event of an emergency no readily accessible shut down devices. | 4 | Missing mandatory safety controls | Escott2.png | file://x:/photopub/docs/0000000453/d439ecf5-1762-42d0-81df-74a15f45e542.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b403b52_f218_4b52_9c73_4f3aab803215
GAHE-607773-2016 | HE-408656-2016 | 7/8/2016 6:31:40 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | At time of inspection on propane filling dispenser, emergency shut down systems missing, no scale and power to dispenser. In the event of an emergency no readily accessible shut down devices. | 4 | Missing mandatory safety controls | Escott1.png | file://x:/photopub/docs/0000000453/e75b00a0-9454-4a98-9a4f-9a3e77ed2727.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b403b52_f218_4b52_9c73_4f3aab803215
ELIN-636299-2016 | EL-352213-2016 | 8/24/2016 4:44:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Found service grounding conductor #6 AWG copper run from 125 amp 120/240 volt service panelboard to outdoors on surface of building while the grounding conductor is exposed to possible mechanical damage and is not protected as required. When a #6AWG grounding conductor is run exposed on surface of building without mechanical protection, the grounding conductor could get damaged and result in a possible electric shock hazard to people due to possible fault condition or voltage differences in the system. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 100.png | file://x:/photopub/docs/0000000475/7dd0f4a0-652a-434d-a730-fe984ed30e69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcf8daef_7a5d_4283_831f_16c0ecf44d38
ELIN-636299-2016 | EL-352213-2016 | 8/24/2016 4:44:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Found service grounding conductor #6 AWG copper run from 125 amp 120/240 volt service panelboard to outdoors on surface of building while the grounding conductor is exposed to possible mechanical damage and is not protected as required. When a #6AWG grounding conductor is run exposed on surface of building without mechanical protection, the grounding conductor could get damaged and result in a possible electric shock hazard to people due to possible fault condition or voltage differences in the system. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 101.png | file://x:/photopub/docs/0000000475/475894b8-c68b-4894-b9ff-424aeaac90cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcf8daef_7a5d_4283_831f_16c0ecf44d38
ELIN-627713-2016 | EL-386584-2016 | 8/9/2016 5:08:21 PM | ASSESS: EL: Final | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | Found terminations of conductors made inside terminal lugs for 120/240 volt generator transfer switch and its wiring system terminal lugs which lug screws are not torqued tight enough onto conductors. When conductors are not terminated correctly or not torqued tight enough onto conductor then the full current carrying capacity of rated circuit is not provided and the electrical equipment can overheat and possibly cause an electrical fire or shock hazard to people or property | 3 | Protection and control Loading of distribution equipment exceeded | Conductor_pulled_out_easily_with_no_effort1.png | file://x:/photopub/docs/0000000469/b960d7c6-abc6-42dc-999c-59fbd0099eff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b7b7279_6008_4ae6_9753_6790843311ea
ELIN-627713-2016 | EL-386584-2016 | 8/9/2016 5:08:21 PM | ASSESS: EL: Final | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | Found terminations of conductors made inside terminal lugs for 120/240 volt generator transfer switch and its wiring system terminal lugs which lug screws are not torqued tight enough onto conductors. When conductors are not terminated correctly or not torqued tight enough onto conductor then the full current carrying capacity of rated circuit is not provided and the electrical equipment can overheat and possibly cause an electrical fire or shock hazard to people or property | 3 | Protection and control Loading of distribution equipment exceeded | Conductor_pulled_out_easily_with_no_effort3.png | file://x:/photopub/docs/0000000469/4ae01529-b5ff-4193-929d-3389f97d3129.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b7b7279_6008_4ae6_9753_6790843311ea
ELIN-627713-2016 | EL-386584-2016 | 8/9/2016 5:08:21 PM | ASSESS: EL: Final | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | Found terminations of conductors made inside terminal lugs for 120/240 volt generator transfer switch and its wiring system terminal lugs which lug screws are not torqued tight enough onto conductors. When conductors are not terminated correctly or not torqued tight enough onto conductor then the full current carrying capacity of rated circuit is not provided and the electrical equipment can overheat and possibly cause an electrical fire or shock hazard to people or property | 3 | Protection and control Loading of distribution equipment exceeded | Conductor_pulled_out_easily_with_no_effort2.png | file://x:/photopub/docs/0000000469/eb54f55c-9d36-4fb9-9c0b-0bb5d9e74522.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b7b7279_6008_4ae6_9753_6790843311ea
ELIN-634812-2016 | EL-368350-2016 | 8/23/2016 5:29:31 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | Repairs to electrical equipment are required to be made in an approved method with approved products. This requirement is so that the repaired equipment is equal to the standard of the equipment before it was damaged. In this installation, a splice was made using an unapproved product and method in an underground armoured cable for an electrical panel. The product and method used for this repair could allow moisture into the spliced cable and cause an electrical fault between the conductors when the cable is energized. An electrical fault would cause damage to the underground conductors and would also have the potential to cause equipment damage within the building if the over current device did not operate in time to limit the electrical fault. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Unapproved_cable_splice.png | file://x:/photopub/docs/0000000474/74895e5f-b13c-4c2c-bd19-7fb08adcb049.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1c966b7_4dec_424c_b829_c61878f91ba6
ELIN-598837-2016 | EL-368982-2016 | 6/30/2016 10:29:17 AM | ASSESS: EL: Final | png | #asFound | EL138 | Installation of electrical equipment General: boxes are not accessible. | 3 | 3 | The 30 amp 120/240 volt dryer receptacle is not accessible and hidden behind a cabinet, the dryer cord is run though the cabinet , this is a thermal hazard | 3 | Installation of electrical equipment General: boxes are not accessible. | Dryer_receptacle.png | file://x:/photopub/docs/0000000452/149587e2-9bf9-44ad-ae21-7f4ca17bf047.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b1bff1e_cfec_4dc2_bdf5_5f6073406c2c
ELIN-633771-2016 | EL-420502-2016 | 8/23/2016 9:17:37 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | A new duplex under construction has been authorized for connection to the utility. The panel boards are exposed to the open environment without adequate protection from rain and are accessible to the general public. Unpredictable damage can occur when overcurrent devices and panel parts are wetted and persons can be hurt or property damage can occur if panels are not installed to restrict access. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | No_roof_open_to_sky__no_lockable_cover.png | file://x:/photopub/docs/0000000474/b555c1c9-7b09-4ef6-bf16-fcca2e6dcdf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b9eccc4_a491_4d3c_bc98_50222d959bc1
ELIN-611174-2016 | EL-274572-2015 | 7/14/2016 2:16:06 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Where currents are imposed on the grounding conductor, the magnetic field encircling the conductor is increased by magnetic material surrounding the conductor unless the magnetic material is bonded at both ends. the increased magnetic field correspondingly increases the inductive voltage drop Thus increasing conductor impedance. Non-magnetic material such as PVC and aluminum are not affected by magnetic fields and accordingly need not be bonded at both ends at both ends as shown in the illustration of appendix B rule 10 806 subrule 4. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Name_plate__name_plate_rating_of_diesel_generator.png | file://x:/photopub/docs/0000000456/7b4ee49c-45d2-4b61-88ce-0973d94bc105.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f447fba_9561_4dc3_8ad3_c40765dc193a
ELIN-611174-2016 | EL-274572-2015 | 7/14/2016 2:16:06 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Where currents are imposed on the grounding conductor, the magnetic field encircling the conductor is increased by magnetic material surrounding the conductor unless the magnetic material is bonded at both ends. the increased magnetic field correspondingly increases the inductive voltage drop Thus increasing conductor impedance. Non-magnetic material such as PVC and aluminum are not affected by magnetic fields and accordingly need not be bonded at both ends at both ends as shown in the illustration of appendix B rule 10 806 subrule 4. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4160_diesel__4160_diesel_generator_grounding_conductor_installed_in_steel_conduit.png | file://x:/photopub/docs/0000000456/426ca7dd-7336-42c7-b240-fd42d25ff320.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f447fba_9561_4dc3_8ad3_c40765dc193a
GAUP-662965-2016 | UW-437362-2016 | 9/14/2016 10:32:49 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | Construction heater running, regulator not compliant, over pressurized and vented next to open flame. In the event of regulator relieving, source of ignition to light the gas. | 4 | Ignition sources present with-in minimum distance required | Wonowon_heater.png | file://x:/photopub/docs/0000000484/8107a8c3-3dc8-447b-a6d8-57163a1e2f2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df4f0185_a37c_4771_90f0_d8c226eec6df
BPVOP-616997-2016 | 2276589 | 7/22/2016 11:43:19 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety valves and pressure relief devices require periodic service or replacement. I found no record of testing/service/replacement for safety valve on 100psi hot water boiler. Potential exists for a safety valve not to function properly in an over pressure situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Relief_valve.png | file://x:/photopub/docs/0000000460/6ed6c5f8-dca8-4b13-8366-14879b89aa2c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d893e83c_308e_4dd9_baf4_9ea4509bc65c
ELIN-632576-2016 | EL-410416-2016 | 8/19/2016 9:23:31 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumer service conductors are exceeding maximum allowable distance of 1.5 meters without being protected by breaker/fusing to main electrical panel. This could be a fire/shock hazard if it was pierced or broken due to the conductors not being protected by a breaker/fuse. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Exceeding_1_5_meters.png | file://x:/photopub/docs/0000000473/aafd5e8f-eb2f-4fce-9155-a213aedd9480.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__50a86da9_8b1d_40b4_a8d1_175f452f6a3c
BPVOP-608041-2016 | BPV-128804-2014 | 7/11/2016 10:33:56 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP184 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | 3 | 3 | During the inspection of a Hot Water Boiler with MAWP of 75 psig I found a plywood structure build on top of the boiler touching the boiler casing. In case of the boiler overheating it can cause a fire. | 3 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | Plywood_structure_built_on_the_boiler.png | file://x:/photopub/docs/0000000454/ff9de781-d216-4639-953b-51501c165025.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7003f46_b8ff_4bd2_873e_897d80b5d9ca
ELIN-661685-2016 | EL-436494-2016 | 9/13/2016 12:22:29 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound |  |  |  |  | Shock and arc flash hazard from possible damage of service cable at ground level. |  |  | Cable2.png | file://x:/photopub/docs/0000000484/c1c7cbdd-75ac-4a9b-9770-abdae24760cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9663f13_838a_42bc_bdc8_7a8d95035476
ELIN-661685-2016 | EL-436494-2016 | 9/13/2016 12:22:29 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound |  |  |  |  | Shock and arc flash hazard from possible damage of service cable at ground level. |  |  | Box2.png | file://x:/photopub/docs/0000000484/2f739562-8644-4a21-958d-1191b425fe24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9663f13_838a_42bc_bdc8_7a8d95035476
ELIN-661685-2016 | EL-436494-2016 | 9/13/2016 12:22:29 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound |  |  |  |  | Shock and arc flash hazard from possible damage of service cable at ground level. |  |  | Wall1.png | file://x:/photopub/docs/0000000484/4c7dbcfe-997f-4a42-b38a-e71e32820c62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9663f13_838a_42bc_bdc8_7a8d95035476
GAIN-645609-2016 | GA-277105-2015 | 9/14/2016 1:46:05 PM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | While assessing this job I found several regulator relief vents located too close to the mechanical air intakes of the units they are serving. Should the units be running and the regulators relieve, raw gas could be drawn into the building. This would create a fire or explosion hazard. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Vent_termination.png | file://x:/photopub/docs/0000000485/38cf44bf-e1d4-402c-88c3-ae75ab0269e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81e7838e_fcc8_4424_9e1f_a2f3104cc5a9
GAIN-645609-2016 | GA-277105-2015 | 9/14/2016 1:46:05 PM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | While assessing this job I found several regulator relief vents located too close to the mechanical air intakes of the units they are serving. Should the units be running and the regulators relieve, raw gas could be drawn into the building. This would create a fire or explosion hazard. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Relief_vent_clearance_.png | file://x:/photopub/docs/0000000485/1f547a73-a78f-4abc-877f-93e30116dfef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81e7838e_fcc8_4424_9e1f_a2f3104cc5a9
ELIN-640661-2016 | EL-428856-2016 | 8/30/2016 12:34:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Conductors in the wire way may get damaged from use of GFCI receptacles located in the wire way. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Temp_service1.png | file://x:/photopub/docs/0000000477/e37a23f9-8d17-41c9-83d5-0675792f2c94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f780662e_e813_4e2c_8081_7f93fbe01b02
ELIN-640661-2016 | EL-428856-2016 | 8/30/2016 12:34:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Conductors in the wire way may get damaged from use of GFCI receptacles located in the wire way. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Wireway1.png | file://x:/photopub/docs/0000000477/9181b1fb-74ed-4e98-950e-1aee6d59d465.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f780662e_e813_4e2c_8081_7f93fbe01b02
ELIN-640661-2016 | EL-428856-2016 | 8/30/2016 12:34:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Conductors in the wire way may get damaged from use of GFCI receptacles located in the wire way. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Wireway2.png | file://x:/photopub/docs/0000000477/5044c3d7-c15f-45aa-90e1-6993561bfe9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f780662e_e813_4e2c_8081_7f93fbe01b02
ELIN-640661-2016 | EL-428856-2016 | 8/30/2016 12:34:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Conductors in the wire way may get damaged from use of GFCI receptacles located in the wire way. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Temp_service2.png | file://x:/photopub/docs/0000000477/e53e9f3b-9c29-48e2-a6c5-edabb862d7f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f780662e_e813_4e2c_8081_7f93fbe01b02
ELIN-640661-2016 | EL-428856-2016 | 8/30/2016 12:34:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Conductors in the wire way may get damaged from use of GFCI receptacles located in the wire way. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Feeder_to_trailer.png | file://x:/photopub/docs/0000000477/a4ded056-f1d3-43b4-8d07-ddd71c9eb75b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f780662e_e813_4e2c_8081_7f93fbe01b02
ELIN-657232-2016 | EL-406828-2016 | 9/8/2016 3:58:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | The service cable is not protected as it exits the ground inside the wall. Without this protection a nail could penetrate the cable armour and short the service conductors that have no over current protection. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Service_cable_.png | file://x:/photopub/docs/0000000482/539ab447-6cd4-4ad6-bdd0-e852389b5764.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6bc7ea28_5c30_47b8_9e06_f60004cda088
ELIN-594754-2016 | EL-398116-2016 | 6/20/2016 8:56:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found exposed energized conductors hanging out of luminaires from ceiling and out of outlet boxes in walls. When conductors are connected to power supply system and are energized and exposed and not installed safely and not in full compliance with the code, the electrical equipment is an electrical shock or fire hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_conductors_hanging_from_box1.png | file://x:/photopub/docs/0000000457/dc53d8f2-3306-4598-872b-d2e66ab15dbe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__35153f7c_3d58_48ae_8d4f_044ef783445a
ELIN-594754-2016 | EL-398116-2016 | 6/20/2016 8:56:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found exposed energized conductors hanging out of luminaires from ceiling and out of outlet boxes in walls. When conductors are connected to power supply system and are energized and exposed and not installed safely and not in full compliance with the code, the electrical equipment is an electrical shock or fire hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_conductors_hanging_from_ceiling_or_luminaire2.png | file://x:/photopub/docs/0000000457/8ecee88c-bd93-42bb-96e8-f52fb66b4b23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__35153f7c_3d58_48ae_8d4f_044ef783445a
ELIN-594754-2016 | EL-398116-2016 | 6/20/2016 8:56:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found exposed energized conductors hanging out of luminaires from ceiling and out of outlet boxes in walls. When conductors are connected to power supply system and are energized and exposed and not installed safely and not in full compliance with the code, the electrical equipment is an electrical shock or fire hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_conductors_hanging_from_outlet_box2.png | file://x:/photopub/docs/0000000457/1a87b9c9-a66b-475c-9d48-95256a69cc6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__35153f7c_3d58_48ae_8d4f_044ef783445a
ELIN-625019-2016 | EL-395407-2016 | 8/17/2016 9:24:57 AM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Main distribution is bonded twice this will result in objectionable current flow. This condition could result in thermal or shock hazards. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Service_is_bonded_twice_.png | file://x:/photopub/docs/0000000472/ac6fb5ab-a962-4237-8e47-7595f0be680c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b60e152_7c91_4b2c_b10f_232bf3618767
ELIN-625019-2016 | EL-395407-2016 | 8/17/2016 9:24:57 AM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Main distribution is bonded twice this will result in objectionable current flow. This condition could result in thermal or shock hazards. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | No_bushing.png | file://x:/photopub/docs/0000000472/bcec926e-1291-4f4a-8f4c-b6e07593bf2d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b60e152_7c91_4b2c_b10f_232bf3618767
ELIN-625019-2016 | EL-395407-2016 | 8/17/2016 9:24:57 AM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Main distribution is bonded twice this will result in objectionable current flow. This condition could result in thermal or shock hazards. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Correct_bonding.png | file://x:/photopub/docs/0000000472/fec671a5-9b18-4c1b-b650-320b8a5d0279.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b60e152_7c91_4b2c_b10f_232bf3618767
BPVOP-604618-2016 | 2270318 | 7/4/2016 9:32:24 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP202 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | 2 | 2 | Upon assessment of boiler it is determined that refractory at burner throat has broken/ fallen off. Refractory lining will deteriorate further resulting in overheating of metal parts if refractory is not repaired. | 2 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | Fallen_off_refractory_at_burner_throat.png | file://x:/photopub/docs/0000000451/2ea4bb2a-aed7-43b0-815c-c18f725fe9bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46e90d29_98cb_4eb9_a925_9d7bacbab180
BPVOP-603108-2016 | 2271384 | 6/29/2016 11:07:40 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP140 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | 1 | 1 |  | 1 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | Pressure_gauge_range_not_to_code.png | file://x:/photopub/docs/0000000451/039cea44-5728-44cc-8b57-3ed8493fdc94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0940ca29_442d_4a02_9fae_edcd7bffd89b
ELIN-638039-2016 | EL-161617-2014 | 9/8/2016 1:40:13 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 3 | Fire hazard from conductors not enclosed in outlet box or cable. | 3 | Conductors, No expansion joint or not installed correctly. | Photo_of_top_of_recep_in_cabinetry.png | file://x:/photopub/docs/0000000482/5d0a8ca4-4edc-4d36-9db9-797c91e4620c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93718cd2_e860_4afe_8bc9_78ddb49b7e27
ELIN-636292-2016 | UW-427679-2016 | 8/22/2016 12:12:42 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Before any regulated electrical work begins, it is required that a electrical permit be obtained and inspections to be requested at each phase of work. In this installation in the garage of a single family home, electrical equipment and cable was installed for a horticultural project with out a permit and with out inspections. The incorrect installation of the electrical equipment, building cable and the use of flexible cord (extension cords) as permanent wiring can create a shock hazard to persons and a potential fire hazard for persons and property. | 4 | Conductors, Misuse of flexible cords. | Lighting_ballasts.png | file://x:/photopub/docs/0000000474/04b6d2ca-6b40-4cbf-8fbc-2459ae38c721.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8caad15d_57cf_41e4_8c4c_99dbb16845ca
ELIN-636292-2016 | UW-427679-2016 | 8/22/2016 12:12:42 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Before any regulated electrical work begins, it is required that a electrical permit be obtained and inspections to be requested at each phase of work. In this installation in the garage of a single family home, electrical equipment and cable was installed for a horticultural project with out a permit and with out inspections. The incorrect installation of the electrical equipment, building cable and the use of flexible cord (extension cords) as permanent wiring can create a shock hazard to persons and a potential fire hazard for persons and property. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_for_permanent_wiring.png | file://x:/photopub/docs/0000000474/163d63a9-56ac-4516-aacd-9ddac35408ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8caad15d_57cf_41e4_8c4c_99dbb16845ca
BPVOP-608069-2016 | 3076394 | 7/11/2016 11:55:28 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon the assessment of an Electric Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 2004 and was overdue as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_2004.png | file://x:/photopub/docs/0000000454/3412fb49-aeaf-47b0-937d-71d594b1d259.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__680af44f_99ff_4bd6_9eec_aa64f2bfe9bd
BPVOP-608044-2016 | BPV-128805-2014 | 7/11/2016 11:46:06 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP184 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | 3 | 3 | During the inspection of a Hot Water Boiler with MAWP of 75 psig I found a plywood structure build on top of the boiler touching the boiler casing. In case of the boiler overheating it can cause a fire. | 3 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | Plywood.png | file://x:/photopub/docs/0000000454/e2be4b9a-9908-4d70-87b0-cf8e0ce86fcf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bca450a2_d34b_4119_8647_41bb72bad52c
ELOP-636992-2016 | 1107 | 9/1/2016 10:21:24 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL154 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | 2 | 2 |  | 2 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | Motor_feed_connector.png | file://x:/photopub/docs/0000000479/1f08cce8-25b9-409f-89c7-b8e05592c4e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55f658cf_d9af_4175_89a0_bbe763125d47
ELIN-608757-2016 | EL-352139-2016 | 7/12/2016 11:01:44 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | System grounding conductor is not continuos between system grounding electrode and point of attachment to system. In the event of a fault this does not provide for a low impedance path to ground which could prevent the system protection devices from operating as designed. This poses a serious risk of personal injury (shock) or property damage (thermal event). | 4 | Installation Grounding; conductor is not continuous. | View01_system_grounding_conductor.png | file://x:/photopub/docs/0000000455/7be14ea8-f65a-42c4-be5f-4b2f5e78cf8d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e87e14c7_f1d2_4b10_942a_932b25696439
GAWP-627573-2016 | GA-381697-2016 | 8/9/2016 3:08:19 PM | ASSESS: GA Work In Progress | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | Commercial kitchen equipment with casters install with unapproved appliance connectors. Repeated movement of the appliances may result in the failure of the appliance connector and gas leaking into the occupied space. | 2 | Certified appliance connector installed but not approved for application | Appliance_connector.png | file://x:/photopub/docs/0000000468/a728e1c0-9dc2-491c-843b-37967429dbbd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd2d6803_bc84_4800_a598_3f585e8c021b
GAIN-620231-2016 | GA-407146-2016 | 8/10/2016 10:26:42 AM | ASSESS: GA: Rough-In | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Found several street elbows used in the piping system. These elbows are prone to breaking after being overtightened and could result in a gas leak. | 3 | Non-compliant material/fittings installed | Street_elbow.png | file://x:/photopub/docs/0000000469/79480e43-afc3-45d4-9c5c-7fe23f519a49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5660c6cd_712a_4c68_b4da_721e85110971
GAIN-609292-2016 | GA-397932-2016 | 7/11/2016 2:02:12 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | 2lb-"w.c. Regulator not installed according to manufacturer's installation instructions. Regulator may not operate as designed if not installed as per installation instructions. | 2 | Not installed according to certified installation instructions | Regulator_not_installed_as_per_manufacturers_installation_instructions.png | file://x:/photopub/docs/0000000454/ae252142-a342-45bb-a4cc-cd22cd97f85d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89f7ee00_05c2_402b_8ccb_9b2660a4e200
ELIN-594754-2016 | EL-398116-2016 | 6/20/2016 8:56:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found exposed energized conductors hanging out of luminaires from ceiling and out of outlet boxes in walls. When conductors are connected to power supply system and are energized and exposed and not installed safely and not in full compliance with the code, the electrical equipment is an electrical shock or fire hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_conductors_hanging_from_ceiling_or_luminaire1.png | file://x:/photopub/docs/0000000457/81b89c64-838d-4d85-97d1-e7dc296f3b08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__35153f7c_3d58_48ae_8d4f_044ef783445a
ELIN-659114-2016 | EL-435754-2016 | 9/12/2016 12:02:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Damaged GFCI receptacle for temp power and no extra duty in use covers on outlets. This is a shock hazard. 120 Volt. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Damaged_GFCI_receptacle_and_no_in_use_cover.png | file://x:/photopub/docs/0000000484/422cd31b-9172-4b6c-88fe-e2740f5095f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e9c10fe8_1c4a_46f1_9b6a_7820c681845c
EDOP-625672-2016 | 2038082 | 8/4/2016 1:51:45 PM | ASSESS: ED OP: Call | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | Outstanding BCSA Safety Order SO-ED 2013-01. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | GriffinController.png | file://x:/photopub/docs/0000000467/81a6c656-9615-49a7-b3d1-679aae4cc7f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6dcf20c_9ec7_4b98_9e4a_c1a3297bbd3b
EDOP-625672-2016 | 2038082 | 8/4/2016 1:51:45 PM | ASSESS: ED OP: Call | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | Outstanding BCSA Safety Order SO-ED 2013-01. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | GriffinDataPlate.png | file://x:/photopub/docs/0000000467/a3e980b0-fe9a-433b-a2e6-b4324508d47e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6dcf20c_9ec7_4b98_9e4a_c1a3297bbd3b
ELIN-640861-2016 | EL-345609-2016 | 8/30/2016 6:58:08 AM | ASSESS: EL: Final | png | #asFound | EL039 | Equipment is not marked / identified Multiple service boxes not marked. | 2 | 2 |  | 2 | Equipment is not marked / identified Multiple service boxes not marked. | View01_meter_base_.png | file://x:/photopub/docs/0000000478/b330eb7b-4806-4086-b79e-6456144bdd0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3835364_dc94_48cb_84d4_e21e757f03fb
ELIN-599029-2016 | EL-401372-2016 | 7/6/2016 10:54:29 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Weatherhead_beside_Clevis_bolt.png | file://x:/photopub/docs/0000000452/ee3b585c-084c-4742-94e4-1b57fd51b2de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3887db4_1292_4b65_a47f_bf0c36448ad5
ELIN-599029-2016 | EL-401372-2016 | 7/6/2016 10:54:29 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Guy-wire_guard_missing.png | file://x:/photopub/docs/0000000452/5e9d6d87-093f-4a9e-ac78-ac8f95a0547b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3887db4_1292_4b65_a47f_bf0c36448ad5
ELIN-599029-2016 | EL-401372-2016 | 7/6/2016 10:54:29 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | No_sealing_ring.png | file://x:/photopub/docs/0000000452/885b8fb8-c104-4488-8e81-0dae7b12ee22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3887db4_1292_4b65_a47f_bf0c36448ad5
ELIN-599029-2016 | EL-401372-2016 | 7/6/2016 10:54:29 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Non-approved_mounting_equipt.png | file://x:/photopub/docs/0000000452/34f05e0c-2405-4dd3-8fe5-d536ad1f89a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3887db4_1292_4b65_a47f_bf0c36448ad5
GAIN-606431-2016 | GA-401429-2016 | 7/6/2016 12:26:11 PM | ASSESS: GA: Rough-In | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 2 | Underground tubing exiting a building below grade. In the event of a leak on the underground tubing gas could enter the occupied space undetected and cause a fire or explosion. | 3 | Underground piping entering a building below grade (unapproved) | Underground_tubing_entering_below_grade.png | file://x:/photopub/docs/0000000452/e8125147-fbef-41b8-bed3-f419f4577d73.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15a6e1e0_3116_43b1_bae8_4d5626427732
GAIN-601027-2016 | GA-395149-2016 | 7/6/2016 12:13:22 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Piping must be secured when connecting to a certified gas connector to prevent damage to piping caused by movement of appliance. | 2 | Physical protection of piping and tubing absent. | Unsecured_piping.png | file://x:/photopub/docs/0000000452/551fc9ce-1045-45db-ba56-369e7425643d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b99c743_4fd8_42b4_903c_0fb99e304b0b
GAIN-634711-2016 | GA-426586-2016 | 8/23/2016 11:27:08 AM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | Found bird screen on combustion air intake for furnace completely plugged with debris. This could lead to the production of carbon monoxide and could be harmful to occupants of the home. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Combustion_air.png | file://x:/photopub/docs/0000000474/fc01a306-af76-4dea-93ef-d7b0a1a78bb4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0409b7e_92e3_4aef_a0b6_dc8b61ab301d
ELIN-607371-2016 | EL-402352-2016 | 7/13/2016 11:13:53 AM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | Approval label missing from sign | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Signs_on_building.png | file://x:/photopub/docs/0000000455/ca3cf335-0a79-42b4-9542-7149aafb0314.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__603f84bf_a016_4321_9ae8_1078381a368f
ELIN-599751-2016 | EL-291409-2015 | 7/19/2016 5:10:24 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The electrical code requires that electrical equipment be approved for the specific purpose in which it is intended. When electrical equipment is not used for the correct purpose, a hazard can develop. In this installation for a single family residence, wall mounted plastic lamp holders with plastic guards where installed at the entrance to the crawl space and in the closet for the hot water tank. The lamp holders did not have a lip for the plastic guards to mount to. This allowed the plastic guards to slip off the lamp holder and rest on the lamp. When the light is turned on, the heat from the lamp can melt the plastic guard and create a fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Front_of_house.png | file://x:/photopub/docs/0000000459/cd25bced-b935-4255-8cdb-cc2220adbee4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43860190_a9fe_4c97_955d_41f8812b39a1
ELIN-599751-2016 | EL-291409-2015 | 7/19/2016 5:10:24 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The electrical code requires that electrical equipment be approved for the specific purpose in which it is intended. When electrical equipment is not used for the correct purpose, a hazard can develop. In this installation for a single family residence, wall mounted plastic lamp holders with plastic guards where installed at the entrance to the crawl space and in the closet for the hot water tank. The lamp holders did not have a lip for the plastic guards to mount to. This allowed the plastic guards to slip off the lamp holder and rest on the lamp. When the light is turned on, the heat from the lamp can melt the plastic guard and create a fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Fixture_in_hot_water_tank_closet_.png | file://x:/photopub/docs/0000000459/420c914b-266d-4019-a401-a34a790e53f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43860190_a9fe_4c97_955d_41f8812b39a1
ELIN-599751-2016 | EL-291409-2015 | 7/19/2016 5:10:24 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The electrical code requires that electrical equipment be approved for the specific purpose in which it is intended. When electrical equipment is not used for the correct purpose, a hazard can develop. In this installation for a single family residence, wall mounted plastic lamp holders with plastic guards where installed at the entrance to the crawl space and in the closet for the hot water tank. The lamp holders did not have a lip for the plastic guards to mount to. This allowed the plastic guards to slip off the lamp holder and rest on the lamp. When the light is turned on, the heat from the lamp can melt the plastic guard and create a fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Fixture_in_stair_well_closet_with_wire_guard_against_light_bulb.png | file://x:/photopub/docs/0000000459/b8793354-f74c-4c90-bbff-032ff9982bcc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43860190_a9fe_4c97_955d_41f8812b39a1
ELIN-599751-2016 | EL-291409-2015 | 7/19/2016 5:10:24 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The electrical code requires that electrical equipment be approved for the specific purpose in which it is intended. When electrical equipment is not used for the correct purpose, a hazard can develop. In this installation for a single family residence, wall mounted plastic lamp holders with plastic guards where installed at the entrance to the crawl space and in the closet for the hot water tank. The lamp holders did not have a lip for the plastic guards to mount to. This allowed the plastic guards to slip off the lamp holder and rest on the lamp. When the light is turned on, the heat from the lamp can melt the plastic guard and create a fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Light_fixture_under_stair_well.png | file://x:/photopub/docs/0000000459/e8f75043-a5ec-4167-b6d4-c0f84e76ce58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43860190_a9fe_4c97_955d_41f8812b39a1
ELIN-599751-2016 | EL-291409-2015 | 7/19/2016 5:10:24 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The electrical code requires that electrical equipment be approved for the specific purpose in which it is intended. When electrical equipment is not used for the correct purpose, a hazard can develop. In this installation for a single family residence, wall mounted plastic lamp holders with plastic guards where installed at the entrance to the crawl space and in the closet for the hot water tank. The lamp holders did not have a lip for the plastic guards to mount to. This allowed the plastic guards to slip off the lamp holder and rest on the lamp. When the light is turned on, the heat from the lamp can melt the plastic guard and create a fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Fixture_in_hot_water_tank_closet_with_plastic_guard_touching_60W_bulb.png | file://x:/photopub/docs/0000000459/3e43f373-ac0c-404b-b968-c14ba5f2ab8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43860190_a9fe_4c97_955d_41f8812b39a1
ELIN-599751-2016 | EL-291409-2015 | 7/19/2016 5:10:24 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The electrical code requires that electrical equipment be approved for the specific purpose in which it is intended. When electrical equipment is not used for the correct purpose, a hazard can develop. In this installation for a single family residence, wall mounted plastic lamp holders with plastic guards where installed at the entrance to the crawl space and in the closet for the hot water tank. The lamp holders did not have a lip for the plastic guards to mount to. This allowed the plastic guards to slip off the lamp holder and rest on the lamp. When the light is turned on, the heat from the lamp can melt the plastic guard and create a fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Fixture_in_closet_under_stairs_with_plastic_guard_touching_60W_light_bulb.png | file://x:/photopub/docs/0000000459/63542ba8-3cee-4321-a098-757adcde07cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43860190_a9fe_4c97_955d_41f8812b39a1
ELIN-625035-2016 | EL-420373-2016 | 8/5/2016 3:08:58 PM | ASSESS: EL: Service Connection | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | The wiring and overcurrent protection are not adequately sized for the load to be connected. This could cause a potential overloading issue which in turn can cause overheating of the wiring. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 50A_receptacle.png | file://x:/photopub/docs/0000000466/fd699560-b5d8-4256-9013-df70f4477725.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__148d1d3b_09f4_49a5_a2d2_73d5a5ed11b6
EDIN-607850-2016 | ED-345966-2016 | 7/18/2016 11:10:05 AM | ASSESS: ED IN: Acceptance | png | #asFound | ED052 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 2 | 2 | Permanent guardrails to be installed (Level 2) | 2 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 40455_40456_as_found1.png | file://x:/photopub/docs/0000000457/21d77547-00ff-4acf-bcd4-c719302781b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f3167ac_5c46_4f32_8bdc_e6cfaa900384
EDIN-607872-2016 | ED-345982-2016 | 7/13/2016 2:35:05 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED052 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 2 | 2 | Permanent guardrails to be installed (Level 2) | 2 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 40456-as_found.png | file://x:/photopub/docs/0000000457/238525bb-be08-402e-9ce4-cec41255e35d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c15c987_f0fb_425b_b43c_9e8cc7901920
EDIN-607850-2016 | ED-345966-2016 | 7/18/2016 11:10:05 AM | ASSESS: ED IN: Acceptance | png | #asFound | ED052 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 2 | 2 | Permanent guardrails to be installed (Level 2) | 2 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 40455-40456-as_found.png | file://x:/photopub/docs/0000000457/8ffdd242-979c-4657-902e-419ccd36cb90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f3167ac_5c46_4f32_8bdc_e6cfaa900384
EDIN-607872-2016 | ED-345982-2016 | 7/13/2016 2:35:05 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED052 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 2 | 2 | Permanent guardrails to be installed (Level 2) | 2 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 40456-as_found2.png | file://x:/photopub/docs/0000000457/cffa7b61-7c13-4ad7-b9af-bcde6a829d94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c15c987_f0fb_425b_b43c_9e8cc7901920
ELIN-599751-2016 | EL-291409-2015 | 7/19/2016 5:10:24 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The electrical code requires that electrical equipment be approved for the specific purpose in which it is intended. When electrical equipment is not used for the correct purpose, a hazard can develop. In this installation for a single family residence, wall mounted plastic lamp holders with plastic guards where installed at the entrance to the crawl space and in the closet for the hot water tank. The lamp holders did not have a lip for the plastic guards to mount to. This allowed the plastic guards to slip off the lamp holder and rest on the lamp. When the light is turned on, the heat from the lamp can melt the plastic guard and create a fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Fixture_in_hot_water_tank_closet.png | file://x:/photopub/docs/0000000459/498953e2-4a75-49fb-a69e-9a814333993b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43860190_a9fe_4c97_955d_41f8812b39a1
ELIN-629049-2016 | EL-421951-2016 | 8/17/2016 12:51:06 PM | ASSESS: EL: Final | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 4 | In an existing modular home, a 120volt 15amp 2-gang box containing a gfci receptacle and switch is not fixed to the wall as required. This can lead to equipment damage. Pic attached. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | Heat_trace.png | file://x:/photopub/docs/0000000473/41444496-1518-4760-8678-68c7045a880f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48b3f3fc_8ace_443a_b513_398fee4f7b90
ELIN-605655-2016 | EL-367186-2016 | 7/14/2016 7:31:09 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | 120 and 240 volt branch circuits fed from a residential panel board rated 200 amps and 240 volts are installed. The branch circuit cables are bundled with as many as 16 cables in contact up to 12 meters. Cables can overheat when proper spacing and routing is not maintained and cause damage to property or injury to persons | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Up_to_16_cables_bundled_up_to_12_meters_multiple_locations_second_time.png | file://x:/photopub/docs/0000000456/c41d6dd6-9e03-4bb1-a0cb-b7e9fd5970f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__711cf1ad_acc7_4196_88cd_716fac02e686
BPVOP-628922-2016 | 4232586 | 8/11/2016 9:45:08 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | Fireside pressures too high for the burner to shell seal, seal has ruptured and allows flue gases into the boiler enclosure and equipment room | 4 | 5.1.0 In service proc/process - Casing leakage | Casing_to_Burner_Seal_Ruptured.png | file://x:/photopub/docs/0000000470/b9e32dfb-337e-4f94-aec8-6b82b8106993.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae08d6d6_7db5_470f_a8f3_f15fef1d5fc7
ELHE-630345-2016 | HE-423856-2016 | 8/12/2016 3:00:25 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | A Consumer power pole is leaning at a severe angle which suggests a imminent failure of the structure of the pole. The support guy wire is at the rear of the pole and only affords some structural strength to the pole in this location. Structural Failure of the pole could likely lead to a grass fire and a shock hazard to livestock in the pasture field. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Pole_guy_wire_at_rear.png | file://x:/photopub/docs/0000000470/d34d708b-95ef-457d-a14d-509903583615.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e14f4402_5cdd_4789_91a0_feb60c5600f9
ELHE-630345-2016 | HE-423856-2016 | 8/12/2016 3:00:25 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | A Consumer power pole is leaning at a severe angle which suggests a imminent failure of the structure of the pole. The support guy wire is at the rear of the pole and only affords some structural strength to the pole in this location. Structural Failure of the pole could likely lead to a grass fire and a shock hazard to livestock in the pasture field. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Existing_Well_pump_service.png | file://x:/photopub/docs/0000000470/1bf99aa2-1b19-4007-bb61-a06d801186ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e14f4402_5cdd_4789_91a0_feb60c5600f9
BPVIN-632690-2016 | BPV-425382-2016 | 8/17/2016 12:19:34 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP002 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | 5 | 5 | The name plate of every boiler and pressure vessel shall be stamped in accordance with the requirements of the appropriate section of the American Society of Mechanical Engineers Code. The stamping shall include the Canadian Registration Number, identification traceable to the manufacture and design characteristics. I found no stamping or certification markings on eight unfired pressure vessels. Potential exists for an incident due to design limits being unknown. | 5 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | pressure_relief_valve.png | file://x:/photopub/docs/0000000473/a19d2ec7-2bf4-4ba3-aa91-e6bbc919f634.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e2695e9_f773_48c8_b2cd_b7065a5eab9f
ELIN-634814-2016 | EL-423022-2016 | 8/25/2016 12:32:40 PM | ASSESS: EL: Final | png | #asFound | EL011 | Conductors are exposed to accidental contact by persons Overhead communication conductors, are not attached or supported adequately. | 2 | 2 |  | 2 | Conductors are exposed to accidental contact by persons Overhead communication conductors, are not attached or supported adequately. | Overhead_trip_mast.png | file://x:/photopub/docs/0000000475/1e5daad4-77be-4ee1-b2a2-37f9f3bda1dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29089206_cb49_4aa0_8150_8acd9db2ac0f
ELIN-634814-2016 | EL-423022-2016 | 8/25/2016 12:32:40 PM | ASSESS: EL: Final | png | #asFound | EL011 | Conductors are exposed to accidental contact by persons Overhead communication conductors, are not attached or supported adequately. | 2 | 2 |  | 2 | Conductors are exposed to accidental contact by persons Overhead communication conductors, are not attached or supported adequately. | Overhead_trip_mast2.png | file://x:/photopub/docs/0000000475/cdfb0ef3-a3ad-466e-8bd3-137cd8d0d2ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29089206_cb49_4aa0_8150_8acd9db2ac0f
ELIN-634814-2016 | EL-423022-2016 | 8/25/2016 12:32:40 PM | ASSESS: EL: Final | png | #asFound | EL011 | Conductors are exposed to accidental contact by persons Overhead communication conductors, are not attached or supported adequately. | 2 | 2 |  | 2 | Conductors are exposed to accidental contact by persons Overhead communication conductors, are not attached or supported adequately. | Old_service.png | file://x:/photopub/docs/0000000475/d8195953-e47a-4762-854f-3c8b7195e75a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29089206_cb49_4aa0_8150_8acd9db2ac0f
GAIN-662478-2016 | GA-397776-2016 | 9/13/2016 11:20:48 AM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | Propane Regulator installed below maximum liquid level of propane tank. The propane regulator is not designed for liquid propane, under certain conditions, (no flow of propane or changes in ambient temperatures) re-liquefaction could occur in the vapour before regulator causing the propane regulator to malfunction / or may pass liquid leading to hazardous conditions downstream. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Propane_regulator_installed_below_liquid_level.png | file://x:/photopub/docs/0000000484/06abd670-b6a5-41dc-a769-a83615e76711.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__890f0531_01d3_45a8_86d6_2f71453f91e5
ELIN-662000-2016 | EL-161617-2014 | 9/13/2016 1:42:07 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | The roof top air conditioning units do not have a dedicated circuit 20 A GFCI receptacle in close proximity to the unit. There are receptacles integral to the roof top air conditioners but when the power is shut off to the unit the power is also shut off to the service receptacles. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | WP_plug_on_RTU.png | file://x:/photopub/docs/0000000484/b4b8a754-87a0-4699-8b15-02efd2c14f82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83b93008_d45a_4657_beaa_c170a823a769
ELIN-662000-2016 | EL-161617-2014 | 9/13/2016 1:42:07 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | The roof top air conditioning units do not have a dedicated circuit 20 A GFCI receptacle in close proximity to the unit. There are receptacles integral to the roof top air conditioners but when the power is shut off to the unit the power is also shut off to the service receptacles. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | WP_plug_on_RTU_750mm.png | file://x:/photopub/docs/0000000484/a381c62d-44f3-49e9-a921-b7a9026a7067.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83b93008_d45a_4657_beaa_c170a823a769
ELIN-662128-2016 | EL-379489-2016 | 9/13/2016 7:15:59 AM | ASSESS: EL: Final | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Expansion of PVC would stress and eventually break conduit, this could result in strain and damage to the conductors causing a thermal or shock hazard . | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Service_conduit_.png | file://x:/photopub/docs/0000000484/81099832-c4cd-47b1-80ea-6d7547a58914.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b3ddd11_cbc7_4aa6_81fd_1ab06efec262
ELIN-629049-2016 | EL-421951-2016 | 8/17/2016 12:51:06 PM | ASSESS: EL: Final | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 4 | In an existing modular home, a 120volt 15amp 2-gang box containing a gfci receptacle and switch is not fixed to the wall as required. This can lead to equipment damage. Pic attached. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | Not_flush.png | file://x:/photopub/docs/0000000473/12639e2f-de2b-4507-8511-c76d333cd994.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48b3f3fc_8ace_443a_b513_398fee4f7b90
ELIN-629049-2016 | EL-421951-2016 | 8/17/2016 12:51:06 PM | ASSESS: EL: Final | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 4 | In an existing modular home, a 120volt 15amp 2-gang box containing a gfci receptacle and switch is not fixed to the wall as required. This can lead to equipment damage. Pic attached. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | AC_.png | file://x:/photopub/docs/0000000473/a7584841-11b2-4dba-8a9a-96149381a952.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48b3f3fc_8ace_443a_b513_398fee4f7b90
ELIN-610301-2016 | EL-368721-2016 | 7/13/2016 12:21:09 PM | ASSESS: EL: Final | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | An existing 100 amp 240 volt panel board has been supplied from a new residential service with 14 gauge wire suitable for 15 amps load at 240 volts. The connected loads at this panel include RV sites, electric dryer, and other loads calculated to require up to 75 amps at 240 volts. Property damage or injury to persons can result when electrical systems are not sized adequately for connected lads | 3 | Protection and control Loading of distribution equipment exceeded | Existing_loads_refed_with_14_gauge_wire_calculated_to_75_amps_as_listed_on_panel_directory.png | file://x:/photopub/docs/0000000456/5216c599-9cf0-42bf-8ab1-8ec07b335224.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89710b68_1e81_41d1_8f3a_6f3b7a3e07c8
ELIN-629205-2016 | 5452520 | 8/16/2016 5:21:54 AM | ASSESS: EL: Final | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Bonding conductor was not in conduit , an alternative ground plate was installed for load centre, but no provision to bond the panel. This scenario in the electrical system allows objectionable current flow creating thermal and shock hazards. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Panel_not_labeled_.png | file://x:/photopub/docs/0000000471/a5eb5720-e7e2-40c7-9c15-d8f602bc1d2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__314ba04d_283f_4702_aada_7538cff38fd0
ELIN-629205-2016 | 5452520 | 8/16/2016 5:21:54 AM | ASSESS: EL: Final | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Bonding conductor was not in conduit , an alternative ground plate was installed for load centre, but no provision to bond the panel. This scenario in the electrical system allows objectionable current flow creating thermal and shock hazards. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | No_bond_in_pipe.png | file://x:/photopub/docs/0000000471/6f65336f-49c1-496e-813e-426682aaa1dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__314ba04d_283f_4702_aada_7538cff38fd0
ELIN-629205-2016 | 5452520 | 8/16/2016 5:21:54 AM | ASSESS: EL: Final | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Bonding conductor was not in conduit , an alternative ground plate was installed for load centre, but no provision to bond the panel. This scenario in the electrical system allows objectionable current flow creating thermal and shock hazards. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Incomplete_lights.png | file://x:/photopub/docs/0000000471/d25e47fa-d30f-4de6-a4a5-7546b9663f37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__314ba04d_283f_4702_aada_7538cff38fd0
GAIN-640918-2016 | GA-419728-2016 | 8/30/2016 3:51:25 PM | ASSESS: GA: Rough-In | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | Venting_not_installed_as_per_manufacturers_installation_instructions.png | file://x:/photopub/docs/0000000477/4d7677cb-968c-4c78-9c48-c406b8e8920e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4592b13e_1325_406a_ae3b_c611af546e05
GAIN-623496-2016 | GA-420088-2016 | 8/9/2016 2:25:39 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | Long-term operation of boiler with low-temperature 636 venting material installed could prematurely fail when subject to high temperatures causing the vent to fail allowing products of combustion to spill into occupied space during operational life of boiler causing carbon monoxide incident | 3 | Unapproved venting material | Venting.png | file://x:/photopub/docs/0000000468/613a07d1-0efa-4b6b-a77c-3141c8b8019d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae29e03b_1000_4686_9371_71504e36e8f0
ELIN-623045-2016 | EL-415079-2016 | 8/11/2016 1:19:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The service mast only provided with 2 support clamps, the clamp required per appendix B (located at roof line) is missing and creates a weak point. This can create an equipment damage issue | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_mast.png | file://x:/photopub/docs/0000000470/ec94b4fa-cc84-4f57-a64d-cfa785b892fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c793c67_0c07_4fc7_a926_2c2a84848ac5
ELIN-638983-2016 | UW-428941-2016 | 8/25/2016 6:08:40 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Nmd90 cable installed in a wet location in a raceway that is not mechanically continuous without the proper connectors. This is a hazard as the cable is not rated for wet locations nor is it rated to be pulled into raceways, let alone raceways that are not mechanically continuous. The dry type connector used is also a shock hazard as water could enter the equipment. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | B.png | file://x:/photopub/docs/0000000475/c8db7fac-09c2-4f97-a840-63c73f31fa04.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf7967da_201c_44b4_b9de_651e8ee03373
ELIN-638983-2016 | UW-428941-2016 | 8/25/2016 6:08:40 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Nmd90 cable installed in a wet location in a raceway that is not mechanically continuous without the proper connectors. This is a hazard as the cable is not rated for wet locations nor is it rated to be pulled into raceways, let alone raceways that are not mechanically continuous. The dry type connector used is also a shock hazard as water could enter the equipment. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000475/ff227721-9970-44bd-a22f-874c547a8fb5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf7967da_201c_44b4_b9de_651e8ee03373
ELIN-638983-2016 | UW-428941-2016 | 8/25/2016 6:08:40 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Nmd90 cable installed in a wet location in a raceway that is not mechanically continuous without the proper connectors. This is a hazard as the cable is not rated for wet locations nor is it rated to be pulled into raceways, let alone raceways that are not mechanically continuous. The dry type connector used is also a shock hazard as water could enter the equipment. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | C.png | file://x:/photopub/docs/0000000475/4871b168-2df4-4b15-a075-0cb14dc59263.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf7967da_201c_44b4_b9de_651e8ee03373
ELIN-642665-2016 | EL-420070-2016 | 9/16/2016 8:56:58 AM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Image_1.png | file://x:/photopub/docs/0000000486/cfa0912c-e6a8-43d3-b79a-f9e89f411d5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b2add61d_fd25_4853_861f_5129126b6e39
ELIN-633629-2016 | EL-101292-2014 | 8/19/2016 10:27:58 AM | ASSESS: EL: Final | png | #asFound | EL016 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate | 2 | 2 | Combustible materials are stored within a room containing energized electrical equipment. This creates an additional fire hazard if electrical equipment developed a fault. | 2 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate | Storage_room_2.png | file://x:/photopub/docs/0000000473/16666a8d-f351-4a60-9707-2df7745e5166.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ab16db7_4636_48d1_9e2e_dd64cff30e63
ELIN-633629-2016 | EL-101292-2014 | 8/19/2016 10:27:58 AM | ASSESS: EL: Final | png | #asFound | EL016 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate | 2 | 2 | Combustible materials are stored within a room containing energized electrical equipment. This creates an additional fire hazard if electrical equipment developed a fault. | 2 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate | Electrical_storage_room.png | file://x:/photopub/docs/0000000473/d0d6650e-8943-4c04-9c94-a130fa0dd48a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ab16db7_4636_48d1_9e2e_dd64cff30e63
ELIN-633629-2016 | EL-101292-2014 | 8/19/2016 10:27:58 AM | ASSESS: EL: Final | png | #asFound | EL016 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate | 2 | 2 | Combustible materials are stored within a room containing energized electrical equipment. This creates an additional fire hazard if electrical equipment developed a fault. | 2 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate | Main_service.png | file://x:/photopub/docs/0000000473/3ed008c1-40da-4df7-b8a9-19ba695eeb64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ab16db7_4636_48d1_9e2e_dd64cff30e63
ELIN-633257-2016 | EL-337461-2016 | 8/19/2016 9:33:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL100 | Conductors, Mis-use of flexible cords. | 4 | 4 | The use of #6 cabtire on the 100 amp 120/240 volt feed exceeds the allowable ampacity of the cable that creates a thermal hazard. The use of the bond conductor as a current carrying conductor that is terminated at the garage sub-panel can creates a shock hazard. | 4 | Conductors, Mis-use of flexible cords. | SeaCan_cabtire_connections.png | file://x:/photopub/docs/0000000473/a54e806e-f532-4fef-8816-3f286ec03e7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f08d50b5_3fc7_4a10_98b3_dd9ee3f76120
ELOP-659794-2016 | 5239499 | 10/4/2016 11:36:58 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Cables are required to be supported within 300mm of equipment they are connected to and every 1.5M thereafter. This is required to support the cable properly at the equipment and locations between equipment so that the cables and points of attachment to equipment do not get damaged by having undue strain imposed on them and to prevent the cables from getting snagged or damaged by other moving equipment or objects. This installation of armored cables at a mill facility has multiple cables feeding motors and other equipment that are not properly supported. Left uncorrected this is a shock and fire hazard if the cables remain unsupported and conductor insulation is mechanically damaged exposing energized conductors to contact with persons or objects. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Cable_under_log_deck_building.png | file://x:/photopub/docs/0000000496/4c35c62d-73f5-43b5-9ef2-f72cfc51a9ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3FD4EC53_17B0_420E_A49B_166B084177DE
ELOP-659794-2016 | 5239499 | 10/4/2016 11:36:58 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Cables are required to be supported within 300mm of equipment they are connected to and every 1.5M thereafter. This is required to support the cable properly at the equipment and locations between equipment so that the cables and points of attachment to equipment do not get damaged by having undue strain imposed on them and to prevent the cables from getting snagged or damaged by other moving equipment or objects. This installation of armored cables at a mill facility has multiple cables feeding motors and other equipment that are not properly supported. Left uncorrected this is a shock and fire hazard if the cables remain unsupported and conductor insulation is mechanically damaged exposing energized conductors to contact with persons or objects. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Cable_at_shingle_machine_7.png | file://x:/photopub/docs/0000000496/bbcaf219-1611-43ba-a803-e3d8a7834ce1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3FD4EC53_17B0_420E_A49B_166B084177DE
ELOP-659794-2016 | 5239499 | 10/4/2016 11:36:58 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Cables are required to be supported within 300mm of equipment they are connected to and every 1.5M thereafter. This is required to support the cable properly at the equipment and locations between equipment so that the cables and points of attachment to equipment do not get damaged by having undue strain imposed on them and to prevent the cables from getting snagged or damaged by other moving equipment or objects. This installation of armored cables at a mill facility has multiple cables feeding motors and other equipment that are not properly supported. Left uncorrected this is a shock and fire hazard if the cables remain unsupported and conductor insulation is mechanically damaged exposing energized conductors to contact with persons or objects. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Improperly_supported_teck_cable_.png | file://x:/photopub/docs/0000000496/b436929d-caf1-44f3-b3ce-c90f7de8a9ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3FD4EC53_17B0_420E_A49B_166B084177DE
GAIN-701676-2016 | GA-464869-2016 | 11/18/2016 2:28:33 PM | ASSESS: GA: Final | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | The plastic portion of the underground line riser exposed above ground and tracer wire is still on the roll and not in trench. Plastic gas line deteriorates if exposed to UV radiation from sunlight. Over time the line could deteriorate and possibly fail leading to a release of gas. The tracer wire should be in the trench with the pipe for locating the gas line. The lack of tracer wire does not allow the underground line to be detected. | 3 | Code prohibited practices or materials | Underground_line_and_tracer_wire_roll.png | file://x:/photopub/docs/0000000518/e07d9185-ea7d-4bba-88ef-7e91b0cbb647.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c37441f_b77d_4f4d_a2b3_b1b323a0a6ea
GAIN-671974-2016 | GA-436905-2016 | 10/5/2016 2:01:40 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | A combustion air intake installed 6" above finished grade may get blocked in the winter by snowfall as well as accumulation of snow falling from roof causing burner to be choked of air. In this installation the burner is sealed and a pressure switch will shutdown appliance. However choking of air could cause damage to the burner element inside heat exchanger. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Comb_air_too_close_to_grade.png | file://x:/photopub/docs/0000000496/294d5398-6a8b-4d6f-8178-5c2588b02a4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f0c3470_46d9_4799_afb6_2e9a47ef89b7
GAIN-675552-2016 | GA-428246-2016 | 10/3/2016 3:21:58 PM | ASSESS: GA: Rough-In | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | Improper grade on venting system. Condensate can deteriorate gasket material if not installed with appropriate grade causing leakage of flue products into occupied space. | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Improper_grade.png | file://x:/photopub/docs/0000000494/d5373279-bee7-4c3a-a0ca-dfd0b90a880a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a82bf9c4_d99a_4dd6_a529_26d391d595e6
GAIN-676713-2016 | GA-382470-2016 | 10/3/2016 4:37:52 PM | ASSESS: GA: Final | png | #asFound | GA093 | Under sized system regulator for multiple appliances = < 10% | 3 | 3 | Under fired appliances due to regulator being undersized. Appliances could be under fired causing carbon monoxide production due to insufficient fuel supply. | 3 | Under sized system regulator for multiple appliances = < 10% | Undersized_regulator.png | file://x:/photopub/docs/0000000494/45d18f44-0766-401a-83ab-a5753a6681db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__154205d2_3135_4366_9eb6_817b8a7459cb
GAHE-670429-2016 | HE-442268-2016 | 10/18/2016 12:23:27 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Building_piping_system_under_strain.png | file://x:/photopub/docs/0000000490/7164c396-4b49-4455-8202-a1f94cfaaaf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2f44fc7_7e31_4056_9214_decd05bb83f2
GAHE-670429-2016 | HE-442268-2016 | 10/18/2016 12:23:27 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Entry_location.png | file://x:/photopub/docs/0000000490/9370fa7b-fa2a-4df4-b6c1-d82cd5bdd7a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2f44fc7_7e31_4056_9214_decd05bb83f2
GAHE-670429-2016 | HE-442268-2016 | 10/18/2016 12:23:27 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Entry_location_below_grade_.png | file://x:/photopub/docs/0000000490/6f6d4814-5cf7-4326-852d-68cdf89d1f69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2f44fc7_7e31_4056_9214_decd05bb83f2
GAHE-670429-2016 | HE-442268-2016 | 10/18/2016 12:23:27 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Building_seal_and_sleeve_damaged.png | file://x:/photopub/docs/0000000490/1b6e310f-11db-48ca-8a06-582dd95c641d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2f44fc7_7e31_4056_9214_decd05bb83f2
ELIN-680598-2016 | EL-448892-2016 | 10/13/2016 11:20:32 AM | ASSESS: EL: Final | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Pic_1.png | file://x:/photopub/docs/0000000501/1dfa9e55-e81b-406a-8e13-0d648e1c9c2b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c0a4f1f_5d80_4798_8cc7_4a4a62dd843b
ELIN-668116-2016 | EL-440629-2016 | 9/29/2016 4:56:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 3 | The 60 amp 120/240 volt main breaker exceeds both the 50 ampere rating of the line side conductors of the main switch and the 50 ampere rating of the receptacle on the load side, this can create a thermal hazard | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Main_breaker.png | file://x:/photopub/docs/0000000492/8cdd9175-0088-4be1-ae8a-da84e1bda0f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe0cfeea_1c16_42c6_bf3e_b976780c3faf
ELIN-668116-2016 | EL-440629-2016 | 9/29/2016 4:56:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 3 | The 60 amp 120/240 volt main breaker exceeds both the 50 ampere rating of the line side conductors of the main switch and the 50 ampere rating of the receptacle on the load side, this can create a thermal hazard | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | _8cu_on_load_side_of_meter.png | file://x:/photopub/docs/0000000492/e365eea4-7d8b-4053-bfa6-b1f32cd390d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe0cfeea_1c16_42c6_bf3e_b976780c3faf
ELIN-700091-2016 | EL-294213-2015 | 11/4/2016 11:53:55 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Energized branch circuitry rated for interior use has been installed in an exterior location in closed proximity to treated wooden siding. This poses a serious risk of personal injury (shock) or property damage (thermal event) due to exposure to mechanical damage and the effects of weather. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | View01_branch_circuitry.png | file://x:/photopub/docs/0000000513/a22a06d5-77ab-4af9-a628-589084fb5f68.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17c22733_7e45_458b_a74f_46f6a5ed5374
GAIN-696838-2016 | GA-425394-2016 | 11/14/2016 11:33:22 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | While assessing a rooftop installation i found a regulator relief termination installed too close to the mechanical air intake of a direct fired make up air unit. Should the regulator relieve while the unit is in operation, raw gas could be drawn into the unit and into the building. This would lead to the potential for a fire or explosion either within the unit or within the building. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | relief_vent_clearance.png | file://x:/photopub/docs/0000000515/acfcd1b7-b734-4b3e-b33b-1b6c0e703e2b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6a2d214_352d_44f3_a955_74ee318bf89d
GAHE-703507-2016 | HE-467310-2016 | 11/14/2016 3:25:32 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Area around propane tank is to be clear of combustibles for a distance of 10 feet. | 3 | Clearance to combustibles not maintained | 217_Murtle.png | file://x:/photopub/docs/0000000515/108aded4-3d98-4d8d-833a-3e9408053663.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06b139f2_6907_4ffe_b0b2_b618e638a786
GAIN-705544-2016 | GA-462530-2016 | 11/17/2016 11:27:08 AM | ASSESS: GA: Final | png | #asFound | GA103 | Power vent not installed according to installation instruction. | 3 | 3 | Power vent not installed as per manufacturers installation instructions. Vent material downstream of a power vent fan must be sealed or rated for positive pressure to prevent leakage of flue product into occupied space. | 3 | Power vent not installed according to installation instruction. | Power_vent_using_b_vent_on_outlet.png | file://x:/photopub/docs/0000000518/5762fee2-b73e-41ff-89dd-24fd992f03d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__672edaf5_b759_454f_b179_170e5e47343c
ELIN-704450-2016 | EL-403739-2016 | 11/21/2016 4:52:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | Lock nuts are installed on metal conduit nipples for bonding of metal enclosures and the electrical equipment they contain. Lock nuts are required to be installed on both sides of enclosures and made up tight. This is required to ensure there is a good bonding path for fault current to flow back to the service ground and grounded conductor if there is a fault on the system. This installation has a new 400A 120/240V service and sub-service equipment for a commercial building. The service equipment and sub-service equipment conductors are contained in metal conduit nipples that are installed between the enclosures. The conduits are connected to the enclosures using lock nuts. The conduits do not have lock nuts installed on both sides of each enclosure and the lock nuts that are installed are not properly tightened to ensure a good connection and continuity of the bonding path. This is a potential shock and fire hazard if there is a fault on the system and the bonding path is not continuous or is inadequate and | 3 | Continuity Bonding; method for equipment is not adequate. | Lock_nuts_on_nipple_not_tightened.png | file://x:/photopub/docs/0000000519/5649ff35-0d97-4b21-ad5e-48d410e313e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__573fbf73_4bcc_4f26_baa7_4a5f8c09f4ea
ELIN-706044-2016 | EL-394964-2016 | 11/21/2016 11:18:46 AM | ASSESS: EL: Final | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Panel covers are not permitted to have any un-used openings in them. This is required to prevent persons and objects from contacting energized parts and to contain thermal energy if there is a fault within the equipment. This installation of a renovated and re-wired house has two 100A 120/240V service panels that are energized and have un-used openings in the panel covers. This is potential shock and fire hazard if persons or objects contact energized parts or if the equipment has an internal fault and does not contain the resulting thermal energy. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Un_used_openings_in_the_panel_cover.png | file://x:/photopub/docs/0000000519/e3f3d2d0-b670-4880-8e30-502a230e2a14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e71ac04b_f3ef_480a_b132_60b9407894c1
ELIN-706044-2016 | EL-394964-2016 | 11/21/2016 11:18:46 AM | ASSESS: EL: Final | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Panel covers are not permitted to have any un-used openings in them. This is required to prevent persons and objects from contacting energized parts and to contain thermal energy if there is a fault within the equipment. This installation of a renovated and re-wired house has two 100A 120/240V service panels that are energized and have un-used openings in the panel covers. This is potential shock and fire hazard if persons or objects contact energized parts or if the equipment has an internal fault and does not contain the resulting thermal energy. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Renovated_and_re-wire_house_with_a_suite.png | file://x:/photopub/docs/0000000519/3c469adf-ede9-4fff-8f10-f67147b1e073.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e71ac04b_f3ef_480a_b132_60b9407894c1
ELIN-704450-2016 | EL-403739-2016 | 11/21/2016 4:52:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | Lock nuts are installed on metal conduit nipples for bonding of metal enclosures and the electrical equipment they contain. Lock nuts are required to be installed on both sides of enclosures and made up tight. This is required to ensure there is a good bonding path for fault current to flow back to the service ground and grounded conductor if there is a fault on the system. This installation has a new 400A 120/240V service and sub-service equipment for a commercial building. The service equipment and sub-service equipment conductors are contained in metal conduit nipples that are installed between the enclosures. The conduits are connected to the enclosures using lock nuts. The conduits do not have lock nuts installed on both sides of each enclosure and the lock nuts that are installed are not properly tightened to ensure a good connection and continuity of the bonding path. This is a potential shock and fire hazard if there is a fault on the system and the bonding path is not continuous or is inadequate and | 3 | Continuity Bonding; method for equipment is not adequate. | Service_equipment.png | file://x:/photopub/docs/0000000519/59605d9d-3bac-4777-ad15-4a60e0fa4be8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__573fbf73_4bcc_4f26_baa7_4a5f8c09f4ea
ELIN-674140-2016 | EL-442199-2016 | 9/29/2016 4:10:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL106 | Conductors Cables, Raceways or conductors are showing signs of wear and will need to be either replaced or repaired. | 2 | 2 | The Armored cable connector set screw is over torqued and is cutting into the Armored of the cable. This could create a short circuit condition and potential fire due to overheating at screw point. | 2 | Conductors Cables, Raceways or conductors are showing signs of wear and will need to be either replaced or repaired. | Connector_over_torque.png | file://x:/photopub/docs/0000000492/926e615d-8628-4df5-a68b-960b1aa6f6d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e71ab7a_0c34_4c62_aa61_7a266866058f
ELIN-674140-2016 | EL-442199-2016 | 9/29/2016 4:10:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL106 | Conductors Cables, Raceways or conductors are showing signs of wear and will need to be either replaced or repaired. | 2 | 2 | The Armored cable connector set screw is over torqued and is cutting into the Armored of the cable. This could create a short circuit condition and potential fire due to overheating at screw point. | 2 | Conductors Cables, Raceways or conductors are showing signs of wear and will need to be either replaced or repaired. | Armour_unwound.png | file://x:/photopub/docs/0000000492/f56385b1-59b7-40ee-8a69-dddb6202b448.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e71ab7a_0c34_4c62_aa61_7a266866058f
BPVOP-667901-2016 | 2292485 | 9/20/2016 2:11:12 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 2 | In the maintenance records there was no indication that the safety valves had been serviced or replaced in the maximum servicing interval which is 6 years for this boiler. There was also no emergency shut down switch located outside the boiler room door. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve.png | file://x:/photopub/docs/0000000488/221ad578-cb87-43d9-94f2-d3085e530ecf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17c4ec0c_5f44_459c_aa46_8b1ad25fe42c
BPVOP-666541-2016 | 2292486 | 9/20/2016 3:27:37 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | The safety valves appear to be older than 6 years old and there is no record of them ever having been changed out or serviced in the maintenance log. There is no manual remote shut down switch located outside the boiler room which would allow the boilers to be shut down in an emergency without entering the boiler room. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | safety.png | file://x:/photopub/docs/0000000488/dcbd6707-7dfd-4ff1-85e4-df168dd7f74d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6da78d5_d4d5_4fb9_b1f1_125f9c4a2038
ELIN-665261-2016 | EL-369972-2016 | 9/19/2016 3:31:46 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | The 70 amp 120/240 volt branch circuit is run with exposed conductors through a knock out of the main panel and not within a conduit system or connector at the panel entrance. This installation can lead to both a shock and a thermal hazard. This installation is located in a secure building with only authorized personnel able to enter. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Conductors-_no_conduit.png | file://x:/photopub/docs/0000000488/094b37df-2058-4b6f-8e7b-2f9a55d00cfc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6de4d139_3aeb_42f0_bc41_78c4e2dfe584
ELHE-673335-2016 | HE-444247-2016 | 9/30/2016 11:12:38 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | The 120/240 volt distribution systems sub-feeds to a sub-distribution panel on pole with no cover on panel, wood enclosure in poor condition and no lock. This installation is accessible to the public and is a shock hazard. See Permit attachments for further photos. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_panel_with_no_cover.png | file://x:/photopub/docs/0000000492/e6ac7f68-8e12-49ad-a031-2d8ef8f473a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e354bae_db4d_4160_8a71_4062815fd628
ELIN-668116-2016 | EL-440629-2016 | 9/29/2016 4:56:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 3 | The 60 amp 120/240 volt main breaker exceeds both the 50 ampere rating of the line side conductors of the main switch and the 50 ampere rating of the receptacle on the load side, this can create a thermal hazard | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Temporary_service.png | file://x:/photopub/docs/0000000492/60282faa-85ca-44c4-b351-6f1158bd33de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe0cfeea_1c16_42c6_bf3e_b976780c3faf
ELIN-669908-2016 | EL-307863-2015 | 9/22/2016 5:20:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | The systems bonding conductor from the 150 amp 600 volt feed for the 150kva transformer has not been installed, this is a shock hazard | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Transformer_systems_bond.png | file://x:/photopub/docs/0000000492/fdf082c4-fadc-4b7a-a679-3458f90478c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__270c579c_f7aa_41b2_b169_df90b500ea6c
ELIN-667692-2016 | EL-425286-2016 | 9/22/2016 8:52:30 AM | ASSESS: EL: Final | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 3 | The low voltage conductors are exposed at floor level. The area is accessible to the general public. Damage of the conductors may cause anti theft system to not operate. | 3 | Protection and control Low voltage protection damaged or not provided. | Exposed_cables.png | file://x:/photopub/docs/0000000489/d8724e46-b45c-4c60-aa3f-5c7d9518bb63.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18024048_8cae_40a3_a144_6e20468b6d0c
ELIN-667692-2016 | EL-425286-2016 | 9/22/2016 8:52:30 AM | ASSESS: EL: Final | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 3 | The low voltage conductors are exposed at floor level. The area is accessible to the general public. Damage of the conductors may cause anti theft system to not operate. | 3 | Protection and control Low voltage protection damaged or not provided. | Camera_installation.png | file://x:/photopub/docs/0000000489/9de29629-cd7e-4699-b1c9-010f09f7464d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18024048_8cae_40a3_a144_6e20468b6d0c
ELIN-688891-2016 | EL-423633-2016 | 10/24/2016 1:38:36 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Halogen lamp bulb has been installed in a close closet. the likelihood of a fire is high due to heat from the lamp being transferred to any items that maybe stored in the closet. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Bear_lamp__Bear_lamp_bulb_located_in_clothes_closet.png | file://x:/photopub/docs/0000000504/f0b15164-0972-4498-91ed-aaaadb800f37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8168e663_380c_4a3a_a835_484020be85c4
ELIN-709598-2016 | EL-467716-2016 | 11/24/2016 10:28:54 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL070 | Effective bonding and grounding The identified conductor is not provided or is not longer functional. | 4 | 4 | In a sub-distribution connection for a residential electrical service the neutral on the feeder conductor is required to be connected to the neutral lug at the panel and not bonded to the panel. This is to prevent neutral currents from circulating through the bonding system and to carry any unbalanced fault currents back to the source. In this installation, a home owner connected the neutral conductor to a bonding lug in the panel. This could lead to circulating currents in the bonding of the panel and create a shock hazard to persons. | 4 | Effective bonding and grounding The identified conductor is not provided or is not longer functional. | Neutral_conductor.png | file://x:/photopub/docs/0000000520/d5adc61d-d60d-480f-92d2-d9a55b558398.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3bbf5e6_f9fd_464b_80dc_9b65669e616d
ELIN-640351-2016 | EL-243595-2015 | 9/21/2016 7:10:56 AM | ASSESS: EL: Final | png | #asFound | EL128 | Installation of electrical equipment Residential: branch circuit for kitchen counter receptacles is not split 15 A, or 20 A. | 3 | 3 | A counter receptacle rated 15 amps 120 volts single pole was installed in lieu of the required 2 pole circuit. Counter receptacles in kitchens are subject to significant loads imposed by appliances. Circuits can overload or be damaged and react unpredictably due to subjected overloads. | 3 | Installation of electrical equipment Residential: branch circuit for kitchen counter receptacles is not split 15 A, or 20 A. | l15r_on_single_pole_circuit_counter.png | file://x:/photopub/docs/0000000499/f5f12e98-0efd-47a4-b36e-c1b867db52b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ff4846a_e186_479d_908d_98c44d4f199b
BPVOP-681417-2016 | 5149016 | 10/11/2016 12:24:39 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 3 | Upon assessment of buffer tank (length-1.8m, diameter-0.70) it is determined that there is no pressure relief device installed on buffer tank. In the event of failure of control, tank may be subject to pressure above Maximum Allowable Working Pressure (MAWP) and consequently tank may rupture with likelihood of severe incident. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | BT3.png | file://x:/photopub/docs/0000000498/2880add3-7a4b-4331-8bb0-5c8c067f92f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0619f768_6b06_4f46_bf5f_f73cdc965fcf
BPVOP-681438-2016 | 5149019 | 10/11/2016 1:54:55 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 3 | Upon assessment of buffer tank (length-1.8, diameter-0.7m) it is determined that there is no pressure relief device installed on buffer tank. In the event of failure of control tank may be subject to pressure above Maximum Allowable Working Pressure (MAWP) and consequently tank may rupture with likelihood of severe incident. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | BT4.png | file://x:/photopub/docs/0000000498/3b8446aa-6ffb-4865-9d8a-a438216b0844.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da39159f_996e_48c9_98af_be2d95e1ad81
GAOP-660320-2016 | 2170868 | 9/21/2016 7:52:20 AM | ASSESS: GA OP: Periodic | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | No immediate hazard but hose needs replacing as soon as possible to reduce the risk of rupture and leaking | 0 | No Created Hazard Identified | Cracked_hose.png | file://x:/photopub/docs/0000000489/1f1ade55-c5a3-4b52-b014-c678c01ff121.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__B903A590_A35A_4F3A_A2D5_F19E1EDB03EC
ELIN-690608-2016 | EL-416867-2016 | 11/3/2016 3:45:18 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Cables that are installed for appliances or spare branch circuits in the future must either be terminated into appliances or into junction boxes with covers. This is required so that the cable is safe from accidental contact if it gets energized. This installation has a 15A, 120V dish washer cable in the kitchen and a 15A 120/240V spare cable in the crawlspace that are not terminated into appliances or junction boxes with covers. The conductors of the cables are capped with wire connectors and the breakers are turned off. Left uncorrected this is a shock and fire hazard if the cables become energized, wire connectors fall off or are removed, and conductors are contacted by persons or objects. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Panel.png | file://x:/photopub/docs/0000000511/01d4689e-1174-45b5-b335-4eef5b926714.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b681cab8_738d_43ba_a449_744a5bf4e0e2
ELIN-690608-2016 | EL-416867-2016 | 11/3/2016 3:45:18 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Cables that are installed for appliances or spare branch circuits in the future must either be terminated into appliances or into junction boxes with covers. This is required so that the cable is safe from accidental contact if it gets energized. This installation has a 15A, 120V dish washer cable in the kitchen and a 15A 120/240V spare cable in the crawlspace that are not terminated into appliances or junction boxes with covers. The conductors of the cables are capped with wire connectors and the breakers are turned off. Left uncorrected this is a shock and fire hazard if the cables become energized, wire connectors fall off or are removed, and conductors are contacted by persons or objects. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Kitchen.png | file://x:/photopub/docs/0000000511/f29dd339-36be-4354-a846-29712a89b556.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b681cab8_738d_43ba_a449_744a5bf4e0e2
ELIN-690608-2016 | EL-416867-2016 | 11/3/2016 3:45:18 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Cables that are installed for appliances or spare branch circuits in the future must either be terminated into appliances or into junction boxes with covers. This is required so that the cable is safe from accidental contact if it gets energized. This installation has a 15A, 120V dish washer cable in the kitchen and a 15A 120/240V spare cable in the crawlspace that are not terminated into appliances or junction boxes with covers. The conductors of the cables are capped with wire connectors and the breakers are turned off. Left uncorrected this is a shock and fire hazard if the cables become energized, wire connectors fall off or are removed, and conductors are contacted by persons or objects. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Dish_washer_cable.png | file://x:/photopub/docs/0000000511/eb1a6097-15de-475d-982f-2cefe735bac5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b681cab8_738d_43ba_a449_744a5bf4e0e2
GAHE-667597-2016 | HE-440258-2016 | 9/20/2016 12:43:22 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA087 | Hydrostatic relief in place but not in correct location of piping system (can be isolated) | 4 | 4 | The as found hazard was a liquid propane piping system which was designed to that the hydrostatic reliefs could be isolated trapping liquid propane in a section of piping with no relief valve. This is a hazard because if isolated there is a risk of over-pressurization potentially resulting in damage to the system. | 4 | Hydrostatic relief in place but not in correct location of piping system (can be isolated) | Missing_hydrostatic_.png | file://x:/photopub/docs/0000000488/734b12bd-d601-4a29-a2ce-06b710884130.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7111b823_e3cf_45a9_bab5_ef148dcb3f85
ELIN-675369-2016 | EL-406878-2016 | 10/3/2016 2:37:17 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | 15 amp, 120 volt non-metallic outlet box that is greater then 100 millimetres supported on one side only. This could cause a thermal effect. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Boxes_greater_then_100mm_supported_on_one_side_only.png | file://x:/photopub/docs/0000000495/0a1337f1-29a4-4da5-ace7-e924aab724fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e9ef926f_9da3_4660_8272_ab8da75932fd
ELIN-690608-2016 | EL-416867-2016 | 11/3/2016 3:45:18 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Cables that are installed for appliances or spare branch circuits in the future must either be terminated into appliances or into junction boxes with covers. This is required so that the cable is safe from accidental contact if it gets energized. This installation has a 15A, 120V dish washer cable in the kitchen and a 15A 120/240V spare cable in the crawlspace that are not terminated into appliances or junction boxes with covers. The conductors of the cables are capped with wire connectors and the breakers are turned off. Left uncorrected this is a shock and fire hazard if the cables become energized, wire connectors fall off or are removed, and conductors are contacted by persons or objects. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Used_mobile_home.png | file://x:/photopub/docs/0000000511/a3cf844d-9bf7-4f38-b929-5aaf34112adf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b681cab8_738d_43ba_a449_744a5bf4e0e2
ELIN-698388-2016 | UW-463466-2016 | 11/5/2016 6:18:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Wrong selection of contactor enclosure has resulted in the inability to close door. The hazard is exposed live parts that are at risk of touch or accidental contact from other objects. This is a shock and arc flash hazard . | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Unapproved_wiring.png | file://x:/photopub/docs/0000000512/e267e83e-52b9-43df-8362-927f2fbd1998.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2dd066b5_acdf_403f_a9e1_39e6f4a00a89
ELIN-698388-2016 | UW-463466-2016 | 11/5/2016 6:18:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Wrong selection of contactor enclosure has resulted in the inability to close door. The hazard is exposed live parts that are at risk of touch or accidental contact from other objects. This is a shock and arc flash hazard . | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Main_panel_has_no_screws_in_panel_cover_.png | file://x:/photopub/docs/0000000512/d7b19e96-d7b4-488c-a776-8fcdf8ec1df3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2dd066b5_acdf_403f_a9e1_39e6f4a00a89
ELIN-698388-2016 | UW-463466-2016 | 11/5/2016 6:18:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Wrong selection of contactor enclosure has resulted in the inability to close door. The hazard is exposed live parts that are at risk of touch or accidental contact from other objects. This is a shock and arc flash hazard . | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Undersized_enclosure.png | file://x:/photopub/docs/0000000512/cb98bc37-b0e5-4080-85ab-0b68c5098c1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2dd066b5_acdf_403f_a9e1_39e6f4a00a89
ELIN-698388-2016 | UW-463466-2016 | 11/5/2016 6:18:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Wrong selection of contactor enclosure has resulted in the inability to close door. The hazard is exposed live parts that are at risk of touch or accidental contact from other objects. This is a shock and arc flash hazard . | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Unapproved_equipment.png | file://x:/photopub/docs/0000000512/2b0c31d0-d3ce-4b33-937b-4d13c51c1214.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2dd066b5_acdf_403f_a9e1_39e6f4a00a89
ELIN-698388-2016 | UW-463466-2016 | 11/5/2016 6:18:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Wrong selection of contactor enclosure has resulted in the inability to close door. The hazard is exposed live parts that are at risk of touch or accidental contact from other objects. This is a shock and arc flash hazard . | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Unprotected_feeder_.png | file://x:/photopub/docs/0000000512/4c8b4879-3af3-41ef-a784-380e277dabe9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2dd066b5_acdf_403f_a9e1_39e6f4a00a89
ELIN-698388-2016 | UW-463466-2016 | 11/5/2016 6:18:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Wrong selection of contactor enclosure has resulted in the inability to close door. The hazard is exposed live parts that are at risk of touch or accidental contact from other objects. This is a shock and arc flash hazard . | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Unsupported_cables.png | file://x:/photopub/docs/0000000512/506e608e-61c7-463b-891e-9713c19bec22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2dd066b5_acdf_403f_a9e1_39e6f4a00a89
PROP-598669-2016 | 4639887 | 11/8/2016 8:56:05 PM | ASSESS: PR OP: RAP | png | #asFound | PR020 | Defect that impairs performance: Performance is outside of limitations or is degenerative Reasonably detectable by the maintenance or operation program | 3 | 3 | Brakes not setup according to a pre-determined value from the acceptance load test. | 3 | Defect that impairs performance: Performance is outside of limitations or is degenerative Reasonably detectable by the maintenance or operation program | Torque_test_procedure.png | file://x:/photopub/docs/0000000515/f7c0a0cf-4b72-4bb4-ae3c-12f06e9f67a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DAFED39C_2D55_4AEA_B0CF_27E970CF5B12
PROP-598643-2016 | 2224156 | 11/10/2016 1:06:31 PM | ASSESS: PR OP: RAP | png | #asFound | PR003 | Drainage impaired or sealing compromised and evidence of accumulated water: Reasonably detectable by maintenance program Unlikely to propagate PR Risk Reg PR-06 | 2 | 2 |  | 2 | Drainage impaired or sealing compromised and evidence of accumulated water: Reasonably detectable by maintenance program Unlikely to propagate PR Risk Reg PR-06 | Debris_buildup.png | file://x:/photopub/docs/0000000515/6b25be79-7890-40a0-adfc-6708d300cd08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87E9CDD9_22EB_4836_9150_9A6E36BA272D
PROP-598629-2016 | 2224073 | 11/10/2016 4:33:46 PM | ASSESS: PR OP: RAP | png | #asFound | PR018 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | Concrete deteriorating for station supports. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Station_support.png | file://x:/photopub/docs/0000000515/e50e39b8-0220-4da3-8e45-8cce69d74c9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__E0BF41E0_52FE_4E82_818E_5CDB6D84A122
ELIN-694874-2016 | EL-458474-2016 | 11/7/2016 12:54:56 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | A 60 amp 240 V consumer service for use with and recreational vehicle has been installed. The main system ground that was existing was used to connect the new service with only one grounding electrode of unknown length or type. Main system grounds must be built to minimum requirements to ensure safety of persons and property. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | One_rod_unknown_length_new_service.png | file://x:/photopub/docs/0000000513/39317af3-ea61-4816-a6c5-05427433670a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6686d38a_2f65_4307_b943_e961ae74520c
ELIN-687899-2016 | EL-449473-2016 | 11/4/2016 7:21:00 AM | ASSESS: EL: Final | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | A manufactured home with a 100 amp service 240 volts has been connected to an existing service cable. The service cable is lacking effective overcurrent protection. This installation has 5 meters of this cable in the combustible crawlspace exposed to damage or interference. Code requires this cable to be limited in length to 1.5 meters maximum to minimize the possibility of damage to the conductors that could result in property damage or injury to persons. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 5_meters_total_unfused_service_conductor_in_combustioble_crawlspace_of_manufactured_home.png | file://x:/photopub/docs/0000000513/3418e151-c726-496c-a041-fdf6b5ccbc62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ce568bc_5e9c_48a0_a862_d1c39f691ce3
ELIN-694050-2016 | EL-438087-2016 | 11/7/2016 8:42:15 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | 15 amp 120 volt electric heat tracing has been connected to an exterior receptacle with an extension cord run in the crawlspace through the wall of the skirting. Flexible cord can break down where it passes through walls and can deteriorate at connections to permanent equipment. This can lead to property damage or injury to persons | 4 | Conductors, Misuse of flexible cords. | Flexible_extension_cord_through_skirting_to_permanent_heat_trace.png | file://x:/photopub/docs/0000000513/0362fc6b-7c1d-471e-96f6-f8417c4c9dad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__478f8897_fad4_4d23_8ad9_d7e1c7482b56
ELIN-700623-2016 | EL-459413-2016 | 11/10/2016 1:02:46 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Panel cover missing and panel is energized. This is a shock hazard condition. 120/208V, 3 phase, 200 amp. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Panel_cover_missing__panel_energized.png | file://x:/photopub/docs/0000000514/d27af06a-1e5a-4baa-8d7b-cbc40405111e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5d3de82_23f1_41bd_9f21_126a3532798f
ELOP-708178-2016 | 4632 | 11/21/2016 1:03:34 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Multi unit outlet extension cord is not approved for permanent use. This could be a fire/shock hazard to persons or property due to the misuse of multi unit outlet extension cord. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Multi_unit_outlet_extension_cord.png | file://x:/photopub/docs/0000000519/4b0024bd-7079-49af-92ca-b7879b8e8a45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd0cb4aa_31a0_4767_8311_cd1463be23ca
ELOP-670122-2016 | 5109382 | 9/23/2016 2:14:59 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL216 | All Classes, All Zones Area is classified; • equipment requires maintenance; and • ventilation is not adequate. | 3 | 3 | Follow up inspection on pallet parts mill. Documentation still required by the Discipline Order has not been produced. Further attention to combustible dust is required. The electrical room and the transformers in it have accumulations of dust infiltrating through their grills. Fire hazard. | 3 | All Classes, All Zones Area is classified; • equipment requires maintenance; and • ventilation is not adequate. | Dust_in_electrical_room_.png | file://x:/photopub/docs/0000000490/cfa9ec91-c34f-449d-82a9-b5169063029f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b46d774_138d_468e_a2c3_7638cd877f56
GAHE-703228-2016 | HE-467052-2016 | 11/14/2016 11:36:39 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Tank location does not meet the required clearances to combustible wall of house. | 3 | Clearance to combustibles not maintained | 2892_Barriere_lakes_.png | file://x:/photopub/docs/0000000515/f4b09010-3dfd-4cd3-b896-8b57a34b9aa9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d500389d_5e14_4084_89b5_51a119c887e9
GAHE-703226-2016 | HE-467049-2016 | 11/14/2016 11:43:06 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Combustibles are located around tank without proper clearance. | 3 | Clearance to combustibles not maintained | 629_Barriere_lakes.png | file://x:/photopub/docs/0000000515/8771be93-2b52-42a3-83ff-0338ce7c17bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__847dbdcc_c7ae_4dbe_b8f3_311312a1658a
ELIN-701599-2016 | EL-455662-2016 | 11/14/2016 11:23:58 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Non compliant TCS exposed to water | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Exposed_equipment.png | file://x:/photopub/docs/0000000515/4089dfe6-4f19-4d25-b8a3-16b339fcf6c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a218eb7_b47d_4871_b87b_f0defc73a883
ELIN-701599-2016 | EL-455662-2016 | 11/14/2016 11:23:58 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Non compliant TCS exposed to water | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | screw_in_attachment_point.png | file://x:/photopub/docs/0000000515/78c38d67-4a1f-4d12-9511-1dcf8b0defac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a218eb7_b47d_4871_b87b_f0defc73a883
ELIN-709673-2016 | EL-320544-2015 | 11/23/2016 12:46:19 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized conductors are left in junction box without a coverplate. This is a possible shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_conductors.png | file://x:/photopub/docs/0000000520/029df220-75bd-4faf-97a8-5794663d5992.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c340902_a041_4e55_be79_947554e689ac
BPVOP-700324-2016 | 2273963 | 11/14/2016 11:40:48 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Scale_on_boiler_tubes_.png | file://x:/photopub/docs/0000000515/2fbe7a60-b193-42af-9d4a-bc0feec50863.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57128190_bc6a_4b1f_baf3_e310fe2e4158
BPVIN-682775-2016 | UW-450946-2016 | 10/18/2016 2:22:44 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP115 | 3.0.1 Safeties will not function - Safety Devices bypassed or failed but the back up corresponding safety devices operational | 4 | 4 | Inappropriately controlled car seal block valves may cause equipment failure which may result in harm to personnel and property. | 4 | 3.0.1 Safeties will not function - Safety Devices bypassed or failed but the back up corresponding safety devices operational | Block_valve.png | file://x:/photopub/docs/0000000502/7141c08d-43d4-4900-9b91-8eb5ac01c90e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08264653_16c8_44b6_816d_89ba9d0c24a1
ELOP-662577-2016 | 2200169 | 9/30/2016 8:13:02 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL230 | Class II, wood dust, Minor cleanup required. Wood dust mitigation and fire plans are in place and being followed. | 1 | 1 |  | 1 | Class II, wood dust, Minor cleanup required. Wood dust mitigation and fire plans are in place and being followed. | Dust.png | file://x:/photopub/docs/0000000499/994044b6-d918-4140-b2bf-1f74b9668bc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__19817e1a_59d7_4d33_ad02_1f93e6904f98
ELIN-681897-2016 | EL-319258-2015 | 10/13/2016 2:56:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | Service subject to damage and falling from tree and unapproved connection to home | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_poa.png | file://x:/photopub/docs/0000000499/af1ddf2a-bdf8-4d38-8bbf-557ba33643dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3e6e07b_a68c_40b5_acad_252c87c5b3cc
ELIN-681897-2016 | EL-319258-2015 | 10/13/2016 2:56:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | Service subject to damage and falling from tree and unapproved connection to home | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Oh_thru_tree.png | file://x:/photopub/docs/0000000499/4309d54e-138f-4c02-9b17-87eac179e450.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3e6e07b_a68c_40b5_acad_252c87c5b3cc
ELIN-685785-2016 | EL-447018-2016 | 10/24/2016 2:37:24 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | A 15A 120V 12/3 non-metallic sheathed cable has been installed in an underground conduit. The cable is not rated for a wet location or use underground, this could result in equipment and wire damage. | 3 | Conductors Equipment is not approved for the specific use. | JB_Underground_Subfeed.png | file://x:/photopub/docs/0000000504/f4c7b96f-a4ba-4666-8b38-75a930166bb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e214c9a6_2c79_4369_a526_9198fe29948a
ELIN-690307-2016 | EL-346543-2016 | 10/26/2016 1:06:55 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Range.png | file://x:/photopub/docs/0000000506/806927a6-9737-4d36-977d-186bbc0a4284.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa854707_3133_461d_8832_0f67ffcbd686
ELIN-691540-2016 | UW-457830-2016 | 10/26/2016 2:35:31 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Un permitted and non compliant electrical modifications | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Modified_branch_circuit.png | file://x:/photopub/docs/0000000506/360a18d5-b078-4fb3-ae2d-953ddd5c964e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ccccfaa_f4f6_46f3_9fe7_658e0038a295
ELIN-691540-2016 | UW-457830-2016 | 10/26/2016 2:35:31 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Un permitted and non compliant electrical modifications | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 30A_circuit.png | file://x:/photopub/docs/0000000506/bd3bfdc8-8288-4820-9900-8a5b9781f281.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ccccfaa_f4f6_46f3_9fe7_658e0038a295
ELIN-690307-2016 | EL-346543-2016 | 10/26/2016 1:06:55 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Water_damage_to_range_cable.png | file://x:/photopub/docs/0000000506/3ed9a79e-12f7-4cf8-a819-bf31cd020b26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa854707_3133_461d_8832_0f67ffcbd686
ELIN-691540-2016 | UW-457830-2016 | 10/26/2016 2:35:31 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Un permitted and non compliant electrical modifications | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | New_cable.png | file://x:/photopub/docs/0000000506/d365bd19-064b-4601-9ce1-930e09bce913.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ccccfaa_f4f6_46f3_9fe7_658e0038a295
ELIN-690307-2016 | EL-346543-2016 | 10/26/2016 1:06:55 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Fan_feed_water_damage.png | file://x:/photopub/docs/0000000506/06e65ac8-bca4-4226-9fcf-d53591ebc724.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa854707_3133_461d_8832_0f67ffcbd686
GAOP-661049-2016 | 2171496 | 11/18/2016 9:37:10 AM | ASSESS: GA OP: Periodic | png | #asFound | GA023 | Inadequate protection Low traffic | 2 | 2 | Tank not protected from truck traffic in parking lot | 2 | Inadequate protection Low traffic | Aurora_roofing.png | file://x:/photopub/docs/0000000518/2d1ad190-cfc4-41c8-a738-14996abe8319.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__EC43CD13_799A_4978_842D_84C91581A1C8
EDIN-670761-2016 | ED-043055-2013 | 9/23/2016 3:58:33 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | All hardware on the counterweight activating arm were loose | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Activating_arm.png | file://x:/photopub/docs/0000000490/bc2e1545-c673-4449-90d5-375a66e2ff3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8b311a8_ad65_408b_b075_585a352f1117
ELIN-701599-2016 | EL-455662-2016 | 11/14/2016 11:23:58 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Non compliant TCS exposed to water | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Water_damage.png | file://x:/photopub/docs/0000000515/b735c15a-4968-4d3c-93e9-a07a9f79c874.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a218eb7_b47d_4871_b87b_f0defc73a883
ELIN-701599-2016 | EL-455662-2016 | 11/14/2016 11:23:58 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Non compliant TCS exposed to water | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Receptacles.png | file://x:/photopub/docs/0000000515/a95e5603-02a4-49f9-acb2-547f44854544.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a218eb7_b47d_4871_b87b_f0defc73a883
GAHE-708519-2016 | HE-470340-2016 | 11/21/2016 3:27:04 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | Propane tank has no clearance to property line. | 2 | Installation clearances or set backs to propane containers not met | 12_4510_Power.png | file://x:/photopub/docs/0000000519/debc4b36-b351-4102-85b3-76a79960f27d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed6b7603_d8fa_43fe_a850_e3de75936f8b
ELIN-689860-2016 | EL-451490-2016 | 10/24/2016 4:24:41 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | It is required that all ungrounded conductors of a feeder or circuit be protected by overcurrent devices at the point where the conductor receives its electrical energy or where its ampacity rating is reduced. Specific exceptions to the general requirement are allowed if a smaller conductor is protected by an overcurrent device installed in an upstream feeder or circuit consisting of larger conductors. This specific requirement does not allow the tap conductor (smaller conductor ) length to be greater than 7.5m. This is so the upstream overcurrent device will react before damage occurs to the smaller tap conductors. In this installation at a single family dwelling, a contractor installed a 250 MCM Al armoured cable for a 200A panel off of a 400A splitter without overcurrent protection and at a distance greater than 7.5m. If an overload or short-circuit was to occur on this cable, there is a potential for thermal damage to occur before the upstream overcurrent device reacted which could resu | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 400A_3ph_splitter.png | file://x:/photopub/docs/0000000505/323d667b-24c4-4bc7-97c2-85bf81b03f5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b290a31c_4c86_4385_b8dc_9b7f92459874
ELIN-689860-2016 | EL-451490-2016 | 10/24/2016 4:24:41 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | It is required that all ungrounded conductors of a feeder or circuit be protected by overcurrent devices at the point where the conductor receives its electrical energy or where its ampacity rating is reduced. Specific exceptions to the general requirement are allowed if a smaller conductor is protected by an overcurrent device installed in an upstream feeder or circuit consisting of larger conductors. This specific requirement does not allow the tap conductor (smaller conductor ) length to be greater than 7.5m. This is so the upstream overcurrent device will react before damage occurs to the smaller tap conductors. In this installation at a single family dwelling, a contractor installed a 250 MCM Al armoured cable for a 200A panel off of a 400A splitter without overcurrent protection and at a distance greater than 7.5m. If an overload or short-circuit was to occur on this cable, there is a potential for thermal damage to occur before the upstream overcurrent device reacted which could resu | 4 | Protection and control Overcurrent devices do not adequately protect conductors | New_200A_panel.png | file://x:/photopub/docs/0000000505/dfdca6aa-9959-43c4-a324-15eea6039136.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b290a31c_4c86_4385_b8dc_9b7f92459874
ELIN-689860-2016 | EL-451490-2016 | 10/24/2016 4:24:41 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | It is required that all ungrounded conductors of a feeder or circuit be protected by overcurrent devices at the point where the conductor receives its electrical energy or where its ampacity rating is reduced. Specific exceptions to the general requirement are allowed if a smaller conductor is protected by an overcurrent device installed in an upstream feeder or circuit consisting of larger conductors. This specific requirement does not allow the tap conductor (smaller conductor ) length to be greater than 7.5m. This is so the upstream overcurrent device will react before damage occurs to the smaller tap conductors. In this installation at a single family dwelling, a contractor installed a 250 MCM Al armoured cable for a 200A panel off of a 400A splitter without overcurrent protection and at a distance greater than 7.5m. If an overload or short-circuit was to occur on this cable, there is a potential for thermal damage to occur before the upstream overcurrent device reacted which could resu | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 250mcm_acwu.png | file://x:/photopub/docs/0000000505/d3c62faf-9d7a-436a-933e-a8a753add975.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b290a31c_4c86_4385_b8dc_9b7f92459874
GAIN-690191-2016 | GA-340544-2016 | 10/25/2016 8:43:23 AM | ASSESS: GA: Rough-In | png | #asFound | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 5 | 5psi into building installed 5psi-inches full relief regulators without venting to the outdoors, if the regulators were to fail they would relieve into the building and could potentially cause an explosion of the gas mixture. | 5 | Relief style regulator/device allowed to vent within building/confined space | I_.png | file://x:/photopub/docs/0000000505/74292620-8963-439b-8fd8-b4646640eb94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15a90f9d_6d1b_41fc_b32e_e64799b713da
GAUP-697189-2016 | UW-463026-2016 | 11/3/2016 4:18:58 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA115 | Vent sizing causing spillage | 5 | 5 | The as found hazard was two commercial hot water tanks which had been installed with vent connectors to small to effectively vent the appliances, the inadequate vent connectors resulted in some of the products of combustion "spilling" from the appliances draft hoods back into the mechanical room. This is a hazard because it creates a risk of carbon monoxide poisoning for anyone entering the mechanical room. | 5 | Vent sizing causing spillage | Vent_size_reduction.png | file://x:/photopub/docs/0000000511/2d383b82-c276-42a2-b8e6-e09544bad7ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5258186d_4f35_427b_bb74_32c25fc05056
GAUP-697189-2016 | UW-463026-2016 | 11/3/2016 4:18:58 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA115 | Vent sizing causing spillage | 5 | 5 | The as found hazard was two commercial hot water tanks which had been installed with vent connectors to small to effectively vent the appliances, the inadequate vent connectors resulted in some of the products of combustion "spilling" from the appliances draft hoods back into the mechanical room. This is a hazard because it creates a risk of carbon monoxide poisoning for anyone entering the mechanical room. | 5 | Vent sizing causing spillage | Tank_Markings.png | file://x:/photopub/docs/0000000511/fc442010-9201-446f-8b31-7ce5e215cb4e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5258186d_4f35_427b_bb74_32c25fc05056
GAHE-697846-2016 | HE-463056-2016 | 11/4/2016 10:52:57 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | Underground gas line was entering the home underground. If the underground line started leaking it could enter the home through the penetration through the foundation wall potentially causing a fire or explosion. | 3 | Underground piping entering a building below grade (unapproved) | Gas_line2.png | file://x:/photopub/docs/0000000512/d7729732-cd03-412b-af56-cd0417d05f52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba028419_9b32_44f5_a7eb_fdb871d2f8ed
GAHE-697846-2016 | HE-463056-2016 | 11/4/2016 10:52:57 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | Underground gas line was entering the home underground. If the underground line started leaking it could enter the home through the penetration through the foundation wall potentially causing a fire or explosion. | 3 | Underground piping entering a building below grade (unapproved) | Gas_line.png | file://x:/photopub/docs/0000000512/d17e2df2-4b17-48be-9fad-9ac6c8ca5b90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba028419_9b32_44f5_a7eb_fdb871d2f8ed
PROP-598660-2016 | 3366611 | 11/4/2016 8:50:02 AM | ASSESS: PR OP: RAP | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | The wand on the tension switch is loose, therefore it will not monitor carriage position. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Tensioning_switch.png | file://x:/photopub/docs/0000000511/e869ffe5-38ab-4fcc-9a23-ac9e5d43d6ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__FBD9DA57_FD51_4575_AA15_79FE756E1A40
BPVOP-551411-2016 | BPV-281240-2015 | 9/21/2016 1:17:40 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Pressure retaining components shall have sufficient thickness to retain pressure. I found some scattered pitting on the external surface of some fire tubes on High Pressure Steam Boiler (180PSIG). Depth of some pits is approximately 50% of the original tube wall. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Pitting.png | file://x:/photopub/docs/0000000490/35e12716-c1a7-40ef-91d1-227b8ff1cdc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3d18497_edc0_45fe_ace7_6ec75bf307e8
BPVOP-525324-2016 | 2261451 | 9/26/2016 2:00:30 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP065 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | 4 | 4 | Pressure retaining components of a boiler must be structurally sound in order to safely contain pressure. I Found some cracks in the ligaments of back tubesheet of a High Pressure Steam Boiler (150 PSIG) and water and steam was leaking from those cracks. | 4 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | Ligament_crack.png | file://x:/photopub/docs/0000000490/bd4b77f5-ac19-48f6-9c81-92b3788b4686.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c3b31de_68b9_4bfe_af9f_1d2a0267b6c4
GAHE-690620-2016 | HE-456926-2016 | 10/25/2016 12:59:47 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA025 | Inadequate protection high traffic | 4 | 4 | Crash protection posts have no clearance to the propane cylinder dispensing cabinet. If the posts are hit the cabinet can be moved possibly damaging the liquid propane piping inside causing a large release of gas. | 4 | Inadequate protection high traffic | Crash_protection.png | file://x:/photopub/docs/0000000505/7a50355c-a8fe-4639-96ed-9139d002451c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1eaf3ffc_39a4_4de0_9958_e27828d13eab
ELIN-671796-2016 | EL-441453-2016 | 9/27/2016 2:53:48 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Standard dry type enclosure used in an installation for a barn housing livestock, enclosures installed in barns are required to be approved for areas where liquid and corrosive vapour are present. Standard enclosures and electrical equipment installed in these enclosures may deteriorate over time, and may not provide adequate protection to circuits. Failing electrical equipment provides a risk of shock and fire to persons and property. | 3 | General Equipment is not approved for the specific use | Regular_enclosure_used_in_barn_installation.png | file://x:/photopub/docs/0000000491/e65ead18-1173-4c8b-a65e-f3fb5522cbd6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df3e08b1_8fdd_434a_b5d1_13bcd30dc45d
BPVOP-687195-2016 | 2279394 | 10/19/2016 11:45:15 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 | Heavy scale in bottom of Boiler and both Low Water Cut Offs feed piping internals | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Bottom_handhole.png | file://x:/photopub/docs/0000000503/ae9463f4-0dd5-42af-b1bd-b12bca2d03f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb1a3e4b_03ec_4467_931e_b1833be48b9f
BPVOP-687195-2016 | 2279394 | 10/19/2016 11:45:15 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 | Heavy scale in bottom of Boiler and both Low Water Cut Offs feed piping internals | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | LWCO_1_feed_piping.png | file://x:/photopub/docs/0000000503/a4ae3f8c-f589-4c8c-92ad-905cd6ead27d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb1a3e4b_03ec_4467_931e_b1833be48b9f
BPVOP-687195-2016 | 2279394 | 10/19/2016 11:45:15 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 | Heavy scale in bottom of Boiler and both Low Water Cut Offs feed piping internals | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | LWCO_2_feed_piping.png | file://x:/photopub/docs/0000000503/1ddbeca9-47ce-46b1-a099-20b73dbe81f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb1a3e4b_03ec_4467_931e_b1833be48b9f
ELIN-663834-2016 | EL-050681-2013 | 10/25/2016 12:34:20 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Flexible cords not properly installed, feeding out of rigid PVC raceway, and increasing the risk of exposure to electric shock. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Flexible_cords_feeding_out_of_raceway_fitting.png | file://x:/photopub/docs/0000000505/2c23e5b5-ed37-40e5-9231-cd1d4d451620.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68a779dc_503d_464c_b438_901d30b65708
ELOP-690939-2016 | 5109382 | 10/26/2016 9:58:22 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | Follow up combustible dust assessment on pallet parts mill. Combustible dust is entering the electrical room from the mill because the door will not remain closed. A hydraulic door closure has been installed on the wrong side of the door so that the door will only open approximately 30Â°. The door is not tight fitting and there is an opening where there is no passage set (door knob) on the door allowing dust to enter. Accumulations of dust from this condition can cause equipment failure and fire. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Electrical_room_door.png | file://x:/photopub/docs/0000000506/49c181a3-ac66-4d18-ba91-7f8a99c3a0f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45f06ee1_bcd2_40b2_967f_0cd053a4805e
ELIN-690604-2016 | EL-371797-2016 | 10/26/2016 1:08:32 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | Rough wire of new single-family dwelling. Ceiling outlet box is not approved for fan support and therefore may not withstand the weight of a ceiling fan. Possible injury to persons in the vicinity. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Ceiling_fan.png | file://x:/photopub/docs/0000000506/54316211-349e-459d-b340-1530ba78158e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a95e2ff_8eda_40a3_81c1_8af21a428f2a
ELIN-705383-2016 | EL-466219-2016 | 11/17/2016 11:41:49 AM | ASSESS: EL: Final | png | #asFound | EL159 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | 3 | 3 | Maximum breaker size exceeded. Manufacturer specified maximum 20 amp breaker. Exceeding the recommended breaker size can result in damage to equipment and or fire. | 3 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | A.png | file://x:/photopub/docs/0000000517/ac3bd2c7-d749-45b1-ad7f-9fe769005d2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a40b5f7d_fc2e_4d2c_8b87_dbb168fdc257
ELIN-705383-2016 | EL-466219-2016 | 11/17/2016 11:41:49 AM | ASSESS: EL: Final | png | #asFound | EL159 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | 3 | 3 | Maximum breaker size exceeded. Manufacturer specified maximum 20 amp breaker. Exceeding the recommended breaker size can result in damage to equipment and or fire. | 3 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | B.png | file://x:/photopub/docs/0000000517/7838e75d-1fb8-4328-a28f-c1b3581a3aff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a40b5f7d_fc2e_4d2c_8b87_dbb168fdc257
BPOP-670677-2016 | BPV-405590-2015 | 10/25/2016 2:19:17 PM | ASSESS: Propane PV: Periodic | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Pressure relief valve on 5000 USWG tank exceeds its required 10 year service interval. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Relief_valve.png | file://x:/photopub/docs/0000000505/c742a902-4800-4006-870d-6eca7539827a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__501e2020_5052_43ad_819d_bb327323db24
ELHE-685897-2016 | HE-452781-2016 | 10/25/2016 1:35:34 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | Gang operated load break switch installed and in the closed position. Grounding conductors are not visible and not installed onto switch where required. Grounding conductors are required for gang operated load break switches in order to clear faults, in the case of the pole mounted equipment having a failure these grounding conductors(which are not installed) would have to clear a line to ground fault. If the fault cannot be cleared an increase in step and touch potential is present, creating a risk of shock and fire to persons and equipment. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Grounding_provisions_are_not_in_place_for_gang_operated_load_break_switch__.png | file://x:/photopub/docs/0000000505/bf667ae0-d376-4fa7-8242-0a90eef4ae5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__337273c9_ec4f_4045_ac9e_7d69b485c3e1
ELIN-709270-2016 | EL-462930-2016 | 11/21/2016 12:13:19 PM | ASSESS: EL: Final | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | Found a panel installed in kitchen cupboard with out clearances to safely work on panel. Cables entree ring panel had no mechanical protection. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Kitchen_panel.png | file://x:/photopub/docs/0000000522/0767c3d2-c9ad-4ef6-8a4d-3bad1d6a1898.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b383b4dd_a3e6_4362_9c37_8b37835e39a7
BPVOP-680809-2016 | 2285473 | 10/7/2016 11:30:00 AM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP047 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | 5 | 5 | Corrosion has reduced the shell thickneses to zero in at least two places, vessel has been removed from service pending repairs or replacement. | 5 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | Outside_corrosion_of_DHWT__2.png | file://x:/photopub/docs/0000000497/7a80b112-2331-469d-b702-52507ff32ff5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92d87386_c757_4e4d_938f_b1f21e7c5fcb
BPVOP-680809-2016 | 2285473 | 10/7/2016 11:30:00 AM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP047 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | 5 | 5 | Corrosion has reduced the shell thickneses to zero in at least two places, vessel has been removed from service pending repairs or replacement. | 5 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | Inside_DHWT_2_Glass_Lining_Failure.png | file://x:/photopub/docs/0000000497/c85020bf-a7f6-4471-b3f8-61f803b3634a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92d87386_c757_4e4d_938f_b1f21e7c5fcb
ELHE-708460-2016 | HE-470286-2016 | 11/21/2016 5:14:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/208 volt 3 phase overhead conductor line on power pole structure was struck by machinery and the rotted pole was damaged and leaning over with possibly of falling over. The pole was temporarily tied off and supported with ropes and slings tied to a metal wire mesh fence to prevent pole from falling. When power pole structures are rotted and damaged and supported with methods not compliant with code standards, the pole could fall over and could cause an electrical fire or shock hazard to people or property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 6.png | file://x:/photopub/docs/0000000520/6beecb07-116a-4904-81f5-f172305cb728.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51a029cb_28df_4056_bdc0_db74c2a47073
ELHE-708460-2016 | HE-470286-2016 | 11/21/2016 5:14:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/208 volt 3 phase overhead conductor line on power pole structure was struck by machinery and the rotted pole was damaged and leaning over with possibly of falling over. The pole was temporarily tied off and supported with ropes and slings tied to a metal wire mesh fence to prevent pole from falling. When power pole structures are rotted and damaged and supported with methods not compliant with code standards, the pole could fall over and could cause an electrical fire or shock hazard to people or property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 2.png | file://x:/photopub/docs/0000000520/09e7a419-d47b-4edb-af54-01f095888ccb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51a029cb_28df_4056_bdc0_db74c2a47073
ELHE-708460-2016 | HE-470286-2016 | 11/21/2016 5:14:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/208 volt 3 phase overhead conductor line on power pole structure was struck by machinery and the rotted pole was damaged and leaning over with possibly of falling over. The pole was temporarily tied off and supported with ropes and slings tied to a metal wire mesh fence to prevent pole from falling. When power pole structures are rotted and damaged and supported with methods not compliant with code standards, the pole could fall over and could cause an electrical fire or shock hazard to people or property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 12.png | file://x:/photopub/docs/0000000520/fa8a9b12-64cb-42cc-b688-9e134aa59e28.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51a029cb_28df_4056_bdc0_db74c2a47073
ELHE-708460-2016 | HE-470286-2016 | 11/21/2016 5:14:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/208 volt 3 phase overhead conductor line on power pole structure was struck by machinery and the rotted pole was damaged and leaning over with possibly of falling over. The pole was temporarily tied off and supported with ropes and slings tied to a metal wire mesh fence to prevent pole from falling. When power pole structures are rotted and damaged and supported with methods not compliant with code standards, the pole could fall over and could cause an electrical fire or shock hazard to people or property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 9.png | file://x:/photopub/docs/0000000520/0d3c0c6e-3c46-4e67-927f-0d08b159e7b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51a029cb_28df_4056_bdc0_db74c2a47073
ELHE-708460-2016 | HE-470286-2016 | 11/21/2016 5:14:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/208 volt 3 phase overhead conductor line on power pole structure was struck by machinery and the rotted pole was damaged and leaning over with possibly of falling over. The pole was temporarily tied off and supported with ropes and slings tied to a metal wire mesh fence to prevent pole from falling. When power pole structures are rotted and damaged and supported with methods not compliant with code standards, the pole could fall over and could cause an electrical fire or shock hazard to people or property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 7.png | file://x:/photopub/docs/0000000520/75048a65-6b35-4f56-bdda-b8b77a773d27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51a029cb_28df_4056_bdc0_db74c2a47073
ELHE-708460-2016 | HE-470286-2016 | 11/21/2016 5:14:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/208 volt 3 phase overhead conductor line on power pole structure was struck by machinery and the rotted pole was damaged and leaning over with possibly of falling over. The pole was temporarily tied off and supported with ropes and slings tied to a metal wire mesh fence to prevent pole from falling. When power pole structures are rotted and damaged and supported with methods not compliant with code standards, the pole could fall over and could cause an electrical fire or shock hazard to people or property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 1.png | file://x:/photopub/docs/0000000520/80d05ab8-c45b-4ce4-ab2c-4a2689ec1ecc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51a029cb_28df_4056_bdc0_db74c2a47073
ELHE-708460-2016 | HE-470286-2016 | 11/21/2016 5:14:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/208 volt 3 phase overhead conductor line on power pole structure was struck by machinery and the rotted pole was damaged and leaning over with possibly of falling over. The pole was temporarily tied off and supported with ropes and slings tied to a metal wire mesh fence to prevent pole from falling. When power pole structures are rotted and damaged and supported with methods not compliant with code standards, the pole could fall over and could cause an electrical fire or shock hazard to people or property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 11.png | file://x:/photopub/docs/0000000520/77bd8972-8a07-414d-a7c2-84aa208c0f71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51a029cb_28df_4056_bdc0_db74c2a47073
ELHE-708460-2016 | HE-470286-2016 | 11/21/2016 5:14:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/208 volt 3 phase overhead conductor line on power pole structure was struck by machinery and the rotted pole was damaged and leaning over with possibly of falling over. The pole was temporarily tied off and supported with ropes and slings tied to a metal wire mesh fence to prevent pole from falling. When power pole structures are rotted and damaged and supported with methods not compliant with code standards, the pole could fall over and could cause an electrical fire or shock hazard to people or property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 3.png | file://x:/photopub/docs/0000000520/dfdf9464-07ae-4b20-8da9-a0c9f9140781.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51a029cb_28df_4056_bdc0_db74c2a47073
ELHE-708460-2016 | HE-470286-2016 | 11/21/2016 5:14:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/208 volt 3 phase overhead conductor line on power pole structure was struck by machinery and the rotted pole was damaged and leaning over with possibly of falling over. The pole was temporarily tied off and supported with ropes and slings tied to a metal wire mesh fence to prevent pole from falling. When power pole structures are rotted and damaged and supported with methods not compliant with code standards, the pole could fall over and could cause an electrical fire or shock hazard to people or property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 5.png | file://x:/photopub/docs/0000000520/5c41995c-f34f-4500-a339-e62e4664b6d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51a029cb_28df_4056_bdc0_db74c2a47073
ELHE-708460-2016 | HE-470286-2016 | 11/21/2016 5:14:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/208 volt 3 phase overhead conductor line on power pole structure was struck by machinery and the rotted pole was damaged and leaning over with possibly of falling over. The pole was temporarily tied off and supported with ropes and slings tied to a metal wire mesh fence to prevent pole from falling. When power pole structures are rotted and damaged and supported with methods not compliant with code standards, the pole could fall over and could cause an electrical fire or shock hazard to people or property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4.png | file://x:/photopub/docs/0000000520/2a769aac-aed1-4d3b-92e9-394fe230fe77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51a029cb_28df_4056_bdc0_db74c2a47073
ELHE-708460-2016 | HE-470286-2016 | 11/21/2016 5:14:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/208 volt 3 phase overhead conductor line on power pole structure was struck by machinery and the rotted pole was damaged and leaning over with possibly of falling over. The pole was temporarily tied off and supported with ropes and slings tied to a metal wire mesh fence to prevent pole from falling. When power pole structures are rotted and damaged and supported with methods not compliant with code standards, the pole could fall over and could cause an electrical fire or shock hazard to people or property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 10.png | file://x:/photopub/docs/0000000520/50cb6dd6-cca1-44d6-8476-bf29d6c6ba5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51a029cb_28df_4056_bdc0_db74c2a47073
ELHE-708460-2016 | HE-470286-2016 | 11/21/2016 5:14:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/208 volt 3 phase overhead conductor line on power pole structure was struck by machinery and the rotted pole was damaged and leaning over with possibly of falling over. The pole was temporarily tied off and supported with ropes and slings tied to a metal wire mesh fence to prevent pole from falling. When power pole structures are rotted and damaged and supported with methods not compliant with code standards, the pole could fall over and could cause an electrical fire or shock hazard to people or property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 8.png | file://x:/photopub/docs/0000000520/5d4ea4da-c3cc-4d99-9ec9-37078028e477.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51a029cb_28df_4056_bdc0_db74c2a47073
BPVOP-686364-2016 | 5058630 | 10/18/2016 2:48:32 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Hot Water Boiler with Heating Surface (HS) of 33 square meters, Allowable Working Pressure (AWP) of 30psig and Maximum Allowable Water Temperature (MAWT) of 250Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_room_doo.png | file://x:/photopub/docs/0000000502/d0ac8017-feea-44e5-bcea-23cdd5998e70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64b45a02_928c_4072_ad87_c08a6203b809
BPVOP-686372-2016 | 5058631 | 10/18/2016 3:49:03 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Hot Water Boiler with Heating Surface (HS) of 33 square meter, Allowable Working Pressure (AWP) of 30psig and Maximum Allowable Water Temperature (MAWT) of 250Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | BOILER_ROOM_DOOR.png | file://x:/photopub/docs/0000000502/e03def3c-8447-4029-a3f0-958215ee3838.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f3910dc8_e6ff_4688_ba85_31ee3fcefea2
PROP-599992-2016 | 2908803 | 10/27/2016 12:48:09 PM | ASSESS: PR OP: RAP | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | Unable to check function of detector, it may not be functioning properly | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Smoke_detector_machine_room.png | file://x:/photopub/docs/0000000506/717d9ed3-f204-4042-8a6a-70bfdc9a736d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__622C2947_8A17_420C_B27E_C5FB3DDED2AF
ELIN-671753-2016 | EL-413339-2016 | 9/27/2016 9:31:37 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Sub panel feeder rated at 90 amp max. at 75 degrees. Installed on 100 amp over current device. No raceway provided for non-heating leads of in floor heat. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 5282_Dewar_5.png | file://x:/photopub/docs/0000000491/c2c397fe-cc35-4e9c-93dd-a9ad03dc2fba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4af73f38_b44e_49db_b096_2c0fc8e95cb8
ELIN-671753-2016 | EL-413339-2016 | 9/27/2016 9:31:37 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Sub panel feeder rated at 90 amp max. at 75 degrees. Installed on 100 amp over current device. No raceway provided for non-heating leads of in floor heat. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 5282_Dewar_2.png | file://x:/photopub/docs/0000000491/eb222e79-3e5f-4aa1-a660-f9b2b5155f71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4af73f38_b44e_49db_b096_2c0fc8e95cb8
ELIN-671753-2016 | EL-413339-2016 | 9/27/2016 9:31:37 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Sub panel feeder rated at 90 amp max. at 75 degrees. Installed on 100 amp over current device. No raceway provided for non-heating leads of in floor heat. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 5282_Dewar_3.png | file://x:/photopub/docs/0000000491/52eb1646-ac51-4a68-8cd7-aee9e95696aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4af73f38_b44e_49db_b096_2c0fc8e95cb8
ELIN-671753-2016 | EL-413339-2016 | 9/27/2016 9:31:37 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Sub panel feeder rated at 90 amp max. at 75 degrees. Installed on 100 amp over current device. No raceway provided for non-heating leads of in floor heat. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 5282_Dewar_1.png | file://x:/photopub/docs/0000000491/4a63e8b0-9e52-4e28-92f9-e77b14f10545.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4af73f38_b44e_49db_b096_2c0fc8e95cb8
ELIN-671753-2016 | EL-413339-2016 | 9/27/2016 9:31:37 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Sub panel feeder rated at 90 amp max. at 75 degrees. Installed on 100 amp over current device. No raceway provided for non-heating leads of in floor heat. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 5282_Dewar_4.png | file://x:/photopub/docs/0000000491/8d1c02db-21d5-426c-89ac-f469831263bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4af73f38_b44e_49db_b096_2c0fc8e95cb8
ELIN-691357-2016 | EL-415332-2016 | 10/27/2016 11:15:12 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Not energized | 0 | No Created Hazard Identified | Switch.png | file://x:/photopub/docs/0000000506/9d49d9f6-834f-472b-bcb6-48ca6ac9a3c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e46d0668_46dd_4190_8aa2_aaff53d39c62
ELIN-691357-2016 | EL-415332-2016 | 10/27/2016 11:15:12 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Not energized | 0 | No Created Hazard Identified | Switch_label.png | file://x:/photopub/docs/0000000506/325e70b6-247b-44d9-9776-9bb832810e55.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e46d0668_46dd_4190_8aa2_aaff53d39c62
ELIN-691357-2016 | EL-415332-2016 | 10/27/2016 11:15:12 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Not energized | 0 | No Created Hazard Identified | Enclosure.png | file://x:/photopub/docs/0000000506/1332d5c2-c64d-4bbd-98f2-8a8d96d95d76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e46d0668_46dd_4190_8aa2_aaff53d39c62
ELOP-708223-2016 | 4606 | 11/28/2016 10:36:16 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | Panels (F) and (D) do not have 1 meter or working space and have obstructed means of egress. This could be hazard if a person needs access to these panels to turn off a branch circuit feeding a possible electrical hazard. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Panel_F.png | file://x:/photopub/docs/0000000522/0ebbd38a-a379-4792-b6f4-662a5f2b1094.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c96a8e8c_242a_4846_bbc9_c73675b6af53
ELOP-708219-2016 | 4621 | 11/25/2016 11:16:21 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | Panel (E) does not have 1 meter of working space and has obstructed means of egress. This could be hazard if a person needs access to these panels to turn off a branch circuit feeding a possible electrical hazard. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Panel_E.png | file://x:/photopub/docs/0000000522/7f3d7bf9-26b7-4f29-a08d-458bc03bda4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eaf70bdf_8c66_4f26_bbe2_0c73d10bc0ab
ELOP-708216-2016 | 4607 | 11/25/2016 11:02:13 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | Panel boards (K) and (R) do not have 1 meter or working space and have obstructed means of egress. This could be hazard if a person needs access to these panels to turn off a branch circuit feeding a possible electrical hazard. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Panel_R.png | file://x:/photopub/docs/0000000522/79fac26c-e8a2-481a-839e-f55a6009898c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c47355b_d1d1_4ec2_9235_c4140fa814cd
ELOP-708223-2016 | 4606 | 11/28/2016 10:36:16 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | Panels (F) and (D) do not have 1 meter or working space and have obstructed means of egress. This could be hazard if a person needs access to these panels to turn off a branch circuit feeding a possible electrical hazard. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Panel_D.png | file://x:/photopub/docs/0000000522/4a869c89-41c6-4407-ba21-82f3f0d0e81c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c96a8e8c_242a_4846_bbc9_c73675b6af53
ELIN-671443-2016 | EL-432951-2016 | 9/27/2016 2:48:19 PM | ASSESS: EL: Final | png | #asFound | EL134 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | 3 | 3 | Front of electrical outlet box is recessed behind the combustible wall. This would lead to a fire if the switch or wiring failed and arked. | 3 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | Bathroom_switch.png | file://x:/photopub/docs/0000000491/5b74b844-f483-456a-9110-fc2670d820ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e4183b8e_efcb_4284_b28c_a078f4121b5b
ELIN-671443-2016 | EL-432951-2016 | 9/27/2016 2:48:19 PM | ASSESS: EL: Final | png | #asFound | EL134 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | 3 | 3 | Front of electrical outlet box is recessed behind the combustible wall. This would lead to a fire if the switch or wiring failed and arked. | 3 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | Office_switch.png | file://x:/photopub/docs/0000000491/acf6c783-8185-4074-902a-651a5ba96ee0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e4183b8e_efcb_4284_b28c_a078f4121b5b
ELHE-675652-2016 | HE-445846-2016 | 9/30/2016 2:58:13 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Overhead service cable resting on newly constructed building extension roof. Overhead service conductors are required to have clearances from buildings and structures, accidental contact or failure of the line( having it fall) would have the line come in contact with the building or an individual. Accidental contact with service cables provides a shock and fire risk to persons and property | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Overhead_service_line_resting_on_building_roof__.png | file://x:/photopub/docs/0000000493/788d83c3-9d1a-49df-a862-8a7201ff9ded.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91a621cf_5b1f_4a2b_8d0c_a4f666e34ca9
ELOP-708216-2016 | 4607 | 11/25/2016 11:02:13 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | Panel boards (K) and (R) do not have 1 meter or working space and have obstructed means of egress. This could be hazard if a person needs access to these panels to turn off a branch circuit feeding a possible electrical hazard. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Panel_K.png | file://x:/photopub/docs/0000000522/26656bf2-e448-40f1-b74d-003f16c0c23e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c47355b_d1d1_4ec2_9235_c4140fa814cd
GAIN-706448-2016 | GA-435623-2016 | 11/28/2016 11:46:07 AM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | Found propane regulator installed in such a way that propane liquefaction could occur in the hoses and the liquid could end up at the inlet of the regulator. Vapour service regulators are not designed to regulate propane liquid, and may be damaged by it, or may pass liquid leading to hazardous conditions downstream. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Propane_hoses.png | file://x:/photopub/docs/0000000522/e619f5a7-7566-41dc-88a0-b63f5ea0b6b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d358298_5549_47f5_acc7_cfb25687ed71
ELIN-690624-2016 | EL-456215-2016 | 10/26/2016 1:16:55 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumer service cable inside residence exceeds 1.5 meters without concrete encasement, service cables are protected by utility overcurrent devices at the utility connection. A fault in this service cable would result in a risk of fire and shock to persons and property, thus the requirement to concrete encase if in excess of 1.5 meters inside residence. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_cable_not_encased_and_in_excess_of_1_5_meters_in_residence__.png | file://x:/photopub/docs/0000000506/decc8a97-a1ae-4397-8a6e-81c509c20210.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b9de4a7_5f4a_405d_a2a4_26f985c29051
GAIN-687077-2016 | GA-450784-2016 | 11/29/2016 10:51:45 AM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | Vent attached to boiler is not installed or supported correctly. The dip in the vent does not allow the condensate in the vent to drain back to the appliance. | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | non_approved_CPVC_vent_connection_.png | file://x:/photopub/docs/0000000523/00eb1761-7650-489e-946a-bff97c53b777.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c296af6_56da_43bc_a435_f7abf5703115
GAIN-687077-2016 | GA-450784-2016 | 11/29/2016 10:51:45 AM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | Vent attached to boiler is not installed or supported correctly. The dip in the vent does not allow the condensate in the vent to drain back to the appliance. | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Dip_in_vent_.png | file://x:/photopub/docs/0000000523/6711709d-2a0e-4d4b-ba08-e9c1347b82b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c296af6_56da_43bc_a435_f7abf5703115
GAIN-709298-2016 | GA-458732-2016 | 11/29/2016 11:28:49 AM | ASSESS: GA: Final | png | #asFound | GA040 | Identification of piping and tubing not completed or incorrect | 1 | 1 | Gas shut off not readily accessible | 1 | Identification of piping and tubing not completed or incorrect | Gas_shut-off_not_accessible_.png | file://x:/photopub/docs/0000000523/57bbec05-a206-481c-986d-3ff8d171d29b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94ce23d3_c587_4ac7_aec1_e782ce57ccb1
GAIN-709298-2016 | GA-458732-2016 | 11/29/2016 11:28:49 AM | ASSESS: GA: Final | png | #asFound | GA040 | Identification of piping and tubing not completed or incorrect | 1 | 1 | Gas shut off not readily accessible | 1 | Identification of piping and tubing not completed or incorrect | No_power_connected_to_furnace__.png | file://x:/photopub/docs/0000000523/d63e26dc-7102-4be4-9232-4c3f21df9764.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94ce23d3_c587_4ac7_aec1_e782ce57ccb1
GAIN-709298-2016 | GA-458732-2016 | 11/29/2016 11:28:49 AM | ASSESS: GA: Final | png | #asFound | GA040 | Identification of piping and tubing not completed or incorrect | 1 | 1 | Gas shut off not readily accessible | 1 | Identification of piping and tubing not completed or incorrect | Copper_used_as_condensates_drain_.png | file://x:/photopub/docs/0000000523/2346ac9e-3d13-4652-8e5a-e7952cc9210d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94ce23d3_c587_4ac7_aec1_e782ce57ccb1
ELIN-685719-2016 | 4321322 | 10/25/2016 2:59:36 PM | ASSESS: EL: Final | png | #asFound | EL133 | Installation of electrical equipment General: improper polarity at receptacle. | 3 | 3 | Receptacles located in addition bathroom are reverse polarized. This could become a hazard because on a standard duplex receptacle, there are two wires that carry electricity. One of these wires is connected to ground at the service and named as the grounded conductor (more commonly referred to as the neutral wire.) It is usually recognizable as the white wire. The other wire is the ungrounded conductor or hot wire. This wire is usually black or red, but can be any colour besides white or green. The hot wire completes a circuit by coming in contact with the earth so, if an unsuspecting person touches a hot wire while in contact with the earth, he or she will complete the circuit and get shocked. | 3 | Installation of electrical equipment General: improper polarity at receptacle. | Reverse_polarity_receptacles.png | file://x:/photopub/docs/0000000505/58786da7-78f6-4fb4-a4a9-9d7cc262c48a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__60d0b0b4_163e_4ddf_aeae_055bb8466aec
ELIN-688876-2016 | EL-436182-2016 | 11/2/2016 12:13:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL089 | Continuity Bonding; conductor is not properly sized. | 3 | 3 | The 200 amp 120/208 volt 3-phase 4-wire service conduit between the panel and meterbase does not include a bonding bushing for the conduit and the bonding conductor does not meet Table 41 requirements. This could cause a shock hazard if a fault was to occur as the path may not be sufficient to carry the total fault | 2 | Continuity Bonding; conductor is not properly sized. | Panelboard.png | file://x:/photopub/docs/0000000510/649790d0-e7e6-4212-9463-a7a5c08f107f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__553d15d4_d52c_4feb_81c8_de538a9a9fe5
ELIN-688876-2016 | EL-436182-2016 | 11/2/2016 12:13:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL089 | Continuity Bonding; conductor is not properly sized. | 3 | 3 | The 200 amp 120/208 volt 3-phase 4-wire service conduit between the panel and meterbase does not include a bonding bushing for the conduit and the bonding conductor does not meet Table 41 requirements. This could cause a shock hazard if a fault was to occur as the path may not be sufficient to carry the total fault | 2 | Continuity Bonding; conductor is not properly sized. | Meterbase.png | file://x:/photopub/docs/0000000510/4521931c-de03-44d3-a76e-8f3fc57c3ff5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__553d15d4_d52c_4feb_81c8_de538a9a9fe5
GAHE-704466-2016 | HE-468141-2016 | 11/15/2016 3:33:23 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Tank is touching the ground at one end. A clearance of 6" is required by code. | 3 | Clearance to combustibles not maintained | 529_Fawn.png | file://x:/photopub/docs/0000000516/25969343-35b3-4560-8de2-4b6e82138bee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bca897f_c21f_4f74_afad_ff0e7fad2a89
GAUP-688467-2016 | UW-455243-2016 | 10/31/2016 2:34:33 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | The as found hazard was a gas range which had been tied into a gas piping system supplying a gas pressure higher than the maximum allowable inlet pressure for the appliance. If the appliance regulator were to fail due to the excessive inlet pressure the range would over fire significantly, risk of fire. | 3 | Appliance not installed according to installation instructions | No_Reg.png | file://x:/photopub/docs/0000000508/d87e7890-f459-4ff1-9e09-a3f0bc556acb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b98e5040_fb84_4940_a27c_17265bd0822a
BPVOP-689766-2016 | 2267654 | 10/24/2016 8:35:06 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Hot Water Boiler with Heating Surface (HS) of 63 square meter, MaximumAllowable Working Pressure (MAW of 125psig and Maximum Allowable Water Temperature (MAWT) of 250Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_emergency_shutdown_switch_at_boiler_room_door.png | file://x:/photopub/docs/0000000505/1d61ec52-bf7c-436d-82d1-45ee868d812d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ea0e36e_cf29_41fb_b683_b6c0d638d0ce
ELIN-694097-2016 | EL-452006-2016 | 11/1/2016 1:46:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Allowable length of main service cable inside residence has been exceeded. Allowable length inside residence is 1.5 meters. This service cable is protected by utility overcurrent devices located at the street. In the case of a fault in this cable, the excess length may provide a risk of fire and shock to persons and property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Allowable_length_of_service_cable_inside_residence_exceeded.png | file://x:/photopub/docs/0000000509/15e2b56f-572e-41b3-b899-ecf4caa4f86a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9db9118_7079_4ed7_88a9_7c2b1331e604
ELOP-699767-2016 | 5242 | 11/10/2016 7:03:49 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 15 amp 120 volt receptacles located within 1.5 meters of sinks have not been provided with GFCI protection, this poses a shock hazard to persons and possible damage to equipment using the receptacle. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Counter_Plug.png | file://x:/photopub/docs/0000000515/729d1f7a-9284-4673-82cc-a65059897840.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33880e25_2ca1_47cf_a4d1_fb7e6bd953ce
ELIN-703522-2016 | EL-392980-2016 | 11/15/2016 12:43:53 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | NMSC cables are in contact with heating ducts. This is a shock hazard condition. 120/240 Volt. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_cables_in_contact_with_heating_ducts.png | file://x:/photopub/docs/0000000516/d726c3fc-498f-4df3-bba1-22bc5fce54c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ef7b464_e3fc_4565_895c_301ecc487395
PROP-598682-2016 | PR-312477-2015 | 11/25/2016 12:09:19 PM | ASSESS: PR OP: RAP | png | #asFound | PR018 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | Conveyor belt guides are used to prevent pinch point and ensure belt tracks correctly. During a RAP inspection some belt guides at the load are were found to be damaged or missing. Missing or damaged guides could cause a possible pinch point for rides and damage to the conveyor belt. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Damaged_Belt_Guides.png | file://x:/photopub/docs/0000000521/0a74c305-421b-405d-9190-56db57b0589d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67967608_DD1D_42C7_B512_64CFAABFC893
PROP-598685-2016 | PR-312474-2015 | 11/23/2016 12:59:38 PM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 |  | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Carpet_on_Walkways.png | file://x:/photopub/docs/0000000521/f2396a1b-713f-4116-b37a-affcae1bd9d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__AE28CEF5_AE50_4096_B998_AC94EF66E389
PROP-598683-2016 | PR-312473-2015 | 11/23/2016 1:17:24 PM | ASSESS: PR OP: RAP | png | #asFound | PR018 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | Conveyor belt guides are used to prevent pinch points and ensure belt tracks correctly. During a RAP inspection multiple belt guides on the walkways were found to be damaged or missing. Missing or damaged guides could cause a possible pinch point for rides and damage to the conveyor belt. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Inside_Conveyor__Belt_Guides_on_inside_of_White_Carpet_Above_Belt.png | file://x:/photopub/docs/0000000521/fe65a04e-5752-4fb9-a40c-c0638089f97d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1AC3253F_EBA6_4018_9D88_E9CEBBF11930
PROP-598683-2016 | PR-312473-2015 | 11/23/2016 1:17:24 PM | ASSESS: PR OP: RAP | png | #asFound | PR018 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | Conveyor belt guides are used to prevent pinch points and ensure belt tracks correctly. During a RAP inspection multiple belt guides on the walkways were found to be damaged or missing. Missing or damaged guides could cause a possible pinch point for rides and damage to the conveyor belt. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Damaged_Belt_Guides_Conveyor_4.png | file://x:/photopub/docs/0000000521/176ca4d4-0c51-4a0f-8e5a-d6e3b009550b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1AC3253F_EBA6_4018_9D88_E9CEBBF11930
ELIN-670019-2016 | EL-438379-2016 | 9/26/2016 10:56:08 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Lighting for a residential outdoor deck was installed and connected to a 120 volt 15 amp circuit. The dry location cable was installed exposed to rain and ultraviolet rays. This cable is known to be damaged by prolonged exposure to these conditions and can lead to property damage or injury to persons | 3 | Conductors Equipment is not approved for the specific use. | No_access_to_box__NMD_90_exposed_to_rain_and_uv__building_not_sealed.png | file://x:/photopub/docs/0000000491/daf63ec2-54a0-4075-8293-f26cd2bbb0b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddd28655_4fec_4bbf_95e8_24e0f1021716
ELIN-669421-2016 | EL-439524-2016 | 9/27/2016 12:32:51 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Existing flourescent light fixtures operating at 120 volts on a 20 amp circuit have been retrofit for energy saving purposes. New labeling on these fixtures does not identify the lamp type required should replacement be needed. Other lamp types will fit into these fixtures. With the altered wiring and components this can create a risk for unpredictable failure that could damage property or injure persons | 3 | Installation of electrical equipment Equipment is not approved for the specific use | New_label_no_lamp_type.png | file://x:/photopub/docs/0000000491/72d01b96-a65b-491b-9bee-62c8b0e53ad2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8d451ea_d113_40c1_910d_af0bf35d5d15
BPVIN-626840-2016 | BPV-067062-2013 | 11/3/2016 1:13:47 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon the assessment of a LP Steam Boiler with MAWP of 150 psig, was found that the Safety Relief Valve was overdue as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_.png | file://x:/photopub/docs/0000000511/8868c798-f602-4084-83b7-81c35ebfbfed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b03c98aa_3a77_4cd8_aba4_1c527d319653
GAUP-544369-2016 | UW-367083-2016 | 11/16/2016 9:56:10 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | Piping not properly supported, fresh air vent blocked. Can cause unit to produce co due to lack of combustion air | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Csst.png | file://x:/photopub/docs/0000000516/6b1ab3e0-2445-41c0-81e9-43d3c4f25ff1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99556ed6_91fb_4b1a_b3fd_0300f71c6b96
GAUP-544369-2016 | UW-367083-2016 | 11/16/2016 9:56:10 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | Piping not properly supported, fresh air vent blocked. Can cause unit to produce co due to lack of combustion air | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Fresh_air_vent_plugged.png | file://x:/photopub/docs/0000000516/eab39c4c-094c-4a1d-ad11-381a660b91db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99556ed6_91fb_4b1a_b3fd_0300f71c6b96
GAIN-449136-2015 | GA-285397-2015 | 11/15/2016 1:03:05 PM | ASSESS: GA: Final | png | #asFound | GA023 | Inadequate protection Low traffic | 2 | 2 |  | 2 | Inadequate protection Low traffic | Arbutus_rv_.png | file://x:/photopub/docs/0000000516/9f59fef0-5334-48cc-8a91-1453a6f1563a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be7cea12_ef39_4fe2_b5df_45b777eae06a
ELIN-690502-2016 | EL-430725-2016 | 10/26/2016 11:02:42 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 3 | The device boxes were set into the wall approximately 25 Millimeters from the surface of the wall. This condition leads to energized wire and terminals being outside of the protective device box exposing occupants to a potential shock or fire hazard. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | Device_box_at_approximately_25_mils_from_surface_.png | file://x:/photopub/docs/0000000506/720ddf4d-7b3e-4cb4-959a-e1e5b76b64d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f12e472_a9f3_4ae0_bcd2_7cae4115814f
ELIN-672813-2016 | EL-425014-2016 | 9/28/2016 12:17:20 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Stranded #8 wire for range bonding is incomplete, stranded and solid wire #8 and larger require a solderless type wire connection(lug). Current installation has only a wire binding screw which is acceptable for wire size #10 and smaller. Installed in this manner adequate enclosure bonding may not be achieved. In the case of a fault, inadequate bonding may result in overcurrent devices not performing as required which may cause damage to electrical equipment, persons and property. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Bonding_incomplete_for__8__awg_stranded_conductor__.png | file://x:/photopub/docs/0000000492/2402c34e-3252-4fe4-9ac3-76e9f13abd8d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9429e96_25ff_413e_9914_43389d66ffc1
GAUP-544369-2016 | UW-367083-2016 | 11/16/2016 9:56:10 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | Piping not properly supported, fresh air vent blocked. Can cause unit to produce co due to lack of combustion air | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Pipe_support.png | file://x:/photopub/docs/0000000516/2a9f43a4-14d1-43d4-84bc-948fca5e215b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99556ed6_91fb_4b1a_b3fd_0300f71c6b96
ELIN-614305-2016 | EL-337701-2016 | 7/25/2016 11:56:38 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Receptacle located within 1.5 meters of sink in laundry room is not GFCI protected. This could be a shock hazard if water from sink was to splash onto a person while they were plugging in a device into the receptacle. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_located_near_sink__.png | file://x:/photopub/docs/0000000492/d2dba313-5bde-4339-9aac-b3e4ff65e95c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e61f89f_8d51_4a06_b49b_546e136d0bb1
GAIN-663799-2016 | GA-285980-2015 | 9/14/2016 3:23:38 PM | ASSESS: GA: Final | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | In event of a leak of gas between the riser outside of the camp and the odour system located inside of the camp gas could leak undetected. The leaking gas could cause a fire or explosion hazard when undetected. | 3 | Code prohibited practices or materials | Odourant_system_at_compound_generator_location_.png | file://x:/photopub/docs/0000000488/82a9d58e-d9a8-4507-b71f-f5dc0fbe2172.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__86ec06d0_1030_483e_bb37_ad8e41a9c4d4
GAIN-666500-2016 | GA-268426-2015 | 9/20/2016 8:11:05 AM | ASSESS: GA: Commissioning Approval | png | #asFound | GA068 | Improperly sized gas piping or tubing according to delivery pressure for a single appliance | 2 | 2 |  | 2 | Improperly sized gas piping or tubing according to delivery pressure for a single appliance | Under_sized_regulator.png | file://x:/photopub/docs/0000000488/63ed2bcc-4235-443c-9b50-34f467c2436e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce6972a6_1a5d_46a9_a1d3_f69ed50db04f
BPVOP-695609-2016 | 2797669 | 11/22/2016 2:40:38 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | During the external inspection of a HP Steam boiler with MAWP of 150 psig was found that the Safety Valve was leaking and was overdue as per CSA B-51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Overdue_SV.png | file://x:/photopub/docs/0000000519/26ddac56-e9e4-4a3f-b41f-ccb4a4aff934.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d545345_51de_4b31_b725_95fc6bd0d3fb
ELIN-706175-2016 | EL-425730-2016 | 11/21/2016 12:51:50 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | A suite panel is fed with #8 aluminum cable. This could result in circuit overloading. | 3 | Protection and control Loading of distribution equipment exceeded | suite_panel_fed_with_8_guage_al_cable.png | file://x:/photopub/docs/0000000519/7c91b0fc-09ae-476f-96ea-9ae97cf1adcd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15ed23d6_ebb2_4436_9741_239a28a0d275
ELIN-706175-2016 | EL-425730-2016 | 11/21/2016 12:51:50 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | A suite panel is fed with #8 aluminum cable. This could result in circuit overloading. | 3 | Protection and control Loading of distribution equipment exceeded | vandalized_cables.png | file://x:/photopub/docs/0000000519/786883b7-e1ff-4e1e-8e4f-e19af3026abf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15ed23d6_ebb2_4436_9741_239a28a0d275
GAIN-707955-2016 | GA-292255-2015 | 11/28/2016 9:54:54 AM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | First stage propane regulator installed below liquid level of tank. Liquid propane could be drawn into system containing components only rated for propane vapour. Possible damage to downstream components resulting in over fire condition of installed equipment. Possible fire risk. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Wiltshire.png | file://x:/photopub/docs/0000000523/41e383d3-c0e1-45bf-b226-ea7f8f562858.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d801ecc_04f7_4730_81ad_ca6ff78b8bf6
BPVOP-710942-2016 | 2265151 | 11/24/2016 11:10:22 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Hot Water Boiler with Heating Surface (HS) of 35 square meters, Maximum Allowable Working Pressure (MAWP) of 30psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_room_without_boiler_emergency_shutdown_switch_at_door.png | file://x:/photopub/docs/0000000523/edbc7e98-0f40-4e5d-a1ce-21c5208b1012.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__751cf710_a2b8_4e49_9cde_350f93527243
ELIN-696635-2016 | UW-462605-2016 | 11/3/2016 3:15:05 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Found exposed energized conductors and bus bars in panelboard while panel cover is missing and cover is confirmed to not be installed for several days. When energized panelboards are missing panel covers the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | cover_missing_on_exposed_energized_conductors_bus_1.png | file://x:/photopub/docs/0000000511/f149b807-23f2-48b6-b140-842e12a4f76e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e04786bb_beef_4f03_96ab_adfac009e6d5
ELIN-696635-2016 | UW-462605-2016 | 11/3/2016 3:15:05 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Found exposed energized conductors and bus bars in panelboard while panel cover is missing and cover is confirmed to not be installed for several days. When energized panelboards are missing panel covers the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | cove_laying_on_floor_for_7_days.png | file://x:/photopub/docs/0000000511/81fdac16-ddd2-4eed-a535-5a2951ef1b0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e04786bb_beef_4f03_96ab_adfac009e6d5
ELHE-669444-2016 | HE-428070-2016 | 9/23/2016 3:23:09 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL089 | Continuity Bonding; conductor is not properly sized. | 3 | 3 | The grounding of the High voltage switch is incorrect and could create a shock hazard to anyone operating the switch. | 2 | Continuity Bonding; conductor is not properly sized. | Ground_mat.png | file://x:/photopub/docs/0000000490/1c1fb77a-1508-4345-8eed-527456e6e858.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91fc7321_2bdb_42fc_92b6_3f59dd78a2d3
ELIN-679071-2016 | EL-442392-2016 | 10/11/2016 3:19:57 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | No_expansion_joint.png | file://x:/photopub/docs/0000000498/5f77260e-dd3a-48f6-b09f-7b70aae636ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c930d3ca_3267_462b_a57e_f604180cee29
GAIN-696112-2016 | GA-462247-2016 | 11/8/2016 12:36:59 PM | ASSESS: GA: Rough-In | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | Mechanical inlet air for boiler has been installed too close to gas meter regulator, if regulator were to fail and relief raw gas it could be sucked back into the boiler through the inlet air piping causing an explosion. | 3 | insufficient mechanical air intake clearance to gas regulator relief | 13408_Marine.png | file://x:/photopub/docs/0000000513/f5747ae1-02b8-43fc-8541-5a5e5a641fd0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33d47501_a0ed_428d_9772_9a02f293794b
ELIN-699664-2016 | EL-320544-2015 | 11/8/2016 10:34:47 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized conductors have been left exposed. This is a possible shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | energized_conductors.png | file://x:/photopub/docs/0000000513/16926abd-cde0-44c5-a76b-e504a826ae19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d7ac852_05a6_4139_94fc_de9466af0e0b
ELIN-699664-2016 | EL-320544-2015 | 11/8/2016 10:34:47 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized conductors have been left exposed. This is a possible shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Junction_box_about_to_be_buried_2.png | file://x:/photopub/docs/0000000513/af588866-ff4f-4fb3-ac6b-406689dd86a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d7ac852_05a6_4139_94fc_de9466af0e0b
ELIN-699664-2016 | EL-320544-2015 | 11/8/2016 10:34:47 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized conductors have been left exposed. This is a possible shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel_cover_left_off.png | file://x:/photopub/docs/0000000513/8967f551-7ba6-4d8d-abda-0fd74dd1ba9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d7ac852_05a6_4139_94fc_de9466af0e0b
ELIN-699664-2016 | EL-320544-2015 | 11/8/2016 10:34:47 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized conductors have been left exposed. This is a possible shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Junction_box_about_to_be_buried.png | file://x:/photopub/docs/0000000513/0381f298-7b60-4601-a279-5edde68c32ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d7ac852_05a6_4139_94fc_de9466af0e0b
ELIN-699664-2016 | EL-320544-2015 | 11/8/2016 10:34:47 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized conductors have been left exposed. This is a possible shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Junction_box_about_to_be_buried_3.png | file://x:/photopub/docs/0000000513/38904715-2436-4882-9eb2-c412c8b3b6c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d7ac852_05a6_4139_94fc_de9466af0e0b
ELIN-699664-2016 | EL-320544-2015 | 11/8/2016 10:34:47 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized conductors have been left exposed. This is a possible shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Junction_box_about_to_be_buried_4.png | file://x:/photopub/docs/0000000513/2b916df2-36b5-4875-a43f-ca91796b2226.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d7ac852_05a6_4139_94fc_de9466af0e0b
ELIN-664246-2016 | EL-438082-2016 | 9/20/2016 5:29:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Concealed non-metallic sheathed cable is required to be installed a minimum 32 mm away from the closest edge of the nearest framing member or to protect the cable with mechanical protection. This requirement is to protect the concealed cable from penetration by screws or nails. In this installation of non-metallic sheathed cable in a single family dwelling, there where locations where the cable was installed less than 32mm from the nearest edge of the framing member and did not have mechanical protection. When energized, there is a potential of a shock hazard to persons or a fire hazard to the structure if the concealed cable was penetrated by a screw or nail. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable_within_32mm.png | file://x:/photopub/docs/0000000488/990c6844-4648-4f95-ac4e-bcf89e922e2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5fc007e2_954c_4e88_8b3a_708e62231521
ELIN-709674-2016 | EL-444142-2016 | 11/23/2016 7:25:20 PM | ASSESS: EL: Final | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | The electrical code requires that the ampacity of a circuit not to be less than the calculated load of the circuit. This to protect the circuit from becoming overloaded. In this installation for a tenant improvement to add a restaurant to a commercial building, the contractor connected the loads to an existing 125 amp panel. The electrical engineers drawings showed the calculated load as 133 amps. The increased ampacity could lead to an overload condition on the feeder conductors or the transformer supplying power to the panel. The overload condition could cause insulation breakdown to the conductors which could lead to equipment damage and a fault on the circuit which could create potential shock or fire hazards. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Transformer_name_plate.png | file://x:/photopub/docs/0000000520/19d2d623-8870-40da-bbba-015c3696f580.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26ac37eb_1a1c_4984_87a2_e34f7da10889
ELIN-709674-2016 | EL-444142-2016 | 11/23/2016 7:25:20 PM | ASSESS: EL: Final | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | The electrical code requires that the ampacity of a circuit not to be less than the calculated load of the circuit. This to protect the circuit from becoming overloaded. In this installation for a tenant improvement to add a restaurant to a commercial building, the contractor connected the loads to an existing 125 amp panel. The electrical engineers drawings showed the calculated load as 133 amps. The increased ampacity could lead to an overload condition on the feeder conductors or the transformer supplying power to the panel. The overload condition could cause insulation breakdown to the conductors which could lead to equipment damage and a fault on the circuit which could create potential shock or fire hazards. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Panel_Directory.png | file://x:/photopub/docs/0000000520/c8151cd5-f868-4832-aa5d-a0aa761828ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26ac37eb_1a1c_4984_87a2_e34f7da10889
ELIN-709674-2016 | EL-444142-2016 | 11/23/2016 7:25:20 PM | ASSESS: EL: Final | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | The electrical code requires that the ampacity of a circuit not to be less than the calculated load of the circuit. This to protect the circuit from becoming overloaded. In this installation for a tenant improvement to add a restaurant to a commercial building, the contractor connected the loads to an existing 125 amp panel. The electrical engineers drawings showed the calculated load as 133 amps. The increased ampacity could lead to an overload condition on the feeder conductors or the transformer supplying power to the panel. The overload condition could cause insulation breakdown to the conductors which could lead to equipment damage and a fault on the circuit which could create potential shock or fire hazards. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 120_208V_panel.png | file://x:/photopub/docs/0000000520/e209f9c3-e68a-430f-a49c-9d73c5e35aac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26ac37eb_1a1c_4984_87a2_e34f7da10889
ELIN-709674-2016 | EL-444142-2016 | 11/23/2016 7:25:20 PM | ASSESS: EL: Final | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | The electrical code requires that the ampacity of a circuit not to be less than the calculated load of the circuit. This to protect the circuit from becoming overloaded. In this installation for a tenant improvement to add a restaurant to a commercial building, the contractor connected the loads to an existing 125 amp panel. The electrical engineers drawings showed the calculated load as 133 amps. The increased ampacity could lead to an overload condition on the feeder conductors or the transformer supplying power to the panel. The overload condition could cause insulation breakdown to the conductors which could lead to equipment damage and a fault on the circuit which could create potential shock or fire hazards. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Load_calculation.png | file://x:/photopub/docs/0000000520/0786fa14-f635-40bb-9567-fe5c946e09fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26ac37eb_1a1c_4984_87a2_e34f7da10889
ELOP-693440-2016 | 6533 | 11/1/2016 9:17:52 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Office_of_the.png | file://x:/photopub/docs/0000000509/a6c612ed-d8fc-468a-8689-dabe7f3a318c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb119ae_869e_471a_8262_96e2260dda77
ELOP-693440-2016 | 6533 | 11/1/2016 9:17:52 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Maintenance_clean__maintenance_cleanup_records.png | file://x:/photopub/docs/0000000509/b84b2285-d36c-4a97-9ed3-e8f998f3b22a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb119ae_869e_471a_8262_96e2260dda77
ELOP-693440-2016 | 6533 | 11/1/2016 9:17:52 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Training_records__training_records_stored_on_electronic_format.png | file://x:/photopub/docs/0000000509/4ff05211-69ee-4242-8ee8-78679b8da0d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb119ae_869e_471a_8262_96e2260dda77
ELOP-693440-2016 | 6533 | 11/1/2016 9:17:52 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Electrical_logbook__electrical_logbook_completed_and_maintained.png | file://x:/photopub/docs/0000000509/0c0123b9-a042-4955-8512-971f9f9a5088.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb119ae_869e_471a_8262_96e2260dda77
ELOP-693440-2016 | 6533 | 11/1/2016 9:17:52 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Electrical_logbook.png | file://x:/photopub/docs/0000000509/3dbba52a-b519-41b1-aa1d-5e01ccce5480.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb119ae_869e_471a_8262_96e2260dda77
ELOP-693440-2016 | 6533 | 11/1/2016 9:17:52 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | View_of__View_of_floor_observing_any_material_and_debris.png | file://x:/photopub/docs/0000000509/71a3cce9-7fe3-4000-9cfe-91b35a14ceca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb119ae_869e_471a_8262_96e2260dda77
ELOP-693440-2016 | 6533 | 11/1/2016 9:17:52 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Log_of.png | file://x:/photopub/docs/0000000509/f6d76eb9-10e1-4737-8da9-85758ad416f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb119ae_869e_471a_8262_96e2260dda77
ELOP-693440-2016 | 6533 | 11/1/2016 9:17:52 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | View_of__View_of_any_dust_accumulation_on_cable_tray.png | file://x:/photopub/docs/0000000509/2df55ded-4b9d-44c7-9898-ac8b63c2be0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb119ae_869e_471a_8262_96e2260dda77
ELOP-693440-2016 | 6533 | 11/1/2016 9:17:52 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Air-conditioning___air-conditioning_system_for_PLC_cabinet.png | file://x:/photopub/docs/0000000509/4c26adcc-83b5-4b22-9b92-9efbd1a6ab4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb119ae_869e_471a_8262_96e2260dda77
ELOP-693440-2016 | 6533 | 11/1/2016 9:17:52 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Observation_of.png | file://x:/photopub/docs/0000000509/10a6d54e-6e5b-4715-813c-5726c20fa590.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb119ae_869e_471a_8262_96e2260dda77
ELOP-693440-2016 | 6533 | 11/1/2016 9:17:52 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Log_of__log_of_safety_meeting_minutes_shift_a.png | file://x:/photopub/docs/0000000509/6a3acf40-16ff-46f1-8882-e5ba31a9844c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb119ae_869e_471a_8262_96e2260dda77
ELOP-693440-2016 | 6533 | 11/1/2016 9:17:52 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Do___View_of_cable_tray_in_electrical_room.png | file://x:/photopub/docs/0000000509/da5dd88a-9ffd-4f9e-9593-7c9040b706e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb119ae_869e_471a_8262_96e2260dda77
ELOP-693440-2016 | 6533 | 11/1/2016 9:17:52 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Copy_of___copy_of_dust_mitigation_plan_note_division_date.png | file://x:/photopub/docs/0000000509/8821b8e9-a8ca-4131-8948-5e956959b0f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb119ae_869e_471a_8262_96e2260dda77
GAIN-687393-2016 | GA-267379-2015 | 10/28/2016 12:33:42 PM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | New plastic venting off boiler needs to extend through existing event | 2 | Side wall vent termination not compliant with installation instructions | Concealed_vent.png | file://x:/photopub/docs/0000000507/2126ce6b-7d2a-4c25-ba97-a8026191d01d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22d0e457_fc34_4340_b9c5_77fb4cbf5e53
GAIN-687397-2016 | GA-396707-2016 | 10/28/2016 12:50:12 PM | ASSESS: GA: Final | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | When gas value armature brakes and allows uncontrolled flow of Gas to escaping Gas will circulate back through the combustion are opening causing a gas smell and possible build evacuation | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | Vent_termination.png | file://x:/photopub/docs/0000000507/9661485c-8a57-43c5-8cbb-19ae2c6da48e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48c9ddcf_ab31_4e49_8e1d_75aef4969321
ELIN-706993-2016 | EL-464946-2016 | 11/21/2016 2:00:00 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Found feeder cable in main service combination panel has 120/240 volt 3 wire 250 KCM sized aluminum conductors which has the current carrying conductors (the two hots) split into 4 separate conductor ends (2 conductor ends per phase). Found the two hot conductors had a minimal amount of insulating tape and these conductors were terminated onto 4 terminals of 200 amp breaker. When electrical equipment is altered and modified using unapproved wiring methods, the electrical equipment is unapproved for the use and is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 4.png | file://x:/photopub/docs/0000000520/487b9039-0589-46a6-bef6-1a13cfab2552.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1df094dd_96b4_48f2_a71e_77bfa11654c1
ELIN-706993-2016 | EL-464946-2016 | 11/21/2016 2:00:00 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Found feeder cable in main service combination panel has 120/240 volt 3 wire 250 KCM sized aluminum conductors which has the current carrying conductors (the two hots) split into 4 separate conductor ends (2 conductor ends per phase). Found the two hot conductors had a minimal amount of insulating tape and these conductors were terminated onto 4 terminals of 200 amp breaker. When electrical equipment is altered and modified using unapproved wiring methods, the electrical equipment is unapproved for the use and is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 2.png | file://x:/photopub/docs/0000000520/4788148b-e6a4-4850-84be-6347801e8d77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1df094dd_96b4_48f2_a71e_77bfa11654c1
ELIN-706993-2016 | EL-464946-2016 | 11/21/2016 2:00:00 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Found feeder cable in main service combination panel has 120/240 volt 3 wire 250 KCM sized aluminum conductors which has the current carrying conductors (the two hots) split into 4 separate conductor ends (2 conductor ends per phase). Found the two hot conductors had a minimal amount of insulating tape and these conductors were terminated onto 4 terminals of 200 amp breaker. When electrical equipment is altered and modified using unapproved wiring methods, the electrical equipment is unapproved for the use and is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 1.png | file://x:/photopub/docs/0000000520/0f9051be-e512-47ad-bea9-f8f2567fa98f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1df094dd_96b4_48f2_a71e_77bfa11654c1
ELIN-706993-2016 | EL-464946-2016 | 11/21/2016 2:00:00 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Found feeder cable in main service combination panel has 120/240 volt 3 wire 250 KCM sized aluminum conductors which has the current carrying conductors (the two hots) split into 4 separate conductor ends (2 conductor ends per phase). Found the two hot conductors had a minimal amount of insulating tape and these conductors were terminated onto 4 terminals of 200 amp breaker. When electrical equipment is altered and modified using unapproved wiring methods, the electrical equipment is unapproved for the use and is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 3.png | file://x:/photopub/docs/0000000520/90476ae5-a77e-4dee-b504-fb5bbb3ba6c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1df094dd_96b4_48f2_a71e_77bfa11654c1
ELIN-706993-2016 | EL-464946-2016 | 11/21/2016 2:00:00 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Found feeder cable in main service combination panel has 120/240 volt 3 wire 250 KCM sized aluminum conductors which has the current carrying conductors (the two hots) split into 4 separate conductor ends (2 conductor ends per phase). Found the two hot conductors had a minimal amount of insulating tape and these conductors were terminated onto 4 terminals of 200 amp breaker. When electrical equipment is altered and modified using unapproved wiring methods, the electrical equipment is unapproved for the use and is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 5.png | file://x:/photopub/docs/0000000520/fc005193-0f33-4076-ab91-a28b4a7a5680.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1df094dd_96b4_48f2_a71e_77bfa11654c1
ELIN-712069-2016 | EL-444895-2016 | 11/29/2016 12:45:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 200 amp, 120/240 volt type 1 main distribution panel installed were subject to outdoor elements. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_distribution_subject_to_outdoor_elements.png | file://x:/photopub/docs/0000000523/92727dff-5a7c-49c2-be94-83262e3eaf24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__66b7b6c1_cdf7_4147_8ce6_f7f764b03a2a
ELIN-713564-2016 | EL-427932-2016 | 11/29/2016 9:37:38 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | 20 amp, 120 volt non-metallic cable installed below 1.5 meters with no mechanical protection. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD90_no_mech_protection.png | file://x:/photopub/docs/0000000523/beab0619-0f57-472e-9bc7-6fa9e7a84b52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__952a2484_0b7b_4b96_8cd7_9f36ed04f638
GAIN-694550-2016 | GA-459326-2016 | 11/29/2016 3:15:54 PM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | Vent termination does not comply with certified manufacturers installation instructions. Damage to appliance and/or building wall could occur from not following installation instructions. | 2 | Side wall vent termination not compliant with installation instructions | Non_compliant_vent_termination.png | file://x:/photopub/docs/0000000523/e039eb6a-9d8a-450a-8ce8-5a031c7ca223.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92b94968_fc34_49ee_9c0a_bedd762efb92
ELIN-708840-2016 | EL-470517-2016 | 11/25/2016 9:23:42 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Replaced_panel__replaced_panel_board_100_amp_main_breaker_protected_by_50_amp_outside.png | file://x:/photopub/docs/0000000521/533bd8c0-3358-4790-a678-feee5b52b7fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d7476ce_ab83_4b26_8a5d_2408fbb8d0d8
ELIN-708840-2016 | EL-470517-2016 | 11/25/2016 9:23:42 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Silver_label__Silver_label_35887_apply_to_paddleboard.png | file://x:/photopub/docs/0000000521/d568a92d-87c3-4a23-b951-43657854ddd1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d7476ce_ab83_4b26_8a5d_2408fbb8d0d8
ELIN-708840-2016 | EL-470517-2016 | 11/25/2016 9:23:42 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Condition_of__condition_of_electrical_equipment_acceptable.png | file://x:/photopub/docs/0000000521/aba2d185-2dbc-450d-8aec-c942f5483443.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d7476ce_ab83_4b26_8a5d_2408fbb8d0d8
EDIN-413126-2015 | ED-085445-2014 | 10/27/2016 4:56:49 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | Hydraulic flexible hose must have a safety factor of 10 times working pressure | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Hose2.png | file://x:/photopub/docs/0000000506/553e34e4-61df-4b3c-aedb-43b296ae0ea0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03fa3e08_f6b8_4dba_84f5_a36b7a9c217c
EDIN-413126-2015 | ED-085445-2014 | 10/27/2016 4:56:49 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | Hydraulic flexible hose must have a safety factor of 10 times working pressure | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Hose1.png | file://x:/photopub/docs/0000000506/da9476b9-6156-48bc-ac43-228827224980.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03fa3e08_f6b8_4dba_84f5_a36b7a9c217c
EDIN-413126-2015 | ED-085445-2014 | 10/27/2016 4:56:49 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | Hydraulic flexible hose must have a safety factor of 10 times working pressure | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | MR.png | file://x:/photopub/docs/0000000506/757bddbc-eda3-46a8-8159-7986b8884b6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03fa3e08_f6b8_4dba_84f5_a36b7a9c217c
EDIN-413126-2015 | ED-085445-2014 | 10/27/2016 4:56:49 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | Hydraulic flexible hose must have a safety factor of 10 times working pressure | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Shoring.png | file://x:/photopub/docs/0000000506/4f06aac1-dcc5-4c4d-851b-c712ed9870f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03fa3e08_f6b8_4dba_84f5_a36b7a9c217c
EDIN-413126-2015 | ED-085445-2014 | 10/27/2016 4:56:49 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | Hydraulic flexible hose must have a safety factor of 10 times working pressure | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Guide.png | file://x:/photopub/docs/0000000506/a059c108-cf5b-4012-840e-ceba1130de18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03fa3e08_f6b8_4dba_84f5_a36b7a9c217c
EDIN-413126-2015 | ED-085445-2014 | 10/27/2016 4:56:49 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | Hydraulic flexible hose must have a safety factor of 10 times working pressure | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Cam_running_clearance.png | file://x:/photopub/docs/0000000506/04d934d7-4e66-4c92-919c-ee0ac0ad717e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03fa3e08_f6b8_4dba_84f5_a36b7a9c217c
ELIN-681727-2016 | EL-430649-2016 | 10/27/2016 1:47:58 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | The difference of equipotential plane could be a shock hazard between the two systems. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Box_support.png | file://x:/photopub/docs/0000000506/a384000f-a550-4f9b-88ba-220e445ebf24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__053a2bbe_9127_400a_b3d1_a05e142d50b3
ELIN-681727-2016 | EL-430649-2016 | 10/27/2016 1:47:58 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | The difference of equipotential plane could be a shock hazard between the two systems. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Bonding_strap_in_sub_panel.png | file://x:/photopub/docs/0000000506/5bc8255b-4a50-48fc-9c69-030cd373c153.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__053a2bbe_9127_400a_b3d1_a05e142d50b3
ELIN-681727-2016 | EL-430649-2016 | 10/27/2016 1:47:58 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | The difference of equipotential plane could be a shock hazard between the two systems. | 3 | Equipment Gas line, cast or water pipe has not been bonded | NMD_14_2_for_island_receptacle__.png | file://x:/photopub/docs/0000000506/f5cb1280-d550-4e3c-a94e-ff5ff4e09168.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__053a2bbe_9127_400a_b3d1_a05e142d50b3
ELIN-681727-2016 | EL-430649-2016 | 10/27/2016 1:47:58 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | The difference of equipotential plane could be a shock hazard between the two systems. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Conduit_missing___conduit_missing_for_floor_heat.png | file://x:/photopub/docs/0000000506/72170090-9e78-4c04-94b4-aab229c66eca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__053a2bbe_9127_400a_b3d1_a05e142d50b3
ELIN-696635-2016 | UW-462605-2016 | 11/3/2016 3:15:05 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Found exposed energized conductors and bus bars in panelboard while panel cover is missing and cover is confirmed to not be installed for several days. When energized panelboards are missing panel covers the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | cover_missing_on_exposed_energized_conductors_bus_2.png | file://x:/photopub/docs/0000000511/5dc39b4f-f6a9-473d-9a05-a4b011bf82c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e04786bb_beef_4f03_96ab_adfac009e6d5
GAHE-708130-2016 | HE-470073-2016 | 11/21/2016 11:19:51 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Propane tank does not meet the required clearance to combustibles as per B149.2 code. | 3 | Clearance to combustibles not maintained | 3165_Ball.png | file://x:/photopub/docs/0000000518/2839509d-8a2e-417a-bef2-fee67ad5f79c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02c66338_6e7d_4b64_a3ac_2d9974fc170b
ELIN-697213-2016 | EL-341987-2016 | 11/7/2016 11:38:22 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Dry type connectors used in a wet location. This is a shock hazard as water can enter the electrical enclosure through the connector. | 3 | Conductors Equipment is not approved for the specific use. | E.png | file://x:/photopub/docs/0000000512/ec5dc47a-952f-4665-9d6f-68b2083ef434.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32fecd97_eaed_4767_a32e_52a87d3df853
ELIN-697213-2016 | EL-341987-2016 | 11/7/2016 11:38:22 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Dry type connectors used in a wet location. This is a shock hazard as water can enter the electrical enclosure through the connector. | 3 | Conductors Equipment is not approved for the specific use. | D.png | file://x:/photopub/docs/0000000512/7ea4c862-1c81-4bd6-9859-7d23d4f42539.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32fecd97_eaed_4767_a32e_52a87d3df853
ELIN-697213-2016 | EL-341987-2016 | 11/7/2016 11:38:22 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Dry type connectors used in a wet location. This is a shock hazard as water can enter the electrical enclosure through the connector. | 3 | Conductors Equipment is not approved for the specific use. | C.png | file://x:/photopub/docs/0000000512/2fb87dda-ce1b-4688-b0e9-fb3fc72d99c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32fecd97_eaed_4767_a32e_52a87d3df853
GAIN-701448-2016 | GA-384769-2016 | 11/15/2016 8:45:51 AM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | 635_Sentinal.png | file://x:/photopub/docs/0000000516/4d9bce09-4fcb-4857-8b74-ef0039245e92.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f436dd38_7ee6_4f79_b658_9d9cc0875bfd
GAIN-697429-2016 | GA-437315-2016 | 11/15/2016 12:02:49 PM | ASSESS: GA: Final | png | #asFound | GA134 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | 2 | 2 |  | 2 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | Sophia.png | file://x:/photopub/docs/0000000516/5f4827f6-eed1-4303-b2e4-bcc005ee28f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e74563b5_8d8c_480f_84ab_4d67791c120d
GAHE-694630-2016 | HE-459613-2016 | 11/1/2016 8:00:28 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Chimney_liner.png | file://x:/photopub/docs/0000000510/25841e17-4c94-4dda-97dd-df92a15effa8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__88eab99e_9a9f_4802_8048_7a4d7b83fc65
GAIN-710241-2016 | GA-389420-2016 | 11/24/2016 1:11:09 PM | ASSESS: GA: Final | png | #asFound | GA055 | Bonding for Corrugated Stainless Steel Tubing missing | 3 | 3 | Un bonded corrugated stainless steel tubing(CSST) gas line. Potential for shock hazard should gas line become inadvertently energized. This material is also susceptible to lighting strikes and has resulted in structure fires due to perforation of the tubing wall. Shock hazard and or fire risk. | 3 | Bonding for Corrugated Stainless Steel Tubing missing | Second_ave.png | file://x:/photopub/docs/0000000521/7b59a7b2-9263-4ef2-a206-910ed523ca6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a948d58a_91eb_4738_a036_abecc2039487
GAHE-713082-2016 | HE-473620-2016 | 11/28/2016 1:33:51 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | While assessing a hazard report from the local fire department, i found an uncapped gas line protected by a single shut off. Should someone have bumped the shut off valve open, or partially open, an uncontrolled release or raw gas would have occurred. Should this gas find a source of ignition a fire or explosion could have occurred. Furthermore given the close proximity to standing pilots in the adjacent kitchen equipment, there was a very high probability that this could have occurred. | 5 | Open gas line connected to fuel supply (no cap/plug) | Open_gas_line_2.png | file://x:/photopub/docs/0000000522/16b7c01a-cd2c-4671-a3c1-fd87b645558c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cef73ba0_94b6_4045_8c69_12162fe3252a
GAHE-713082-2016 | HE-473620-2016 | 11/28/2016 1:33:51 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | While assessing a hazard report from the local fire department, i found an uncapped gas line protected by a single shut off. Should someone have bumped the shut off valve open, or partially open, an uncontrolled release or raw gas would have occurred. Should this gas find a source of ignition a fire or explosion could have occurred. Furthermore given the close proximity to standing pilots in the adjacent kitchen equipment, there was a very high probability that this could have occurred. | 5 | Open gas line connected to fuel supply (no cap/plug) | Open_gas_line.png | file://x:/photopub/docs/0000000522/9c011c09-a213-456e-934c-863f2954a410.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cef73ba0_94b6_4045_8c69_12162fe3252a
ELIN-696635-2016 | UW-462605-2016 | 11/3/2016 3:15:05 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Found exposed energized conductors and bus bars in panelboard while panel cover is missing and cover is confirmed to not be installed for several days. When energized panelboards are missing panel covers the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | cover_missing_on_exposed_energized_conductors_bus_3.png | file://x:/photopub/docs/0000000511/b9d3496a-ee01-4def-af43-aa9946f376e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e04786bb_beef_4f03_96ab_adfac009e6d5
ELIN-696635-2016 | UW-462605-2016 | 11/3/2016 3:15:05 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Found exposed energized conductors and bus bars in panelboard while panel cover is missing and cover is confirmed to not be installed for several days. When energized panelboards are missing panel covers the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | cover_missing_on_exposed_energized_conductors_bus_5.png | file://x:/photopub/docs/0000000511/36edf715-9603-4e4b-827e-50ab4691c233.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e04786bb_beef_4f03_96ab_adfac009e6d5
ELIN-696635-2016 | UW-462605-2016 | 11/3/2016 3:15:05 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Found exposed energized conductors and bus bars in panelboard while panel cover is missing and cover is confirmed to not be installed for several days. When energized panelboards are missing panel covers the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | cover_missing_on_exposed_energized_conductors_bus_4.png | file://x:/photopub/docs/0000000511/49b4a40e-6207-4ed4-b61b-37f3b0eef5fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e04786bb_beef_4f03_96ab_adfac009e6d5
GAIN-669357-2016 | GA-441462-2016 | 10/7/2016 10:38:14 AM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | Missing_orifice.png | file://x:/photopub/docs/0000000497/b2768199-11db-4f74-bd0e-2a7d2b552a36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42ca5033_c656_4ad3_9172_846ed2d79096
ELIN-688667-2016 | 5398875 | 11/9/2016 2:53:52 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | The overhead line wiring is attached to a tree branch. The wire is subject to physical stress and may be damaged creating a fire hazard. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Mid_span_support.png | file://x:/photopub/docs/0000000514/50eac39d-d812-4aa7-a9bd-bc59695062f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__318088ef_af8b_4e09_b023_9f5868f5bc38
ELIN-699534-2016 | EL-431403-2016 | 11/9/2016 8:51:12 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 3 | The service cable is installed against the exterior plywood without mechanical protection. Siding fasteners still to be installed may penetrate the cable and create a fire hazard. Reference: Page 37-39 "where did I go wrong" BCSA's most recent Tech. Talk. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Service_cable.png | file://x:/photopub/docs/0000000514/67f95b5f-f2f8-4db7-8f7b-70d679807590.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__05a1f8f0_7702_477b_8d42_7ce32d36556a
ELIN-698014-2016 | EL-461752-2016 | 11/9/2016 9:35:49 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | 120 volt cabling installed too close to the front of the wall stud face without mechanical protection. Wallboard fasteners may penetrate the cable causing a fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Branch_circuit.png | file://x:/photopub/docs/0000000514/b80e617e-5a24-49e9-a365-e33b15b9637b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37c61e85_9547_4514_b705_3cfdcce2ff79
ELIN-699906-2016 | EL-320039-2015 | 11/9/2016 10:24:42 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | An energized outdoor wall receptacle was hanging from the box with no cover plate. The outlet creates a shock hazard as there are bare terminals and parts exposed. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outlet.png | file://x:/photopub/docs/0000000514/c1065846-6850-498f-9c46-067c9262635f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b90e661d_4d80_4a82_8e6b_a26ae5846c82
ELIN-667616-2016 | EL-414937-2016 | 9/20/2016 11:49:14 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | Installation of rigid PVC conduit is in a wall where thermal insulation will be used, temperatures that are likely to occur at this location will result in damage to service conduits. Protection and control of the electrical system in this portion of the installation does not provide adequate controls to prevent a failure. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_conduits_rigid_PVC_in_wall.png | file://x:/photopub/docs/0000000488/a5c321a7-1d39-4900-92f8-cfb3a0582b69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f3f91eb6_ff6a_42ee_a51d_a0507418ac40
ELIN-697213-2016 | EL-341987-2016 | 11/7/2016 11:38:22 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Dry type connectors used in a wet location. This is a shock hazard as water can enter the electrical enclosure through the connector. | 3 | Conductors Equipment is not approved for the specific use. | B.png | file://x:/photopub/docs/0000000512/d247f76c-6882-4697-859e-12ae4be9ba7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32fecd97_eaed_4767_a32e_52a87d3df853
ELIN-697213-2016 | EL-341987-2016 | 11/7/2016 11:38:22 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Dry type connectors used in a wet location. This is a shock hazard as water can enter the electrical enclosure through the connector. | 3 | Conductors Equipment is not approved for the specific use. | A.png | file://x:/photopub/docs/0000000512/d902c1ae-1ba1-4a74-94c2-3fbfd6896785.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32fecd97_eaed_4767_a32e_52a87d3df853
ELIN-700181-2016 | EL-465107-2016 | 11/9/2016 12:57:35 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 2 | A three conductor cable was supported with a staple approved for only a two conductor cable resulting in damage to the cable sheath. There is potential for damage to the conductor insulation or the conductors themselves which could lead to thermal damage to the cable and surrounding combustible material. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Damaged_cable_sheath_at_staple_location.png | file://x:/photopub/docs/0000000513/a60f2719-652c-4bb8-bd84-aa6200626bd3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__648625c7_0f74_4c75_9db0_55c69c45685e
BPVOP-700071-2016 | 3136371 | 11/8/2016 11:51:03 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or 125psig) air receiver for the last 5 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | pressure_relief_device_overdue.png | file://x:/photopub/docs/0000000513/b4696664-b3a4-45b3-bc37-838bd10c04c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a39df791_2875_4cf0_a8f5_4575e392da40
BPVOP-700068-2016 | 2718376 | 11/8/2016 11:42:32 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve on this air receiver (high pressure, 125 PSIG) for the last 6 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | pressure_relief_device_1.png | file://x:/photopub/docs/0000000513/77f6015d-7798-4372-8c4a-16365425f0cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dae097b3_2adc_4872_bb55_4712c5725bd9
ELIN-700147-2016 | EL-430141-2016 | 11/8/2016 12:57:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Dry type equipment exposed to wet conditions | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Temporary_construction_service.png | file://x:/photopub/docs/0000000513/9958bf16-3298-4295-bc3c-3d896fe6e0da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8551b1a6_c7b8_4a6b_9ee3_bd5bbed842f5
ELIN-678860-2016 | EL-448213-2016 | 10/13/2016 3:04:35 PM | ASSESS: EL: Final | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 3 | The breaker installed to protect the circuit is rated greater than the rating of the receptacle and of the conductors in this instance. This could lead to overloading of the circuit causing thermal damage to the circuit which could result in a fire hazard. | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | The_white_breaker_is_a_20_amp_breaker_protecting_AWG__14_conductors_and_a_15_amp_receptacle_.png | file://x:/photopub/docs/0000000499/3c0bd498-0ec8-419f-b8e9-821ab9fdf503.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b8dd0cf_cef1_4d47_aa24_67831d38593f
ELIN-698590-2016 | EL-247443-2015 | 11/7/2016 1:38:11 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | Partial rough wiring of new apartment building. Each suite has a dining room & a bedroom plastic outlet box in the ceiling that are not marked as approved for fan support. These boxes will not adequately support ceiling fans which can result in failure of the box. This could cause injury to anyone sitting or standing below these boxes. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Boxes_used_for_fan_support.png | file://x:/photopub/docs/0000000512/1396ef22-7848-43a9-9c84-deba17367903.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e8c6765_e40f_4cbc_a879_9e2738c23094
ELIN-675149-2016 | EL-421171-2016 | 10/4/2016 11:42:11 AM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | Cover not installed for junction box above main panel. Conductors in junction are exposed to accidental contact providing a risk of shock and fore to persons and property. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Junction_without_cover.png | file://x:/photopub/docs/0000000495/315a215b-5720-4b1c-99a8-56419227afc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32764555_67ea_4195_9100_ee1dcc1af6cf
EDIN-676021-2016 | ED-417300-2016 | 10/3/2016 3:22:02 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | The deck cover provides a safe and stable deck for the shopping carts to either enter or exit the Cartveyor. During an acceptance inspection only a temporary wooden deck was installed at both the top and bottom decks. The unstable temporary deck cover poses a tripping and unstable jamming hazard for the shopping carts used by the public with the cartveyor. It was found the Elevator Contractor failed to order the deck cover in time. The cartveyor serves 2 floors and is installed in a commercial supermarket. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Cartveyor_temporary_deck_cover_Oct_3_2016.png | file://x:/photopub/docs/0000000495/e441bf58-5e79-4abf-a6ba-face7f92e6c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c57f899_e895_4a22_ae95_c89a433cb4a8
EDIN-676022-2016 | ED-417307-2016 | 10/3/2016 3:39:01 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | The deck cover provides a safe and stable deck for the shopping carts to either enter or exit the Cartveyor. During an acceptance inspection only a temporary wooden deck was installed at both the top and bottom decks. The unstable temporary deck cover poses a tripping and unstable jamming hazard for the shopping carts used by the public with the cartveyor. It was found the Elevator Contractor failed to order the deck cover in time. The cartveyor serves 2 floors and is installed in a commercial supermarket. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Temporary_deck_cover_cartveyor_Oct_3_2016.png | file://x:/photopub/docs/0000000495/e2dc9938-f054-435b-8735-9f9f9fc2624c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3990af35_017b_424e_ad80_a18309949ccd
EDIN-676018-2016 | ED-417303-2016 | 10/4/2016 7:27:43 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | The deck cover provides a safe and stable deck for the shopping carts to either enter or exit the Cartveyor. During an acceptance inspection only a temporary wooden deck was installed at both the top and bottom decks. The unstable temporary deck cover poses a tripping and unstable jamming hazard for the shopping carts used by the public with the cartveyor. It was found the Elevator Contractor failed to order the deck cover in time. The cartveyor serves 2 floors and is installed in a commercial supermarket. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Cartveyor_temporary_deck_cover_Oct_4_2016.png | file://x:/photopub/docs/0000000495/68af7028-a252-42e0-b6c2-7fbefc3c6bd0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce18cfc5_39ce_4690_9158_5c481d9c69e2
EDIN-676019-2016 | ED-417306-2016 | 10/4/2016 7:03:26 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | The deck cover provides a safe and stable deck for the shopping carts to either enter or exit the Cartveyor. During an acceptance inspection only a temporary wooden deck was installed at both the top and bottom decks. The unstable temporary deck cover poses a tripping and unstable jamming hazard for the shopping carts used by the public with the cartveyor. It was found the Elevator Contractor failed to order the deck cover in time. The cartveyor serves 2 floors and is installed in a commercial supermarket. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Cartveyor_temporary_deck_cover__Oct_4_2016.png | file://x:/photopub/docs/0000000495/6388d072-f29d-4437-a6de-ff8e58595162.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9cf07f2f_be17_4ca6_89ab_b8efe1ad95ca
ELIN-667895-2016 | EL-263532-2015 | 9/20/2016 3:58:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Box fill exceeded. This is a hazard as excessive heat can be created by having to many conductors in the device box. 10awg wire terminated on a device rated for 14awg wire. This is a fire hazard as the terminals on the device can fail and overheat from the stress created by the larger conductor. | 3 | Conductors Equipment is not approved for the specific use. | A.png | file://x:/photopub/docs/0000000488/b3dbf2d7-7acb-41c5-b4d0-4bc9768cedf7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47e3a5c1_6251_485a_b0ea_dff045e682a5
ELIN-667895-2016 | EL-263532-2015 | 9/20/2016 3:58:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Box fill exceeded. This is a hazard as excessive heat can be created by having to many conductors in the device box. 10awg wire terminated on a device rated for 14awg wire. This is a fire hazard as the terminals on the device can fail and overheat from the stress created by the larger conductor. | 3 | Conductors Equipment is not approved for the specific use. | B.png | file://x:/photopub/docs/0000000488/da8a5c8a-fb19-4df0-afb3-46e0ffb78aba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47e3a5c1_6251_485a_b0ea_dff045e682a5
ELIN-708281-2016 | EL-347481-2016 | 11/21/2016 12:10:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Point_of_a__Point_of_attachment_must_be_located_6_to_12_inches_below_weatherhead.png | file://x:/photopub/docs/0000000519/f54ed856-49cb-40f4-8f8d-e0d6714d1126.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8fe1e4de_1351_4c31_bf1d_eea9e56a4fec
ELIN-708281-2016 | EL-347481-2016 | 11/21/2016 12:10:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Metre_mounting__metre_mounting_bracket_must_be_used.png | file://x:/photopub/docs/0000000519/cce06b67-2300-433e-80af-215af7bea8ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8fe1e4de_1351_4c31_bf1d_eea9e56a4fec
ELIN-708281-2016 | EL-347481-2016 | 11/21/2016 12:10:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Dry_type__dry_type_connecter_used_in_an_outdoor_location_and_exposed_to_weather.png | file://x:/photopub/docs/0000000519/9a0b230f-bacc-4e52-83a0-89e4f5402a38.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8fe1e4de_1351_4c31_bf1d_eea9e56a4fec
GAIN-670560-2016 | GA-346216-2016 | 10/4/2016 12:10:14 PM | ASSESS: GA: Final | png | #asFound | GA068 | Improperly sized gas piping or tubing according to delivery pressure for a single appliance | 2 | 2 | Undersized appliance connector. Appliance will be under fired due to insufficient flow of gas through the undersized connector. | 2 | Improperly sized gas piping or tubing according to delivery pressure for a single appliance | Undersized_appliance_connector.png | file://x:/photopub/docs/0000000496/d932c232-6eae-4d5f-b8f4-7da6f2460026.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df9d4006_9d69_4b41_b7c6_d08ec14697a2
GAIN-701291-2016 | GA-247476-2015 | 11/9/2016 4:36:41 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | On demand water heater is installed with vent terminated too close to fresh air intake ducted into furnace return air. This could cause flu gases to recirculate into the furnace return air causing carbon monoxide to be distributed throughout home. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_clearance_to_mechanicalairintake.png | file://x:/photopub/docs/0000000514/c8901435-a4a7-473c-ae45-e2636457df23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__482cf2d5_ca40_439c_bd95_b33120dca87b
PRIN-712552-2016 | PR-449681-2016 | 11/29/2016 1:58:38 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | Skirting had not yet been installed at time of inspection, users of the conveyor could fall into unguarded conveyor if skirting is not installed correctly. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Skirting_not_installed.png | file://x:/photopub/docs/0000000523/ef283c59-2903-4a11-8542-03ee33bf6527.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__555cf2f7_efce_4f6d_8f5e_ff19220fbaa1
ELIN-662746-2016 | EL-186642-2014 | 9/27/2016 1:14:05 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Exposed splices. This is a shock hazard. Junction boxes require covers. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000491/18193a62-7499-4bb5-a8a0-d404a45828e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b60dced_aeac_4aa0_8b75_0611b6f7abb3
ELOP-669260-2016 | 5300882 | 9/22/2016 1:14:57 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 | Combustible dust has accumulated in the lower and vertical wireways on a 600 volt motor control center. This equipment is configured with components that arc when operating, and occasionally sparks can escape from these components. These sparks can escape control modules and drop into the wireways in the vertical and lower horizontal portions of the equipment which can cause property damage or injury to persons. | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Extra_fine_dust_accumulations_in_MCC_s.png | file://x:/photopub/docs/0000000489/edc5c78b-5e81-4945-aaa1-c1840f29271f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a779110c_554d_4260_9316_34cd2db0a098
GAIN-710328-2016 | GA-418807-2016 | 11/24/2016 2:03:38 PM | ASSESS: GA: Final | png | #asFound | GA045 | Gas connector passes through wall, floor, ceiling, partition or into appliance | 2 | 2 | Appliance connector installed passing through the outer case of the furnace. This may lead to a hole in the appliance connector and a gas leak in the home. | 2 | Gas connector passes through wall, floor, ceiling, partition or into appliance | Appliance_connector.png | file://x:/photopub/docs/0000000521/2fa6594d-86d6-4ad3-8059-6c45ade7e32c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15768ab6_af02_465a_864a_002a9bca9a33
ELIN-693365-2016 | EL-336578-2016 | 10/28/2016 4:56:27 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Feeder cables supplying power to sub-service equipment equipment must be properly sized to carry the load that they are supplying. This is required to prevent thermal damage to the cable, cable insulation, and the points where they terminate at equipment. This installation has 3 x #4/0 AWG feeder cables feeding 3 x 225A panel boards. The load on the panels are continuous lighting and air-conditioning loads that may overload the cables. Left uncorrected this is a potential fire hazard if cables or terminations over heat and fail. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Service_shed_in_and_deatched_building_in_the_back_ground.png | file://x:/photopub/docs/0000000507/0c780627-b5ee-432e-97e0-224873a734b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__790f48ef_57c3_4c63_9da7_41da64900ed9
ELIN-693365-2016 | EL-336578-2016 | 10/28/2016 4:56:27 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Feeder cables supplying power to sub-service equipment equipment must be properly sized to carry the load that they are supplying. This is required to prevent thermal damage to the cable, cable insulation, and the points where they terminate at equipment. This installation has 3 x #4/0 AWG feeder cables feeding 3 x 225A panel boards. The load on the panels are continuous lighting and air-conditioning loads that may overload the cables. Left uncorrected this is a potential fire hazard if cables or terminations over heat and fail. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Service_shed.png | file://x:/photopub/docs/0000000507/a26222fe-ac87-438e-a109-2fe5dfaa257c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__790f48ef_57c3_4c63_9da7_41da64900ed9
ELIN-693365-2016 | EL-336578-2016 | 10/28/2016 4:56:27 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Feeder cables supplying power to sub-service equipment equipment must be properly sized to carry the load that they are supplying. This is required to prevent thermal damage to the cable, cable insulation, and the points where they terminate at equipment. This installation has 3 x #4/0 AWG feeder cables feeding 3 x 225A panel boards. The load on the panels are continuous lighting and air-conditioning loads that may overload the cables. Left uncorrected this is a potential fire hazard if cables or terminations over heat and fail. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Under_ground_cables_terminated_to_splitter_at_service_shed.png | file://x:/photopub/docs/0000000507/88d0ef76-a5a5-411f-be16-58065719ff87.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__790f48ef_57c3_4c63_9da7_41da64900ed9
ELIN-697184-2016 | EL-462599-2016 | 11/8/2016 11:42:53 AM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Water ingress into panel. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Cable-1.png | file://x:/photopub/docs/0000000513/165f1641-445a-416b-9bdc-8c0f1ea10fc6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__499a151a_33cc_4bf8_9287_c3dbe2808bc2
ELIN-697184-2016 | EL-462599-2016 | 11/8/2016 11:42:53 AM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Water ingress into panel. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Service-1.png | file://x:/photopub/docs/0000000513/f9d2940f-a8af-4f38-b1c2-73ee9d76e344.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__499a151a_33cc_4bf8_9287_c3dbe2808bc2
GAIN-665416-2016 | GA-428246-2016 | 9/22/2016 1:15:53 PM | ASSESS: GA: Rough-In | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | Non compliant venting arrangement. 1/4" per foot grade required to prevent condensate from accumulating and damaging venting system. | 2 | Side wall vent termination not compliant with installation instructions | Non_compliant_sidewall_venting_arrangement_.png | file://x:/photopub/docs/0000000490/c4bcf57d-0d26-48bc-b78d-69321d0616dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5e9d782_3620_4c76_8dca_117a861cd767
ELIN-709552-2016 | EL-393659-2016 | 11/28/2016 2:24:04 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | AFCI protection has not been provided for all the 15A receptacles in the home, this could pose a fire hazard. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Panel.png | file://x:/photopub/docs/0000000522/2427d166-86fe-4423-9801-c17845ab2e3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__978e431b_6b85_4bfb_be0f_88962e4cbaff
ELIN-711175-2016 | EL-290110-2015 | 11/28/2016 2:52:21 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | A 2" rigid metal conduit has been used as a Service Mast for an overhead 200 amp 208 volt service, the conduit is not approved for this use or the size required. This could cause a failure of the conduit a pose harm to persons and equipment. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_Mast.png | file://x:/photopub/docs/0000000522/8ea86cdd-fdb0-497e-8fd0-e37a16354458.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8693a5ff_56a2_4c2c_93d1_296bb967bbbb
ELIN-710066-2016 | EL-416158-2016 | 11/28/2016 8:46:45 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | At the 120/240 volt 200 amp Main Panel the ground wire from the ground electrode has been terminated to a bonding lug instead of to the neutral bus. This could pose a shock hazard for persons and equipment damage as the overcurrent devices (breakers) may not function or trip as designed without an effective ground point reference. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding.png | file://x:/photopub/docs/0000000522/8d104fe2-434d-461e-8489-02e026443041.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e834688_bc02_4374_a8fd_136b758006f3
BPVOP-687994-2016 | 2273239 | 10/20/2016 11:08:27 AM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP058 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | 3 | 3 | Corrosion and scale deposits have reduced tube thickness to the point of failure. | 3 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | Tube_2.png | file://x:/photopub/docs/0000000515/6f6e1d31-93d3-4193-9f5f-32ed3b43881b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85062a31_df0f_46c0_856e_855b972a4a1d
BPVOP-687994-2016 | 2273239 | 10/20/2016 11:08:27 AM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP058 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | 3 | 3 | Corrosion and scale deposits have reduced tube thickness to the point of failure. | 3 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | Scale.png | file://x:/photopub/docs/0000000515/c0bb9c02-1ad2-473e-ae76-d41e5f999db2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85062a31_df0f_46c0_856e_855b972a4a1d
BPVOP-687994-2016 | 2273239 | 10/20/2016 11:08:27 AM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP058 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | 3 | 3 | Corrosion and scale deposits have reduced tube thickness to the point of failure. | 3 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | Tube_1.png | file://x:/photopub/docs/0000000515/7fe563aa-0426-4755-a248-cf4077c6285e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85062a31_df0f_46c0_856e_855b972a4a1d
BPVIN-697505-2016 | BPV-463288-2016 | 10/14/2016 7:34:36 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP142 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | 3 | 3 | Upon assessment it is determined that there is no carbon dioxide detection system installed in the bulk carbon dioxide storage room. Without a detection system there is no way to warn personnel (intending to enter the room) of concentration above exposure limit, in the event of carbon dioxide leakage from the system (pipe, fittings etc.) and it can lead to fatality. | 3 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | BULK_CARBON_DIOXIDE_STORAGE_ROOM_WITHOUT_DETECTION_SYSTEM.png | file://x:/photopub/docs/0000000513/6e41fdbd-a9e1-4812-8bc9-d6dc0314f9d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c188868_f9f7_47f1_a78c_db1608415724
GAHE-711986-2016 | HE-472929-2016 | 11/25/2016 1:13:01 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Tank is located in wood frame shed with no vehicle protection to prevent trailer from backing into tank. | 3 | Clearance to combustibles not maintained | Close_tank_overview.png | file://x:/photopub/docs/0000000521/a6642b10-5a61-4427-ad4b-6c52b51c3104.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f71875a_1417_4e54_a347_44f905a8cef5
GAHE-711986-2016 | HE-472929-2016 | 11/25/2016 1:13:01 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Tank is located in wood frame shed with no vehicle protection to prevent trailer from backing into tank. | 3 | Clearance to combustibles not maintained | Tank_overview.png | file://x:/photopub/docs/0000000521/98706be8-7035-4c95-b4ca-e00003d0ba64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f71875a_1417_4e54_a347_44f905a8cef5
ELIN-670384-2016 | EL-442199-2016 | 9/26/2016 9:20:32 AM | ASSESS: EL: Service Connection | png | #asFound | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 4 | 4 | Access has not been provided for the main disconnect switch for the occupants of a future suite in the basement. This creates a hazard to the occupants of the suite or Fire dept as they cannot readily disconnect the supply power to their unit in the event of a fire or equipment failure. | 4 | General Location of equipment does not allow for proper access to disconnecting means | Suite_disconnect_in_main_garage.png | file://x:/photopub/docs/0000000490/cb25ea0b-7e11-4462-9c01-4b4d02602706.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__084d5b3f_0a63_4968_92fd_1dcd7c114030
GAIN-669930-2016 | GA-441334-2016 | 9/23/2016 10:37:25 AM | ASSESS: GA: Rough-In | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Strike_protection_required_.png | file://x:/photopub/docs/0000000491/2f522bef-8ab8-4dc2-a4e0-f44734f84bb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bb1b9eb_4bec_4df8_a2c2_a179b11444e9
ELIN-677889-2016 | EL-420962-2016 | 10/6/2016 2:40:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | In an existing single family dwelling, a new service upgrade was found withe the system ground not attached to the identified conductor as required. This could lead to a thermal effect. Pic attached. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_and_bonding.png | file://x:/photopub/docs/0000000496/9307e2ae-6923-4f99-a323-22260570372e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94fac00a_6c15_4f21_b718_95d4739860db
ELIN-709555-2016 | EL-384214-2016 | 11/28/2016 12:36:52 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | The 20 amp 120 volt receptacles provided on the kitchen island by the island sink are not GFCI protected. This could pose a shock hazard to persons and possible equipment damage to appliances plugged into these outlets. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Island_Receptacle.png | file://x:/photopub/docs/0000000522/495a921f-8ada-4a3f-a720-d1aa62ac5310.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72a7c24f_d52f_48de_b7f4_ab412c925a23
ELIN-699911-2016 | EL-450526-2016 | 11/14/2016 11:44:29 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Non metallic sheathed cable used to provide temporary power to meter base. Non metallic sheathed cable is required to be protected from damage below 1.5 meters from grade, non metallic sheathed cable jacket does not provide mechanical protection to conductors when installed in this manner. Damage to cable could result in a shock or fire hazard to persons or property. | 3 | Conductors Equipment is not approved for the specific use. | NMD90_used_for_temporary_power_to_meter_base__.png | file://x:/photopub/docs/0000000515/217e68a0-5460-4b8d-a0c3-e584f113807d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e33f711_2da4_45f7_98a8_f33bec6827c4
ELIN-701247-2016 | EL-457116-2016 | 11/10/2016 1:25:46 PM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | 20 amp construction receptacles are not ground fault circuit interruptor protected. This could be a hazard to persons because the purpose of a ground fault circuit interruptor is to shuts off an electric power circuit when it detects that current is flowing along an unintended path, such as through water or a person. Most construction sites are wet and damp from the weather elements. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 20_amp_receptacle_not_gfci.png | file://x:/photopub/docs/0000000514/2cabca01-d66b-4dab-9a25-2ef3cc92addc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ac23495_c371_4a9d_a1c6_e443089822a2
BPVIN-684905-2016 | BPV-441045-2016 | 10/14/2016 11:28:57 AM | ASSESS: BPV IN: Installation REF/PV | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Boiler has no pressure or temperature gauges, no lockable disconnect switch and no E-Stop, Pressure relief valve does not discharge to a safe location. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_Gauges_No_SV_Discharge_piping_No_Lockable_Disconnect.png | file://x:/photopub/docs/0000000501/27942124-c4c9-4164-b394-1513fff998cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4668533_37fb_4d47_9370_a7e18c0784d1
ELIN-682862-2016 | EL-443431-2016 | 10/13/2016 9:19:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 3 | Wire size and rating of receptacles not adequately protected due to oversized breaker. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Sheridan_2.png | file://x:/photopub/docs/0000000499/e404d4b0-decd-475e-b29f-bfb7b8e0388a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4479506c_00f3_413e_bdc3_45ab14caeca4
ELIN-682862-2016 | EL-443431-2016 | 10/13/2016 9:19:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 3 | Wire size and rating of receptacles not adequately protected due to oversized breaker. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Sheridan_1.png | file://x:/photopub/docs/0000000499/63882701-aa52-44be-8591-18b36e32739a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4479506c_00f3_413e_bdc3_45ab14caeca4
ELHE-706720-2016 | HE-469431-2016 | 11/18/2016 9:56:50 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Service equipment is no longer approved , as the condition is deprecated and building structure has changed since original install. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_conduit.png | file://x:/photopub/docs/0000000518/488de718-d458-4fce-b044-c0a798bc673f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbf979c3_a801_4d15_aaeb_12e69b74e303
ELHE-706720-2016 | HE-469431-2016 | 11/18/2016 9:56:50 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Service equipment is no longer approved , as the condition is deprecated and building structure has changed since original install. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Meter_mounting_.png | file://x:/photopub/docs/0000000518/6f1fc04c-e2db-4762-8785-52219eff1aab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbf979c3_a801_4d15_aaeb_12e69b74e303
ELHE-706720-2016 | HE-469431-2016 | 11/18/2016 9:56:50 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Service equipment is no longer approved , as the condition is deprecated and building structure has changed since original install. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Pole_condition_.png | file://x:/photopub/docs/0000000518/4d3deb87-87f8-4f99-ae35-2e5c3b776dde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbf979c3_a801_4d15_aaeb_12e69b74e303
ELHE-706720-2016 | HE-469431-2016 | 11/18/2016 9:56:50 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Service equipment is no longer approved , as the condition is deprecated and building structure has changed since original install. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_pole.png | file://x:/photopub/docs/0000000518/383b4a71-3771-4f58-8a60-32c238c56cdd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbf979c3_a801_4d15_aaeb_12e69b74e303
ELHE-706720-2016 | HE-469431-2016 | 11/18/2016 9:56:50 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Service equipment is no longer approved , as the condition is deprecated and building structure has changed since original install. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_pole_2.png | file://x:/photopub/docs/0000000518/24531762-d820-4b4f-8945-fd0ad0984d21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbf979c3_a801_4d15_aaeb_12e69b74e303
GAIN-695923-2016 | GA-454548-2016 | 11/18/2016 11:39:54 AM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | Risk of combustion air inlet getting blocked with snow. Rich running condition could create carbon monoxide due to incomplete combustion. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Northgate.png | file://x:/photopub/docs/0000000518/ec81b1d3-ac5d-48d6-8c45-6d099e05553e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f299cbff_95af_4db2_b173_17114a2a44aa
GAIN-706017-2016 | GA-443436-2016 | 11/18/2016 2:39:11 PM | ASSESS: GA: Final | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | Combustion air intake on appliance installed with less than the required clearance to meter regulator relief. If a failure of the meter regulator were to occur while the appliance was in operation,fuel could be drawn into the appliance. Over fire condition could occur. Possible fire and carbon monoxide risk. | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Malone.png | file://x:/photopub/docs/0000000518/989d76ff-64ec-44ad-8e6f-403d03532c23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e92e79a_2c72_47a6_8ff8_35e4d7d49b06
ELIN-681550-2016 | EL-449991-2016 | 10/14/2016 10:21:20 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Improperly supported electrical equipment may break away from the support provided and create a fire and shock hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | unprotected_service_panel.png | file://x:/photopub/docs/0000000501/93077b06-bd14-49c6-930c-1a572348430b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58ddfdb9_d4d6_4f70_a691_4581651797f4
ELIN-681550-2016 | EL-449991-2016 | 10/14/2016 10:21:20 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Improperly supported electrical equipment may break away from the support provided and create a fire and shock hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Outdoor_service_installation_.png | file://x:/photopub/docs/0000000501/21e8943f-96e1-4bfe-afb5-6ab23643eeb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58ddfdb9_d4d6_4f70_a691_4581651797f4
ELIN-681550-2016 | EL-449991-2016 | 10/14/2016 10:21:20 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Improperly supported electrical equipment may break away from the support provided and create a fire and shock hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Unsupported_service_mast.png | file://x:/photopub/docs/0000000501/12d0e134-178a-45bf-bd07-78b19f088cbc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58ddfdb9_d4d6_4f70_a691_4581651797f4
ELIN-681550-2016 | EL-449991-2016 | 10/14/2016 10:21:20 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Improperly supported electrical equipment may break away from the support provided and create a fire and shock hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Type_1_service_panel_exposed_to_weather.png | file://x:/photopub/docs/0000000501/6f32ab14-7468-4820-84ea-542effb365e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58ddfdb9_d4d6_4f70_a691_4581651797f4
BPVOP-703859-2016 | BPV-149757-2014 | 11/15/2016 8:54:00 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP137 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | 4 | 4 | The Maximum allowable working pressure on this air receiver is 150 psi while the safety valve is set for 160psi which is 10 psi over the maximum allowable pressure that this vessel was designed for. If not corrected the pressure vessel could over pressurize and rupture. | 4 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | SV_160psi.png | file://x:/photopub/docs/0000000516/acad51ea-ad76-4622-9022-87a0bf76a565.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__35b3933d_8976_4827_8198_1c578be2cfd8
BPVOP-683259-2016 | 2259447 | 10/13/2016 11:06:44 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on a 30psi hot water heating boiler for the last 14 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_relief_valve_data_tag.png | file://x:/photopub/docs/0000000499/7937d4da-34cf-46e5-a9f5-b49c044d92bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c305a09_18e0_43c9_a6b3_2971fad6d4bf
BPVOP-683259-2016 | 2259447 | 10/13/2016 11:06:44 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on a 30psi hot water heating boiler for the last 14 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Expired_Safety_relief_valves_.png | file://x:/photopub/docs/0000000499/c7c35b7c-09f8-4904-85da-8264bd1065a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c305a09_18e0_43c9_a6b3_2971fad6d4bf
ELIN-673714-2016 | EL-396368-2016 | 9/29/2016 3:05:24 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Unknown conductors in panel, other end of both cables could not be found in the field. Service was not energized at time of inspection | 0 | No Created Hazard Identified | panel.png | file://x:/photopub/docs/0000000492/d501154d-6bd3-4351-acc1-f115720edef1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca7f7d7c_f032_4a95_9359_d7a4f8a3e00e
ELIN-679411-2016 | EL-448589-2016 | 10/25/2016 3:01:05 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL089 | Continuity Bonding; conductor is not properly sized. | 3 | 3 | High voltage installations are required to be grounded and bonded with the proper type and size of ground conductor as well as the proper type of ground electrode. This is required to keep electrical equipment and the ground around the equipment at the same equipotential during a fault condition where equipment may become energized. This installation has a 25KV to 480V, 3 phase transformer bank installed on top of a pole. The ground conductor is a different size, material, and type specified in the code as is the ground electrode. This is a potential shock and fire hazard if there is a fault on the system and the ground fails to keep equipment and the ground at an equipotential or the conductor or connections fail. | 2 | Continuity Bonding; conductor is not properly sized. | Station_ground_conductor_and_electrode.png | file://x:/photopub/docs/0000000505/78587202-e3af-40b0-a33b-c8e914c40e6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e57e1409_da8b_4845_ba46_ea1025edc180
ELIN-679411-2016 | EL-448589-2016 | 10/25/2016 3:01:05 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL089 | Continuity Bonding; conductor is not properly sized. | 3 | 3 | High voltage installations are required to be grounded and bonded with the proper type and size of ground conductor as well as the proper type of ground electrode. This is required to keep electrical equipment and the ground around the equipment at the same equipotential during a fault condition where equipment may become energized. This installation has a 25KV to 480V, 3 phase transformer bank installed on top of a pole. The ground conductor is a different size, material, and type specified in the code as is the ground electrode. This is a potential shock and fire hazard if there is a fault on the system and the ground fails to keep equipment and the ground at an equipotential or the conductor or connections fail. | 2 | Continuity Bonding; conductor is not properly sized. | New_pole_service_.png | file://x:/photopub/docs/0000000505/6f3afde1-d833-4a59-af43-5f06bf21bd8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e57e1409_da8b_4845_ba46_ea1025edc180
ELIN-679411-2016 | EL-448589-2016 | 10/25/2016 3:01:05 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL089 | Continuity Bonding; conductor is not properly sized. | 3 | 3 | High voltage installations are required to be grounded and bonded with the proper type and size of ground conductor as well as the proper type of ground electrode. This is required to keep electrical equipment and the ground around the equipment at the same equipotential during a fault condition where equipment may become energized. This installation has a 25KV to 480V, 3 phase transformer bank installed on top of a pole. The ground conductor is a different size, material, and type specified in the code as is the ground electrode. This is a potential shock and fire hazard if there is a fault on the system and the ground fails to keep equipment and the ground at an equipotential or the conductor or connections fail. | 2 | Continuity Bonding; conductor is not properly sized. | Transformers_.png | file://x:/photopub/docs/0000000505/82eaf523-9550-4180-97d2-31344fa1404e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e57e1409_da8b_4845_ba46_ea1025edc180
EDMA-689276-2016 | ED-291959-2015 | 10/23/2016 2:17:42 PM | ASSESS: ED MA: Partial Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 |  | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Governor2.png | file://x:/photopub/docs/0000000504/c432e39c-e913-46a9-b949-4b805eb0f01f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__221e8503_9259_4fbf_89c3_ff47697c0b55
BPVIN-683420-2016 | BPV-451344-2016 | 10/13/2016 12:51:41 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP137 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | 4 | 4 | The set pressure of a pressure relief device must be set below or match the Maximum Allowed Working Pressure of the vessel. I found the set pressure(200psi) of the pressure relief device was set above the MAWP(150psi) of an air receiver. This may pose an over pressure hazard on the air receiver from pressures exceeding the MAWP of the vessel. | 4 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | Unit_.png | file://x:/photopub/docs/0000000499/e0dc6aa8-025e-49fa-98ba-e15c6e40f357.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84c9c244_8690_47a1_b234_84c11965bbfe
BPVIN-683420-2016 | BPV-451344-2016 | 10/13/2016 12:51:41 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP137 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | 4 | 4 | The set pressure of a pressure relief device must be set below or match the Maximum Allowed Working Pressure of the vessel. I found the set pressure(200psi) of the pressure relief device was set above the MAWP(150psi) of an air receiver. This may pose an over pressure hazard on the air receiver from pressures exceeding the MAWP of the vessel. | 4 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | Pressure_relief_device_.png | file://x:/photopub/docs/0000000499/821454c9-2320-4b7a-b83b-62995a5f6897.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84c9c244_8690_47a1_b234_84c11965bbfe
BPVIN-683420-2016 | BPV-451344-2016 | 10/13/2016 12:51:41 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP137 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | 4 | 4 | The set pressure of a pressure relief device must be set below or match the Maximum Allowed Working Pressure of the vessel. I found the set pressure(200psi) of the pressure relief device was set above the MAWP(150psi) of an air receiver. This may pose an over pressure hazard on the air receiver from pressures exceeding the MAWP of the vessel. | 4 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | name_plate_mawp_.png | file://x:/photopub/docs/0000000499/ab0f67ba-b19e-4cd6-9977-605d7d72925e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84c9c244_8690_47a1_b234_84c11965bbfe
GAIN-701689-2016 | GA-444933-2016 | 11/10/2016 11:28:27 AM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | Boiler installed in a brewery without any combustion or ventilation openings in the space. This may allow a depletion of oxygen in the occupied space possibly leading to incomplete combustion and the production of carbon monoxide. | 4 | Combustion air supply missing | Blocked_air_openings.png | file://x:/photopub/docs/0000000515/8f7fba62-4b2d-4ddf-ac57-20f638d65d83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f10f888_8bee_4ea8_ace6_9a14af28ba39
ELHE-703546-2016 | HE-467243-2016 | 11/14/2016 10:27:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found building bottom floor level (located below earth grade) has exterior concrete walls located behind 800amp 120/208 volt 3 phase rated combination consumer's service and distribution equipment unit. The above equipment appears to have water leaking into the back side of this electrical equipment and appears electrical equipment is wet, rusted and damaged and is not approved for connection or for continued use of the equipment. When electrical electrical equipment becomes damaged or is not approved for the use as installed, the electrical equipment conductors could short circuit to grounded metal and could become a possible electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4.png | file://x:/photopub/docs/0000000519/b0a6a649-b524-4540-8627-2cd23bed4b3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb8a2db4_7383_4e22_a45e_1044cb73dd5a
ELHE-703546-2016 | HE-467243-2016 | 11/14/2016 10:27:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found building bottom floor level (located below earth grade) has exterior concrete walls located behind 800amp 120/208 volt 3 phase rated combination consumer's service and distribution equipment unit. The above equipment appears to have water leaking into the back side of this electrical equipment and appears electrical equipment is wet, rusted and damaged and is not approved for connection or for continued use of the equipment. When electrical electrical equipment becomes damaged or is not approved for the use as installed, the electrical equipment conductors could short circuit to grounded metal and could become a possible electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 5.png | file://x:/photopub/docs/0000000519/8b7faca1-9a11-44e6-9c5f-c3d1922b5ad7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb8a2db4_7383_4e22_a45e_1044cb73dd5a
ELHE-703546-2016 | HE-467243-2016 | 11/14/2016 10:27:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found building bottom floor level (located below earth grade) has exterior concrete walls located behind 800amp 120/208 volt 3 phase rated combination consumer's service and distribution equipment unit. The above equipment appears to have water leaking into the back side of this electrical equipment and appears electrical equipment is wet, rusted and damaged and is not approved for connection or for continued use of the equipment. When electrical electrical equipment becomes damaged or is not approved for the use as installed, the electrical equipment conductors could short circuit to grounded metal and could become a possible electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 3.png | file://x:/photopub/docs/0000000519/d0fe8fe6-f7b1-4494-b0b7-5e5d5008cec9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb8a2db4_7383_4e22_a45e_1044cb73dd5a
ELHE-703546-2016 | HE-467243-2016 | 11/14/2016 10:27:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found building bottom floor level (located below earth grade) has exterior concrete walls located behind 800amp 120/208 volt 3 phase rated combination consumer's service and distribution equipment unit. The above equipment appears to have water leaking into the back side of this electrical equipment and appears electrical equipment is wet, rusted and damaged and is not approved for connection or for continued use of the equipment. When electrical electrical equipment becomes damaged or is not approved for the use as installed, the electrical equipment conductors could short circuit to grounded metal and could become a possible electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 1.png | file://x:/photopub/docs/0000000519/36a8c2dc-5f47-4342-95ae-c90f061439da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb8a2db4_7383_4e22_a45e_1044cb73dd5a
ELHE-703546-2016 | HE-467243-2016 | 11/14/2016 10:27:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found building bottom floor level (located below earth grade) has exterior concrete walls located behind 800amp 120/208 volt 3 phase rated combination consumer's service and distribution equipment unit. The above equipment appears to have water leaking into the back side of this electrical equipment and appears electrical equipment is wet, rusted and damaged and is not approved for connection or for continued use of the equipment. When electrical electrical equipment becomes damaged or is not approved for the use as installed, the electrical equipment conductors could short circuit to grounded metal and could become a possible electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 6.png | file://x:/photopub/docs/0000000519/fcade5aa-82bd-4d29-9fae-15ce00ca9691.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb8a2db4_7383_4e22_a45e_1044cb73dd5a
ELHE-703546-2016 | HE-467243-2016 | 11/14/2016 10:27:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found building bottom floor level (located below earth grade) has exterior concrete walls located behind 800amp 120/208 volt 3 phase rated combination consumer's service and distribution equipment unit. The above equipment appears to have water leaking into the back side of this electrical equipment and appears electrical equipment is wet, rusted and damaged and is not approved for connection or for continued use of the equipment. When electrical electrical equipment becomes damaged or is not approved for the use as installed, the electrical equipment conductors could short circuit to grounded metal and could become a possible electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 2.png | file://x:/photopub/docs/0000000519/648c2eed-9e57-478e-9aab-68c212c97b3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb8a2db4_7383_4e22_a45e_1044cb73dd5a
GAHE-677098-2016 | HE-446677-2016 | 10/3/2016 2:49:34 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | Single wall vent connector installed without required clearance to combustibles were it passes through the wall. Insufficient clearances could result in a fire due to the high temperature in contact with combustible material. | 3 | Non compliant Type C Vent clearance | Vent_clearance_.png | file://x:/photopub/docs/0000000494/2e2a9c32-2198-4134-afe4-47dad57cc8a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03bee344_819c_470e_a191_505361622793
ELIN-703444-2016 | EL-368045-2016 | 11/15/2016 12:25:07 PM | ASSESS: EL: Final | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | Ground conductors are required to be unbroken and protected from mechanical damage were they run from the service equipment to the grounding electrode. This is required to ensure that during a fault condition the ground conductor can carry fault current to ground and keep all electrical equipment and the ground around it at an equipotential to prevent electrical shock hazards during faults. This installation has a grounding conductor that has several strands that are damaged and broken. Left uncorrected this is a potential shock and fire hazard. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Damaged_ground_conductor.png | file://x:/photopub/docs/0000000516/28642544-4917-44b6-81eb-b6073aa9d126.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec5dc386_a285_463d_a5e1_ddca47302051
GAHE-714003-2016 | HE-474200-2016 | 11/29/2016 12:40:36 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | The as found condition is an appliance with positively pressurized exhaust and a closely placed combustion air intake are placed within 3"of a deck beam with side panelling. The as found hazard is the positive pressurization of the combustion gases with the structural obstacles placed in front creates an environment conducive to the exhaust to be drawn into the appliance through the fresh air intake. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_obstruction.png | file://x:/photopub/docs/0000000523/779b1c3b-ffb8-42d7-a265-285fff91859d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d22a2aca_5ba7_4852_a6dc_9d33faabefe8
ELIN-703145-2016 | EL-413680-2016 | 11/15/2016 1:11:29 PM | ASSESS: EL: Final | png | #asFound | EL039 | Equipment is not marked / identified Multiple service boxes not marked. | 2 | 2 | Panel not labeled. Possibility for shock if circuit bing worked on. | 2 | Equipment is not marked / identified Multiple service boxes not marked. | Main_and_sub_panel.png | file://x:/photopub/docs/0000000516/5969a737-7290-40d3-9f36-91ce199e09a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f838d05_bf54_4e2e_b0cc_110cd0b01d28
BPOP-670561-2016 | BPV-405008-2015 | 10/3/2016 4:48:26 PM | ASSESS: Propane PV: Periodic | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | No rain cap on relief valve. Could allow foreign material to plug relief valve ,preventing valve from functioning as it is designed to do. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 248_cement_street_Princeton.png | file://x:/photopub/docs/0000000494/5764c4da-e2c1-48c2-bd59-dc2bc1158406.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6567a71d_d8fa_4966_968b_2d720e36d5fc
BPOP-670561-2016 | BPV-405008-2015 | 10/3/2016 4:48:26 PM | ASSESS: Propane PV: Periodic | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | No rain cap on relief valve. Could allow foreign material to plug relief valve ,preventing valve from functioning as it is designed to do. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 248_cement_St__.png | file://x:/photopub/docs/0000000494/f4307a45-d558-442d-9303-31df611ac4aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6567a71d_d8fa_4966_968b_2d720e36d5fc
ELIN-706322-2016 | EL-413969-2016 | 11/22/2016 10:22:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Service conduit is not adequately bonded to ground. Service wires are only protected by the upstream utility over current protection and therefore have high fault current potential. This creates a higher potential for a fire under a fault condition. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Panel_service_conduit.png | file://x:/photopub/docs/0000000520/3d6cf9f5-e079-4ffb-99ad-6ad31edcb0e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34fdfcad_c0bd_49a6_bb6e_757fde797ec3
BPVOP-671750-2016 | 2269464 | 9/26/2016 8:17:26 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Upon assessment of low pressure steam heating boiler with 40square meters heating surface it is determined that capacity of safety valve is less than theoretical minimum capacity required. In the event of over-pressure built up in the boiler (due to failure of control and other safety devices) there is possibility of permanent damage or even rupture of pressure boundary of boiler which can lead to incident. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_Valve.png | file://x:/photopub/docs/0000000491/51d01f03-14d6-449c-b43c-f122f22b343b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b991a1b1_86b3_4c7b_811c_c7cbbf9b958b
GAHE-664416-2016 | HE-438165-2016 | 9/26/2016 7:57:36 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA017 | Tank saddles/support failing | 4 | 4 | Propane tank installed on the dirt, no supports, tank ready to fall over and connected to site office | 4 | Tank saddles/support failing | Office.png | file://x:/photopub/docs/0000000491/e459a700-c7e8-42be-b978-b94c71997da7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aceb0e71_d53d_4268_a352_0963bc5dc024
ELIN-703145-2016 | EL-413680-2016 | 11/15/2016 1:11:29 PM | ASSESS: EL: Final | png | #asFound | EL039 | Equipment is not marked / identified Multiple service boxes not marked. | 2 | 2 | Panel not labeled. Possibility for shock if circuit bing worked on. | 2 | Equipment is not marked / identified Multiple service boxes not marked. | Dryer_circuit.png | file://x:/photopub/docs/0000000516/3a13515e-b53c-4ed0-9ef5-42fe81f80fa3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f838d05_bf54_4e2e_b0cc_110cd0b01d28
GAUP-703547-2016 | UW-467360-2016 | 11/10/2016 5:34:41 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | No second stage pressure control regulator installed on a propane piping system.10 PSI regulator installed at tank only, 10 PSIG gas delivery t the furnace valve which is only rated for a maximum of 1/2 psig only. This condition can over pressure the gas valve creating an over fired condition of the appliance or valve to leak gas. | 4 | Missing mandatory safety controls | Pet1.png | file://x:/photopub/docs/0000000515/68e60c0f-b9ab-4329-883d-bc51868cd3de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7c76a26_2620_42f5_ada4_36850b9f1744
GAUP-703547-2016 | UW-467360-2016 | 11/10/2016 5:34:41 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | No second stage pressure control regulator installed on a propane piping system.10 PSI regulator installed at tank only, 10 PSIG gas delivery t the furnace valve which is only rated for a maximum of 1/2 psig only. This condition can over pressure the gas valve creating an over fired condition of the appliance or valve to leak gas. | 4 | Missing mandatory safety controls | Pet2.png | file://x:/photopub/docs/0000000515/0f8f6993-3eb8-4809-9ff0-823aac284de7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7c76a26_2620_42f5_ada4_36850b9f1744
GAIN-636200-2016 | GA-235714-2015 | 10/18/2016 1:26:55 PM | ASSESS: GA: Final | png | #asFound | GA070 | Undersized hose or appliance connector | 3 | 3 | Gas connector used for appliance is undersized. An undersized portion of the piping system will not provide the right amount of gas for complete combustion. Burner will be creating too much CO and possibly damaging the heat exchanger. | 3 | Undersized hose or appliance connector | UndersizedGasConnector.png | file://x:/photopub/docs/0000000502/b886c81c-30d3-4439-bc60-ea6624119eef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__621eab7d_67c7_462c_a411_8c9514df3940
ELIN-700820-2016 | EL-437677-2016 | 11/10/2016 9:29:36 AM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | FSR working in energized electrical equipment. High available fault current estimated by Class A FSR to be 10k. High risk of arc fault exposure, shock and burn. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_equipment.png | file://x:/photopub/docs/0000000514/4759c7cf-12a0-431b-b7fc-33e942cd1c6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f928093_83ef_42d7_9dbe_52d16c7242d0
EDOP-710274-2016 | 2050100 | 11/23/2016 3:09:08 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED046 | Defects found where the required strength may no longer exist. | 4 | 4 | During periodic inspection it was found that the cables for lifting and lowering the elevator were roughing which is oxidation, and were under the actual diameter specified. | 4 | Defects found where the required strength may no longer exist. | 001_ropes.png | file://x:/photopub/docs/0000000520/ae4edd88-f636-4de6-9081-ce135f3ddcc9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29525b7c_24fe_4568_8521_c2246a4642cf
EDOP-692691-2016 | ED -0000128774-2014 | 10/27/2016 3:42:44 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | A collapsable gate has been installed across front of top landing. This has a potential of trapping someone in this space if elevator door closes and elevator leaves floor. Also, controller for this unit is in door jamb and there is no access for service technician in event of entrapment in elevator. Emergency personel will not have access to this floor in event of fire or other such emergency. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Pics__28313.png | file://x:/photopub/docs/0000000506/9aa83070-f9e2-4d6a-8935-3e338d69cef4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d95e019_fcff_4533_831c_377549dfc623
PRIN-706748-2016 | PR-425653-2016 | 11/25/2016 8:43:32 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR010 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 1 | 1 |  | 1 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Silverstar_tube_lift.png | file://x:/photopub/docs/0000000522/bd1bd2b6-f33e-43c0-8770-edf0485c61a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eca12344_7d68_45cb_9d86_c7bbc03194ed
ELIN-670815-2016 | EL-410406-2016 | 9/27/2016 10:52:03 AM | ASSESS: EL: Service Connection | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | In a new commercial warehouse, a 600amp 120/208volt 3phase service was found with the main switch bonding not installed. This could lead to a shock hazard. Pic attached. | 3 | Continuity Bonding conductor is not observed or broken | No_bond_present.png | file://x:/photopub/docs/0000000492/2c5a2007-552d-47ab-95ec-ea81c36bd9a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef795d19_26c7_4f84_966a_e52391577d53
ELIN-689591-2016 | EL-292149-2015 | 10/28/2016 2:10:20 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Panel cover missing leaving live exposed parts accessible. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Image_1.png | file://x:/photopub/docs/0000000507/a2cc8d7c-0d55-41ac-93eb-aa314734f2a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dffcc527_b402_408a_b723_8532362a4fea
ELIN-708238-2016 | EL-459174-2016 | 11/22/2016 2:35:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | Bonding bushing and bonding conductor is not installed on the rigid conduit from the metre base to panel board. There is a possibility that the locknut may become loose there by allowing electrical Current to arc between the metal enclosure and locknut and case a fire. | 3 | Continuity Bonding conductor is not observed or broken | No_bonding__no_bonding_bushing_installed.png | file://x:/photopub/docs/0000000519/f8729388-9804-476d-b9d3-6b51cfcad833.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e129b859_5257_48cc_bf06_f8bb506c500f
ELIN-708238-2016 | EL-459174-2016 | 11/22/2016 2:35:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | Bonding bushing and bonding conductor is not installed on the rigid conduit from the metre base to panel board. There is a possibility that the locknut may become loose there by allowing electrical Current to arc between the metal enclosure and locknut and case a fire. | 3 | Continuity Bonding conductor is not observed or broken | Grounding_conductor__grounding_conductor_terminated_at_the_incorrect_location.png | file://x:/photopub/docs/0000000519/b7683a73-eca7-4aae-937f-c93652f2d5c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e129b859_5257_48cc_bf06_f8bb506c500f
ELIN-679862-2016 | EL-398178-2016 | 10/11/2016 12:43:33 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | The 15 amp receptacles supplied for the microwave, soffit outlet, garburator and fan circulation unit have not been protected by an AFCI type branch breaker, this could pose a fire hazard to the circuit or equipment plugged into this receptacles due to the common failure of extension cords. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Branch_Breakers.png | file://x:/photopub/docs/0000000498/a0c270dd-31db-40a4-a1e7-e7e54310ed0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f9710a1_9f60_422f_93cf_73176afbf358
ELIN-712370-2016 | EL-443140-2016 | 11/29/2016 12:56:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Main Grounding conductor not terminated properly to neutral buss in meter base service box. Without proper connection to ground over current protection devices ( breakers ) could possibly not work as designed. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Bond.png | file://x:/photopub/docs/0000000523/f63095f4-aafc-4daf-bc03-5568feb13a90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d270b811_c7d8_49b0_b37b_ecdb648c9345
ELIN-712370-2016 | EL-443140-2016 | 11/29/2016 12:56:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Main Grounding conductor not terminated properly to neutral buss in meter base service box. Without proper connection to ground over current protection devices ( breakers ) could possibly not work as designed. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Bond2.png | file://x:/photopub/docs/0000000523/1440bbe0-274d-4d44-a60a-90d96088c83f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d270b811_c7d8_49b0_b37b_ecdb648c9345
GAHE-669710-2016 | HE-441720-2016 | 10/4/2016 9:15:41 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA024 | No protection Low traffic | 3 | 3 | 500 gallon propane tank and dispencer not protected from vehicle traffic. | 3 | No protection Low traffic | Protection_barriers.png | file://x:/photopub/docs/0000000495/76d3c572-af46-49e6-b850-f66a759c9d0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f03f358_b395_4e5f_960f_91b5d0d0b44e
GAHE-669710-2016 | HE-441720-2016 | 10/4/2016 9:15:41 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA024 | No protection Low traffic | 3 | 3 | 500 gallon propane tank and dispencer not protected from vehicle traffic. | 3 | No protection Low traffic | Combustible_building_tank_location.png | file://x:/photopub/docs/0000000495/e6d032d5-961c-4de9-810f-d52bc34407ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f03f358_b395_4e5f_960f_91b5d0d0b44e
GAHE-669710-2016 | HE-441720-2016 | 10/4/2016 9:15:41 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA024 | No protection Low traffic | 3 | 3 | 500 gallon propane tank and dispencer not protected from vehicle traffic. | 3 | No protection Low traffic | Electrical_were_used_to_hold_door_open.png | file://x:/photopub/docs/0000000495/9452f397-5edf-4df9-bed7-71a8071ef308.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f03f358_b395_4e5f_960f_91b5d0d0b44e
GAHE-669710-2016 | HE-441720-2016 | 10/4/2016 9:15:41 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA024 | No protection Low traffic | 3 | 3 | 500 gallon propane tank and dispencer not protected from vehicle traffic. | 3 | No protection Low traffic | Decal_and_tank_condition.png | file://x:/photopub/docs/0000000495/d2f21743-5310-4111-b42a-8a574423dea2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f03f358_b395_4e5f_960f_91b5d0d0b44e
GAHE-669710-2016 | HE-441720-2016 | 10/4/2016 9:15:41 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA024 | No protection Low traffic | 3 | 3 | 500 gallon propane tank and dispencer not protected from vehicle traffic. | 3 | No protection Low traffic | Electrical.png | file://x:/photopub/docs/0000000495/b0762dc5-a05a-488d-bc99-6a1ff48a64f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f03f358_b395_4e5f_960f_91b5d0d0b44e
GAHE-669710-2016 | HE-441720-2016 | 10/4/2016 9:15:41 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA024 | No protection Low traffic | 3 | 3 | 500 gallon propane tank and dispencer not protected from vehicle traffic. | 3 | No protection Low traffic | Exposed_piping.png | file://x:/photopub/docs/0000000495/626a01d1-5d67-4cdd-b3a2-7b333c120440.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f03f358_b395_4e5f_960f_91b5d0d0b44e
GAHE-669710-2016 | HE-441720-2016 | 10/4/2016 9:15:41 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA024 | No protection Low traffic | 3 | 3 | 500 gallon propane tank and dispencer not protected from vehicle traffic. | 3 | No protection Low traffic | Paint_condition.png | file://x:/photopub/docs/0000000495/fd3c2b6a-912c-4be0-87ca-3695693d5f30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f03f358_b395_4e5f_960f_91b5d0d0b44e
ELHE-699130-2016 | HE-464349-2016 | 11/7/2016 11:39:11 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Panel covers are missing. Exposure to elect if shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Panel_covers_missing.png | file://x:/photopub/docs/0000000512/6b55aa83-aea6-4534-9916-95877ff481c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2079dd90_a047_4e0a_b607_bba16d7724d7
ELHE-699130-2016 | HE-464349-2016 | 11/7/2016 11:39:11 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Panel covers are missing. Exposure to elect if shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Regular_receptacles_outside.png | file://x:/photopub/docs/0000000512/307569c8-55a2-41f7-ba83-c365caaba362.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2079dd90_a047_4e0a_b607_bba16d7724d7
ELHE-699130-2016 | HE-464349-2016 | 11/7/2016 11:39:11 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Panel covers are missing. Exposure to elect if shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | NMD90_outside.png | file://x:/photopub/docs/0000000512/40ba48d3-1254-4911-9bdd-dce273767862.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2079dd90_a047_4e0a_b607_bba16d7724d7
PROP-683569-2016 | 4966222 | 10/21/2016 11:46:33 AM | ASSESS: PR OP: Annual | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | Heater had no identifiable approval markings, heater may be wrong for its environment. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Seymour_bear_pit_heater_csa.png | file://x:/photopub/docs/0000000503/67ef31db-49dc-4b9d-ba3a-d71318cd66c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1cc912a2_bc9d_4fad_8aad_73151310c3e8
PROP-683567-2016 | 2224029 | 10/21/2016 12:42:17 PM | ASSESS: PR OP: Annual | png | #asFound | PR019 | Defect that impairs performance: Performance remains within limits Non-degenerative or very slow Reasonably detectable by the maintenance or operation program | 2 | 2 | Service brake in contact with brake drum while running evacuation drive, could compromise brake pads and/or disc. | 2 | Defect that impairs performance: Performance remains within limits Non-degenerative or very slow Reasonably detectable by the maintenance or operation program | Seymour_lodge_service_brake.png | file://x:/photopub/docs/0000000503/4b434345-0e60-450c-a5ff-2ac801d6b640.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d1bf538_5806_44fc_894d_c85e5eb57219
PROP-683761-2016 | 2224141 | 10/21/2016 1:43:57 PM | ASSESS: PR OP: Annual | png | #asFound | PR025 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | Return terminal decks are wearing, could result in trips or falls. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Midway_return_deck.png | file://x:/photopub/docs/0000000503/2a2bd1ac-dca8-4cdb-9dc1-8563c4a398fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbb2c1ce_e8e4_468f_b8dd_d0ddacc0b617
PROP-683761-2016 | 2224141 | 10/21/2016 1:43:57 PM | ASSESS: PR OP: Annual | png | #asFound | PR025 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | Return terminal decks are wearing, could result in trips or falls. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Midway_return_decks.png | file://x:/photopub/docs/0000000503/5181d8a0-7730-4779-a32a-95e8cae0d0ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbb2c1ce_e8e4_468f_b8dd_d0ddacc0b617
ELIN-694405-2016 | EL-437691-2016 | 11/4/2016 11:14:36 AM | ASSESS: EL: Final | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Open mast allows water to go directly into meter base. This will cause tracking of voltage creating a shock hazard, and corrosion on the equipment creating a thermal hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Entrance_head.png | file://x:/photopub/docs/0000000511/c6fc3598-bd4d-490c-a74b-9a462bd4abab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__122c8e29_6704_4ca6_b1da_6b34ae5e0808
ELIN-694405-2016 | EL-437691-2016 | 11/4/2016 11:14:36 AM | ASSESS: EL: Final | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Open mast allows water to go directly into meter base. This will cause tracking of voltage creating a shock hazard, and corrosion on the equipment creating a thermal hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Cap.png | file://x:/photopub/docs/0000000511/21ddcddc-5db5-490a-bd0e-1e1e8d30de29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__122c8e29_6704_4ca6_b1da_6b34ae5e0808
ELIN-693071-2016 | EL-452679-2016 | 11/3/2016 8:33:07 AM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The integrity of the wood has deteriorated and will result in the collapse of the service support. This condition could result in a shock and fire hazard when the incident occurs. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Untreated_wood.png | file://x:/photopub/docs/0000000511/d3b80c0c-d93b-4277-9eb7-57b3c6bfacba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__adf9c095_2630_49b4_951f_b67182bf9c6d
ELIN-694405-2016 | EL-437691-2016 | 11/4/2016 11:14:36 AM | ASSESS: EL: Final | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Open mast allows water to go directly into meter base. This will cause tracking of voltage creating a shock hazard, and corrosion on the equipment creating a thermal hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | General_purpose_switch.png | file://x:/photopub/docs/0000000511/ecb4e941-3532-4206-9a51-5395bfcbcf08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__122c8e29_6704_4ca6_b1da_6b34ae5e0808
ELIN-693071-2016 | EL-452679-2016 | 11/3/2016 8:33:07 AM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The integrity of the wood has deteriorated and will result in the collapse of the service support. This condition could result in a shock and fire hazard when the incident occurs. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Deteriorated_support.png | file://x:/photopub/docs/0000000511/20019437-f6df-4608-9e9f-42da9ea80513.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__adf9c095_2630_49b4_951f_b67182bf9c6d
ELIN-713483-2016 | EL-308059-2015 | 11/29/2016 1:32:35 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Gas line not bonded - shock hazard during fault. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Glen_oaks5.png | file://x:/photopub/docs/0000000523/2ffda4e6-3cb9-4203-aa6b-cb1d94fcaabd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9789d3e8_c257_45d7_b58b_1bb7fbaaa914
ELIN-713483-2016 | EL-308059-2015 | 11/29/2016 1:32:35 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Gas line not bonded - shock hazard during fault. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Glen_oaks1.png | file://x:/photopub/docs/0000000523/e916371f-981f-4997-bd4b-85c7a8602f4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9789d3e8_c257_45d7_b58b_1bb7fbaaa914
ELIN-713483-2016 | EL-308059-2015 | 11/29/2016 1:32:35 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Gas line not bonded - shock hazard during fault. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Glen_oaks_2.png | file://x:/photopub/docs/0000000523/8b547e1d-9fd1-49a0-941a-64e42077ca78.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9789d3e8_c257_45d7_b58b_1bb7fbaaa914
ELIN-713483-2016 | EL-308059-2015 | 11/29/2016 1:32:35 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Gas line not bonded - shock hazard during fault. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Glen_oaks4.png | file://x:/photopub/docs/0000000523/765f7c2c-b807-4034-81f8-9ba575475e10.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9789d3e8_c257_45d7_b58b_1bb7fbaaa914
ELIN-713483-2016 | EL-308059-2015 | 11/29/2016 1:32:35 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Gas line not bonded - shock hazard during fault. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Glen_oaks3.png | file://x:/photopub/docs/0000000523/7dd30b8c-533c-4fa9-9ff4-f9ae18e181d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9789d3e8_c257_45d7_b58b_1bb7fbaaa914
BPVOP-703954-2016 | 2299761 | 11/30/2016 1:19:24 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided for a hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_.png | file://x:/photopub/docs/0000000523/c0749c40-00e0-4492-8cf4-9642d32f10e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__771d28ff_2239_4c81_a746_8307547ce573
BPVOP-703953-2016 | 2284509 | 11/30/2016 1:32:58 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided for hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | boiler_2.png | file://x:/photopub/docs/0000000523/2e078458-76f6-4bf0-ba49-c1c952e2aa3d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72334838_20ac_4ba4_8441_35790c12d9d4
BPVOP-703955-2016 | 2284508 | 11/30/2016 1:27:29 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided for hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | boiler_.png | file://x:/photopub/docs/0000000523/c7ade286-e0e0-4544-a07c-1be4b37b0af1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__36adac28_2bbb_4a0d_b5c5_9f0b4f0c27ad
BPVOP-703955-2016 | 2284508 | 11/30/2016 1:27:29 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided for hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | flow_switch_on_the_inlet.png | file://x:/photopub/docs/0000000523/5239a467-107f-4a73-adbc-dda3f71d83c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__36adac28_2bbb_4a0d_b5c5_9f0b4f0c27ad
BPVOP-703943-2016 | 2250773 | 11/30/2016 1:57:12 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP202 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | 2 | 2 |  | 2 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | refractory.png | file://x:/photopub/docs/0000000523/62c276c6-6d8f-4366-9e42-134fa149538a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0538eb1f_66d4_4039_8d36_39b2e8b2ba35
BPVOP-703953-2016 | 2284509 | 11/30/2016 1:32:58 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided for hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | flow_sensor_on_inlet.png | file://x:/photopub/docs/0000000523/18fa1abc-d1a8-4705-80a3-43378893b66a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72334838_20ac_4ba4_8441_35790c12d9d4
ELIN-676825-2016 | UW-446406-2016 | 10/3/2016 11:16:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Wires_hanging.png | file://x:/photopub/docs/0000000494/ee25448d-650b-494d-bfb8-5427b861c508.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1efdff80_62f5_4fec_ba2a_759acacc81d1
ELIN-676825-2016 | UW-446406-2016 | 10/3/2016 11:16:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Fixtures_removed.png | file://x:/photopub/docs/0000000494/e48affba-e6c6-4290-82b6-02a9aeeb44d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1efdff80_62f5_4fec_ba2a_759acacc81d1
ELIN-691117-2016 | EL-456177-2016 | 10/26/2016 11:48:42 AM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | Construction receptacles are not provided with weather proof covers nor GFCI protection. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 4642_sheridan_1.png | file://x:/photopub/docs/0000000505/c9f9d036-4720-4e7b-8725-90c70b64e430.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97fc83d3_d958_44d4_9137_52cbfcf576a0
ELIN-691117-2016 | EL-456177-2016 | 10/26/2016 11:48:42 AM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | Construction receptacles are not provided with weather proof covers nor GFCI protection. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 4642_sheridan_2.png | file://x:/photopub/docs/0000000505/c1186d24-fe49-4462-91f3-4447ee114dd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97fc83d3_d958_44d4_9137_52cbfcf576a0
ELIN-712904-2016 | EL-472770-2016 | 11/30/2016 11:47:52 AM | ASSESS: EL: Service Connection | png | #asFound | EL254 | Category 2 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | 200 amp jumbo meterbase has signs of damage and wear due to being used/recycled. This could be a potential shock/fire hazard if the internal parts of the meterbase were to fail due to the over fusing of the service conductors by the supply service. | 4 | Category 2 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Damaged_meterbase.png | file://x:/photopub/docs/0000000523/fcbf5463-d3dd-42fa-8dc6-7b93985403d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d491d262_2024_407e_ab7f_d4c47debf841
GAIN-713292-2016 | GA-431618-2016 | 12/1/2016 1:38:03 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Found Hayward pool heater installed underneath wooden balcony. Manufacturer states a minimum clearance of 36 inches from top of heater to combustibles etc. Unit was installed with only 10 inches. This is a potential fire hazard as the combustible materials could overheat and catch fire. | 3 | Clearance to combustible not met | Poolheater_clearancesnotmet.png | file://x:/photopub/docs/0000000524/d1094769-7bea-49f6-b35d-e87753867d75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3dd2bab8_5c36_4d08_8955_9f9313d01097
ELOP-690457-2016 | 5140621 | 10/25/2016 11:10:38 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | Reinspection of noncompliance on expired private high-voltage line. Overhead line is not being maintained and the load brake switch is being overgrown by vegetation. Therefore, there is no access to disconnect this system in an emergency or for routine maintenance. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Load_break_switch_covered.png | file://x:/photopub/docs/0000000505/ff63e8f2-1cc3-43e4-863d-d2d802ea26ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__959c31a0_4087_4207_baad_08fbed22b48d
ELIN-714734-2016 | UW-474616-2016 | 11/30/2016 12:17:33 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | Improper grounding of high voltage load break switch. Proper grounding is required to limit step and touch potential. This is a shock and fire hazard. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | B.png | file://x:/photopub/docs/0000000523/ad0d77ef-7438-4684-94bc-72403572af63.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__09b09e9e_8fd2_428c_9dde_91a7006581d7
ELIN-712225-2016 | EL-447319-2016 | 11/30/2016 11:02:52 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | Cables run over top of the upper faces of rafters. This is a fire and a shock hazard an individual could step on these cables and damage them. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | A.png | file://x:/photopub/docs/0000000523/832f9bdf-31a9-47fb-a00a-d9b834cd3b44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0384723d_8856_4d1c_8523_c154b11a565d
ELOP-707851-2016 | 4913810 | 11/30/2016 1:51:18 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Holes in panels covered with duct tape. This is a shock hazard as duct taped is not an approved panel filler. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | V.png | file://x:/photopub/docs/0000000523/5938e755-1c15-444a-a6f1-047577e3dba1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0da969c1_1bf8_4bdb_a32f_e79b66fbcd21
BPVOP-714474-2016 | 3392605 | 11/25/2016 10:37:36 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment it is determined that pressure vessel-domestic hot water storage tank (1.80m long and .60m diameter pressure vessel)- with Maximum Allowable Working Pressure (MAWP) of 150psig, has safety relief valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety relief valve serviced or replaced as required may subject vessel to pressure above MAWP if system control fails. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of hot water and can lead to incident (scalding if personnel and/or damage to equipment). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_device.png | file://x:/photopub/docs/0000000523/3f17d9f0-41ec-4aab-ba7c-8f3ab1c589e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__477583e9_4bb9_40ed_a684_f3d9adf19c95
BPVOP-714471-2016 | 2266786 | 11/25/2016 10:06:51 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Hot Water Boiler with Heating Surface (HS) of 13 square meters, Maximum Allowable Working Pressure (MAWP) of 115psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_room_entrance.png | file://x:/photopub/docs/0000000523/92b9cd45-b74e-4902-8ff3-d2d43ab9c21b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26f31c56_e877_49bc_b859_f2cc1186c9fc
BPVOP-689930-2016 | 2289893 | 10/24/2016 12:28:52 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP135 | 3.1.1 Safeties will not function - Pressure Relief Device non functioning | 4 | 4 | Upon assessment of hot water boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that safety relief valve discharge is plugged. In the event of failure of control to stop boiler while running, boiler will be subjected to pressure above Maximum Allowable Working Pressure (MAWP). This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 4 | 3.1.1 Safeties will not function - Pressure Relief Device non functioning | SAFETY_RELIEF_VALVE_WITH_DISCHARGE_PLUGGED.png | file://x:/photopub/docs/0000000505/9a547a3f-3879-4478-8071-08d2db112055.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f1f019c_acc0_4778_ba96_c58b16752b15
BPVOP-714475-2016 | 2266679 | 11/25/2016 8:15:16 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP163 | 5.0.1 Operator non-compliance - Safety orders not followed or adhered to | 3 | 3 | Upon assessment it is determined that machine mounted horizontal air receiver (1.5m long and .50m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 5.0.1 Operator non-compliance - Safety orders not followed or adhered to | PRESSURE_RELIEF_DEVICE.png | file://x:/photopub/docs/0000000523/4c1dcda1-d3be-41ce-b25a-658013b281ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__000a8b0d_0d17_4d5b_83c9_c775213ce8d6
PROP-598662-2016 | 3614991 | 11/3/2016 9:21:23 PM | ASSESS: PR OP: RAP | png | #asFound | PR031 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | 1 | 1 | Missing fire extinguisher and non functioning smoke detectors. | 1 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | Missing_fire_extingusher.png | file://x:/photopub/docs/0000000511/2265fc01-71e5-44a0-b717-7895c124ca24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__BD4ABD52_D1E1_40E7_B598_B19D1A86B41A
ELIN-667410-2016 | EL-227870-2015 | 9/21/2016 2:17:44 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Splitter missing cover. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | C.png | file://x:/photopub/docs/0000000488/7e2f856b-173f-4eae-b7cb-9c44ad749f48.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a6ef149_8d17_44b5_acb6_8fa94e949fd3
GAHE-666616-2016 | HE-439692-2016 | 9/14/2016 1:36:59 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | [7 empty] | Red_tag_.png | file://x:/photopub/docs/0000000489/2f530b2c-88d2-40f9-b015-9c3f2ce5e79e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d0aebfd_588a_41db_9238_cf0ae950eeee
GAHE-666616-2016 | HE-439692-2016 | 9/14/2016 1:36:59 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | [7 empty] | Boiler.png | file://x:/photopub/docs/0000000489/c6b12e8e-26a6-4bf8-882a-46bc5b24a5d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d0aebfd_588a_41db_9238_cf0ae950eeee
GAHE-698363-2016 | HE-463769-2016 | 11/4/2016 7:00:05 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Propane tanks is less than the required 10 foot clearance to a combustible wall. | 3 | Clearance to combustibles not maintained | 4317_Meadow_Creek.png | file://x:/photopub/docs/0000000511/c1c0e9c1-78aa-4ae8-87db-992977f49866.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82f5b560_d807_4035_995f_358c3df204fb
ELOP-707854-2016 | 4164413 | 11/28/2016 2:58:57 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Non metallic sheathed cable installed outdoors. This is a shock hazard as this type of cable is not rated for outdoors and will break down in the sunlight and waters. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | F.png | file://x:/photopub/docs/0000000522/1d849bb5-92be-4624-80ec-09355571cb5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__292851da_97ea_4caf_a6d4_c2b9f48b4d5a
ELOP-707854-2016 | 4164413 | 11/28/2016 2:58:57 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Non metallic sheathed cable installed outdoors. This is a shock hazard as this type of cable is not rated for outdoors and will break down in the sunlight and waters. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | A.png | file://x:/photopub/docs/0000000522/b0e16526-324c-477a-af01-518e72d136e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__292851da_97ea_4caf_a6d4_c2b9f48b4d5a
ELOP-707854-2016 | 4164413 | 11/28/2016 2:58:57 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Non metallic sheathed cable installed outdoors. This is a shock hazard as this type of cable is not rated for outdoors and will break down in the sunlight and waters. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | B.png | file://x:/photopub/docs/0000000522/71649770-38ca-4883-8d5d-c5acfbdf992c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__292851da_97ea_4caf_a6d4_c2b9f48b4d5a
ELOP-707854-2016 | 4164413 | 11/28/2016 2:58:57 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Non metallic sheathed cable installed outdoors. This is a shock hazard as this type of cable is not rated for outdoors and will break down in the sunlight and waters. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | C.png | file://x:/photopub/docs/0000000522/e232a0ec-955d-4697-b5ac-446a6b97b0bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__292851da_97ea_4caf_a6d4_c2b9f48b4d5a
ELOP-707854-2016 | 4164413 | 11/28/2016 2:58:57 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Non metallic sheathed cable installed outdoors. This is a shock hazard as this type of cable is not rated for outdoors and will break down in the sunlight and waters. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | D.png | file://x:/photopub/docs/0000000522/88920fde-34d8-4ef5-8bb0-f5653f5d5193.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__292851da_97ea_4caf_a6d4_c2b9f48b4d5a
ELOP-707854-2016 | 4164413 | 11/28/2016 2:58:57 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Non metallic sheathed cable installed outdoors. This is a shock hazard as this type of cable is not rated for outdoors and will break down in the sunlight and waters. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | E.png | file://x:/photopub/docs/0000000522/332a4615-3ee6-432e-813f-d13b27a4049d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__292851da_97ea_4caf_a6d4_c2b9f48b4d5a
ELOP-707854-2016 | 4164413 | 11/28/2016 2:58:57 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Non metallic sheathed cable installed outdoors. This is a shock hazard as this type of cable is not rated for outdoors and will break down in the sunlight and waters. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | G.png | file://x:/photopub/docs/0000000522/36f4552f-d311-461e-a726-4ee09183c520.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__292851da_97ea_4caf_a6d4_c2b9f48b4d5a
ELIN-687817-2016 | EL-445464-2016 | 11/3/2016 9:38:39 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Possible cable damage due to improper installation. | 3 | General Equipment is not approved for the specific use | Image_4.png | file://x:/photopub/docs/0000000511/a9bd3ab7-b4d8-4871-9c9d-68f7a4ee3294.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5c24102_dbb4_4ed4_b1f3_c04daae8de75
ELIN-687817-2016 | EL-445464-2016 | 11/3/2016 9:38:39 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Possible cable damage due to improper installation. | 3 | General Equipment is not approved for the specific use | Image_3.png | file://x:/photopub/docs/0000000511/386ea46e-1ed7-4ab9-922c-01a9403950b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5c24102_dbb4_4ed4_b1f3_c04daae8de75
ELIN-687817-2016 | EL-445464-2016 | 11/3/2016 9:38:39 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Possible cable damage due to improper installation. | 3 | General Equipment is not approved for the specific use | Image_2.png | file://x:/photopub/docs/0000000511/901ce8f4-4477-423b-8517-ce27f4712985.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5c24102_dbb4_4ed4_b1f3_c04daae8de75
ELIN-687817-2016 | EL-445464-2016 | 11/3/2016 9:38:39 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Possible cable damage due to improper installation. | 3 | General Equipment is not approved for the specific use | Image_5.png | file://x:/photopub/docs/0000000511/506c28bf-3bc7-4f25-9f53-e4aa70c36561.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5c24102_dbb4_4ed4_b1f3_c04daae8de75
ELIN-687817-2016 | EL-445464-2016 | 11/3/2016 9:38:39 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Possible cable damage due to improper installation. | 3 | General Equipment is not approved for the specific use | Image_1.png | file://x:/photopub/docs/0000000511/85d0f778-26e9-4ce2-bd78-f00515a2008b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5c24102_dbb4_4ed4_b1f3_c04daae8de75
ELOP-696447-2016 | 4299646 | 11/3/2016 12:13:11 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Electrical operating permit assessment on berry plant. Electrical equipment for processing berries in plant does not bear acceptable evidence of approval. An assessment in response to woman injured on the equipment. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Unstrapped_cable_on_unapproved_equipment.png | file://x:/photopub/docs/0000000511/4b2b56d3-82f9-4199-a8da-097bf7975369.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb359952_343f_476e_93c3_ba6d1f98ac1d
ELIN-665203-2016 | EL-436964-2016 | 9/20/2016 10:54:13 AM | ASSESS: EL: Final | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | A surface mounted outlet box which is not securely fastened to the wall also has an incorrect cover plate installed. The combination of the loose box and wrong cover result in a possible shock hazard for anyone trying to insert or remove a plug at this outlet. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Inadequately_supported_surface_mount_box_.png | file://x:/photopub/docs/0000000487/236518fd-f8a7-442b-9dd8-4161cdbe378e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b047005_0c9b_4078_92b7_ff8014cf77bb
BPVOP-698170-2016 | 4198146 | 11/4/2016 3:48:47 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of pressure vessel (condenser in refrigeration system, Length:3.1m, Diameter:0.60m) with Maximum Allowable Working Pressure (MAWP) of 300psig, it is determined that pressure relief valves have exceeded the required 5year interval for servicing/replacement. Failure to have pressure relief valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down system. This could result in failure of pressure-boundary with release of refrigerant and may cause a severe incident (asphyxiation of personnel in the vicinty). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_valve.png | file://x:/photopub/docs/0000000511/5f4ffccb-c6bd-4771-9aa7-eb364c75b7c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6647603f_0499_4918_b68c_22aacfb0230f
BPVOP-698153-2016 | 3549583 | 11/4/2016 2:46:25 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | Upon assessment it is determined that servicing nameplate is incomplete. Inadequate information on servicing nameplate may lead to subsequent wrong selection of safety valve. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Safety_relief_valve.png | file://x:/photopub/docs/0000000511/93322288-cd52-411e-9b08-e266a96f2e2b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f96e4c6b_73ae_4a95_ba14_47454514f7b7
BPVOP-698172-2016 | 4198261 | 11/4/2016 4:38:25 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of pressure vessel (evaporator in refrigeration system, Length:3.1m, Diameter:0.40m) with Maximum Allowable Working Pressure (MAWP) of 300psig, it is determined that pressure relief valve has exceeded the required 5year interval for servicing/replacement. Failure to have pressure relief valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down system. This could result in failure of pressure-boundary with release of refrigerant and may cause a severe incident (asphyxiation of personnel in the vicinty). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRESSURE_RELIEF_VALVE.png | file://x:/photopub/docs/0000000511/8f5944a4-37bb-4da2-852e-595574aafec5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__686d2ccd_61d3_477d_8ba4_01e425768b24
PROP-710924-2016 | 2224094 | 11/24/2016 12:12:23 PM | ASSESS: PR OP: Annual | png | #asFound | PR035 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Structure bolted to concrete not secured with double nuts. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | no_double_nuts.png | file://x:/photopub/docs/0000000521/f81cc5ca-af98-4395-9eb7-8bb4a1877b3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5803ff9d_b84c_49da_8fd3_7ed40f3034c6
ELIN-692824-2016 | EL-442780-2016 | 11/2/2016 3:44:19 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | John_you_ball.png | file://x:/photopub/docs/0000000511/2ada5ae4-3292-45d5-b6a6-27301665267f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58f51a16_1d44_4724_b264_a369c1e244e2
PROP-598662-2016 | 3614991 | 11/3/2016 9:21:23 PM | ASSESS: PR OP: RAP | png | #asFound | PR031 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | 1 | 1 | Missing fire extinguisher and non functioning smoke detectors. | 1 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | Broken_smoke_detector.png | file://x:/photopub/docs/0000000511/d31917ef-b50e-419a-ac57-8c3780008c41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__BD4ABD52_D1E1_40E7_B598_B19D1A86B41A
PROP-598660-2016 | 3366611 | 11/4/2016 8:50:02 AM | ASSESS: PR OP: RAP | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | The wand on the tension switch is loose, therefore it will not monitor carriage position. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | missing_smoke_detector.png | file://x:/photopub/docs/0000000511/8c610b87-972b-43e4-ae02-ec8d5d12c6c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__FBD9DA57_FD51_4575_AA15_79FE756E1A40
ELIN-670797-2016 | UW-442398-2016 | 9/26/2016 2:22:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL232 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | 4 | 4 | Electrical equipment operated in a Hazardous location. Wood dust producing facilities are a fire and explosion hazard is the dust is allowed to accumulate in sufficient quantities. | 4 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | B.png | file://x:/photopub/docs/0000000491/ab19e2f7-d8b2-40ec-b39a-37e527e643b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__820cb0ef_b361_4d60_b937_ba445bbd6d3e
ELIN-670797-2016 | UW-442398-2016 | 9/26/2016 2:22:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL232 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | 4 | 4 | Electrical equipment operated in a Hazardous location. Wood dust producing facilities are a fire and explosion hazard is the dust is allowed to accumulate in sufficient quantities. | 4 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | G.png | file://x:/photopub/docs/0000000491/70b95b9b-3366-4d4b-8b3b-68d1e41fdad2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__820cb0ef_b361_4d60_b937_ba445bbd6d3e
ELIN-670797-2016 | UW-442398-2016 | 9/26/2016 2:22:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL232 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | 4 | 4 | Electrical equipment operated in a Hazardous location. Wood dust producing facilities are a fire and explosion hazard is the dust is allowed to accumulate in sufficient quantities. | 4 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | H.png | file://x:/photopub/docs/0000000491/7a9bf6f5-e662-4946-b23e-610f0c0dde99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__820cb0ef_b361_4d60_b937_ba445bbd6d3e
ELIN-670797-2016 | UW-442398-2016 | 9/26/2016 2:22:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL232 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | 4 | 4 | Electrical equipment operated in a Hazardous location. Wood dust producing facilities are a fire and explosion hazard is the dust is allowed to accumulate in sufficient quantities. | 4 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | A.png | file://x:/photopub/docs/0000000491/e169d0a9-3ba7-4ca1-9b1b-3d01973caba5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__820cb0ef_b361_4d60_b937_ba445bbd6d3e
ELIN-670797-2016 | UW-442398-2016 | 9/26/2016 2:22:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL232 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | 4 | 4 | Electrical equipment operated in a Hazardous location. Wood dust producing facilities are a fire and explosion hazard is the dust is allowed to accumulate in sufficient quantities. | 4 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | J.png | file://x:/photopub/docs/0000000491/c6554831-b1a9-45be-8585-8f0452e771d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__820cb0ef_b361_4d60_b937_ba445bbd6d3e
ELIN-670797-2016 | UW-442398-2016 | 9/26/2016 2:22:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL232 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | 4 | 4 | Electrical equipment operated in a Hazardous location. Wood dust producing facilities are a fire and explosion hazard is the dust is allowed to accumulate in sufficient quantities. | 4 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | E.png | file://x:/photopub/docs/0000000491/35bf8255-c9c0-4393-9db6-ff22be312d76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__820cb0ef_b361_4d60_b937_ba445bbd6d3e
ELIN-681502-2016 | EL-404212-2016 | 11/7/2016 10:56:58 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Outlet boxes, containing energized 120 volt conductors, with no light fixture mounted and with no cover, increase the risk of accidental electrical shock in the event an energized electrical conductor is accidentally contacted by a person. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outlet_box_with_no_light_or_cover.png | file://x:/photopub/docs/0000000512/1f56466f-5f20-4720-b4e9-4cbaab1551b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42aa902e_c0d9_4010_92f6_4f87e241bebd
GAIN-640883-2016 | GA-396506-2016 | 9/20/2016 1:51:12 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Range does not meet side clearance to combustibles. Side wall could overheat and catch fire. | 3 | Clearance to combustible not met | Range_clearance.png | file://x:/photopub/docs/0000000488/e5dc7b96-001b-410a-8221-9d17efd24128.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__afdb8abd_9e7d_4b86_ac9c_8a728070e787
BPVIN-680412-2016 | BPV-449236-2016 | 10/5/2016 10:48:39 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Sand_blasting_air_tank.png | file://x:/photopub/docs/0000000498/58b37e9e-5e68-4510-acda-81c53f9832e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95144eaa_8799_4607_910e_7fad39ab1f39
BPVIN-680412-2016 | BPV-449236-2016 | 10/5/2016 10:48:39 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Sand_blasting_tank_PRD.png | file://x:/photopub/docs/0000000498/3eb1766a-0fe5-4aaf-bd14-e0d32dcec142.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95144eaa_8799_4607_910e_7fad39ab1f39
BPVIN-680412-2016 | BPV-449236-2016 | 10/5/2016 10:48:39 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Sand_blasting_air_tank_2.png | file://x:/photopub/docs/0000000498/ea01639b-172e-4e9d-a667-1b8682769dee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95144eaa_8799_4607_910e_7fad39ab1f39
BPVIN-680148-2016 | UW-449010-2016 | 10/5/2016 10:15:28 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound |  |  |  | 5 | This 30 psi maximum allowable working pressure hot water boiler does not have a hi-temperature limit control device which may contribute to an incident in the event the temperature surpasses the manufacturer's limit of 200 deg.F. |  |  | Front_boiler_.png | file://x:/photopub/docs/0000000498/4990d35f-f821-4cf2-9421-8f3c91e403f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__058ab6ed_5fd7_4d5b_ac1d_da901b345993
ELIN-708840-2016 | EL-470517-2016 | 11/25/2016 9:23:42 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Grounding_conductor__grounding_conductor_high_pressed_to_existing_grounding_conductor.png | file://x:/photopub/docs/0000000521/704b5fdd-3210-4539-90f7-56420c8d466b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d7476ce_ab83_4b26_8a5d_2408fbb8d0d8
ELIN-708840-2016 | EL-470517-2016 | 11/25/2016 9:23:42 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Park_model__Park_model_trailer_fed_by_two_pole_50_amp_circuit_breaker.png | file://x:/photopub/docs/0000000521/590cf991-9a7d-4452-87ab-3ec515fe820c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d7476ce_ab83_4b26_8a5d_2408fbb8d0d8
ELIN-708840-2016 | EL-470517-2016 | 11/25/2016 9:23:42 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Bonding_conductor__bonding_conductor_to_telephone_box.png | file://x:/photopub/docs/0000000521/733c2dba-3229-4f92-ae85-7045af8e55b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d7476ce_ab83_4b26_8a5d_2408fbb8d0d8
GAUP-662082-2016 | UW-436741-2016 | 9/27/2016 2:00:32 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | A First stage pressure regulator serving a consumer propane tank was installed below the liquid level of the tank. This regulator is designed for vapor use only, due to this configuration, liquid could enter the regulator causing failure of the regulator or related connected appliances. | 4 | 1st stage regulator installed below container liquid level | Pink_5_2.png | file://x:/photopub/docs/0000000491/62f6a3c8-9f66-437d-a094-35165706805b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e70837b_bfe2_4b00_8932_52f2878f74f1
GAHE-672272-2016 | HE-443531-2016 | 9/27/2016 1:14:24 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | Propane tank installed beside two diesel storage dispensers | 2 | Installation clearances or set backs to propane containers not met | Deka.png | file://x:/photopub/docs/0000000491/fa9b6494-38c4-4f63-90d3-9172813d8937.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4ab7a6b_0dd4_4757_812f_6a4684fc648a
GAUP-662091-2016 | UW-436748-2016 | 9/27/2016 2:37:10 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA082 | Vent limiter style regulator not installed in a ventilated space | 3 | 3 | Second stage regulator installed in wooden enclosure against house and sealed | 3 | Vent limiter style regulator not installed in a ventilated space | House1_1.png | file://x:/photopub/docs/0000000491/808ed647-c127-45e8-92e0-c04c1a5aecab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__216d9673_3568_4baa_bd88_dfb9480e622e
GAUP-662091-2016 | UW-436748-2016 | 9/27/2016 2:37:10 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA082 | Vent limiter style regulator not installed in a ventilated space | 3 | 3 | Second stage regulator installed in wooden enclosure against house and sealed | 3 | Vent limiter style regulator not installed in a ventilated space | House2.png | file://x:/photopub/docs/0000000491/c328bdca-7e5f-4120-b6e2-07a57e16db6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__216d9673_3568_4baa_bd88_dfb9480e622e
GAUP-662082-2016 | UW-436741-2016 | 9/27/2016 2:00:32 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | A First stage pressure regulator serving a consumer propane tank was installed below the liquid level of the tank. This regulator is designed for vapor use only, due to this configuration, liquid could enter the regulator causing failure of the regulator or related connected appliances. | 4 | 1st stage regulator installed below container liquid level | Pink5_1.png | file://x:/photopub/docs/0000000491/19f9803f-3815-4ff3-8dda-7047bec0649c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e70837b_bfe2_4b00_8932_52f2878f74f1
ELIN-666453-2016 | EL-409760-2016 | 10/5/2016 2:34:30 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | The 15 amp 120 volt circuits have no protection installed and have been energized. This is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_switches.png | file://x:/photopub/docs/0000000497/445dd206-1d52-41b2-8d5f-b85159765d77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__079e8ae6_915f_4a95_a07b_9bbdf96dbd56
ELIN-666453-2016 | EL-409760-2016 | 10/5/2016 2:34:30 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | The 15 amp 120 volt circuits have no protection installed and have been energized. This is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_receptacles.png | file://x:/photopub/docs/0000000497/07d40a84-1f02-451c-93c7-514b3786f8dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__079e8ae6_915f_4a95_a07b_9bbdf96dbd56
BPVIN-680148-2016 | UW-449010-2016 | 10/5/2016 10:15:28 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound |  |  |  | 5 | This 30 psi maximum allowable working pressure hot water boiler does not have a hi-temperature limit control device which may contribute to an incident in the event the temperature surpasses the manufacturer's limit of 200 deg.F. |  |  | Boiler_nameplate.png | file://x:/photopub/docs/0000000498/8ed428f1-d964-4ce6-9a9c-3333a1893262.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__058ab6ed_5fd7_4d5b_ac1d_da901b345993
BPVIN-680148-2016 | UW-449010-2016 | 10/5/2016 10:15:28 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound |  |  |  | 5 | This 30 psi maximum allowable working pressure hot water boiler does not have a hi-temperature limit control device which may contribute to an incident in the event the temperature surpasses the manufacturer's limit of 200 deg.F. |  |  | Temperature_control.png | file://x:/photopub/docs/0000000498/dc943106-7e1d-44ad-92fc-4f224eadca90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__058ab6ed_5fd7_4d5b_ac1d_da901b345993
ELIN-681191-2016 | EL-413838-2016 | 10/12/2016 10:32:34 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL265 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | 3 | 3 | This assessment found switches for lights and fans located within reach of a residential shower. The code requires switches to be 1m from the shower. There is a shock hazard for persons operating the stitches while in the shower. | 3 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | Switches_at_shower.png | file://x:/photopub/docs/0000000499/bf79ba92-787e-4a7c-9cd2-c560ffc6d978.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a783645_5e4f_452d_8f68_670338ef2f5e
ELIN-700316-2016 | UW-465254-2016 | 11/8/2016 4:35:11 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized receptacles are required to have cover plates installed on them. This is required to prevent accidental contact with energized terminals on receptacles. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation has energized terminals exposed to contact at a receptacle, and it's wiring/connections are exposed to contact and damage because the required cover plate is not installed. This is a potential shock and fire hazard if persons or objects contact energized terminals/wiring or if wiring or equipment fails and boxes do not contain thermal energy as intended. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Missing_receptacle_cover.png | file://x:/photopub/docs/0000000514/55556315-5d85-46f2-a4da-fc28e7940b7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e3edb59_aeb2_4894_933a_85d3e285bc65
ELIN-708318-2016 | EL-467222-2016 | 11/28/2016 2:28:30 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non metallic sheathed cable is in contact with heating ducts. Over time the integrity of the insulation can be compromised. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_in_proximity_to_duct_work.png | file://x:/photopub/docs/0000000522/f8fffb94-4591-4f1b-8935-30d288c12dbd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__156a00a5_c4bb_4b22_bd75_524c5f566849
GAIN-512871-2016 | GA-311897-2015 | 10/18/2016 2:23:42 PM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | Combustion Air pot for appliances is too small for combustion air requirements of appliances. Insufficient combustion air could cause flame roll out of flames from burners or possible sooting in heat exchangers | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Comb_air_pot_too_small.png | file://x:/photopub/docs/0000000506/03b442f8-2aeb-4d27-8e86-c7f6d807ff83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2633d76b_0cfc_4e4a_8eb3_c2e53de572fa
GAIN-680175-2016 | GA-417677-2016 | 10/17/2016 1:11:48 PM | ASSESS: GA: Rough-In | png | #asFound | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 5 | The as found condition was a line regulator situated in a mechanical room with gas fired equipment did not have a vent line installed terminating outdoors. The as found hazard is a regulator failure would allow for high pressure gas to flood the mechanical room, leading to a high likely-hood of explosion. | 5 | Relief style regulator/device allowed to vent within building/confined space | Line_Regulator.png | file://x:/photopub/docs/0000000501/566ef376-8b12-4a10-a6e2-b25bb882365f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__769e3c13_a62f_469e_a57d_3241f34d33a3
GAUP-690537-2016 | UW-456826-2016 | 11/4/2016 11:21:16 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA039 | Painting of exterior piping | 1 | 1 | Outdoor piping requires painting to prevent corrosion. | 1 | Painting of exterior piping | Painting_missing_.png | file://x:/photopub/docs/0000000511/3cf01828-af3f-4500-be91-e3212bbed16b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd0f4804_905b_4d46_a974_f890a59229f7
ELIN-681589-2016 | EL-450019-2016 | 10/12/2016 10:39:22 AM | ASSESS: EL: Final | png | #asFound | EL020 | Damage to equipment may result in overheating. | 4 | 4 | Upon inspection of outdoor service; Moisture was penetrated the service disconnect and was found to be very corroded where holes were visible on the bottom of enclosure. The hazards the remain are shock and thermal. | 4 | Damage to equipment may result in overheating. | Corroded_service__rusted_right_through.png | file://x:/photopub/docs/0000000499/7153f54e-22fa-41c7-9ff0-b533b7afe26e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ade88c2_c549_413f_8ccb_c786ccababea
ELHE-682564-2016 | HE-450727-2016 | 10/13/2016 4:49:38 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Main distribution has corrosion and water damage do to environmental conditions, thermal and shock hazards are now present because of this deterioration. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Corroded_distribution.png | file://x:/photopub/docs/0000000499/9935e069-dd24-4397-aa4e-bd65a09360e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96674440_ea0b_4911_84fa_1d8652ae2393
ELIN-681589-2016 | EL-450019-2016 | 10/12/2016 10:39:22 AM | ASSESS: EL: Final | png | #asFound | EL020 | Damage to equipment may result in overheating. | 4 | 4 | Upon inspection of outdoor service; Moisture was penetrated the service disconnect and was found to be very corroded where holes were visible on the bottom of enclosure. The hazards the remain are shock and thermal. | 4 | Damage to equipment may result in overheating. | 2_-panel.png | file://x:/photopub/docs/0000000499/da41066f-b00f-4001-b252-5e64641ab270.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ade88c2_c549_413f_8ccb_c786ccababea
ELIN-674586-2016 | EL-438409-2016 | 10/12/2016 11:56:20 AM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Meter has been pulled away from wall, screws that were securing meter base are now floating in meter base. The hazards are both shock, and thermal . | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Meter_is_not_secure.png | file://x:/photopub/docs/0000000499/751e3eb9-3b6f-456b-ae9a-06bf1ddc1a6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d26167d2_6cf6_4548_8ce4_1d9e7e1dd207
ELIN-680790-2016 | EL-449618-2016 | 10/12/2016 9:34:54 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL035 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | 3 | 3 | Cable has not been covered with sand to avoid mechanical damage to the cable. Also marking tape has not been installed correctly. Mechanical damage to the cable can cause the cable to short circuit if damaged and warning burial tape not been installed could potentially lead to the cable being accidentally damaged in the future due to persons not knowing the location of the energized cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | ACWU_cable.png | file://x:/photopub/docs/0000000499/09d17151-c128-44a2-ad60-f6ff27685afe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acb0bf59_46f3_4845_ad56_0be963dd5772
GAIN-678684-2016 | GA-446959-2016 | 10/11/2016 3:42:09 PM | ASSESS: GA: Final | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | Gas entering below grade is not permitted. Piping entering building below grade is subject to un-noticed corrosion and damage causing leaks which could migrate undetected into the crawl space. | 3 | Underground piping entering a building below grade (unapproved) | Gas_enter_below_grade.png | file://x:/photopub/docs/0000000498/20de7323-2770-4ee9-a8a4-773d4ebbfe95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1224062a_a8de_4a10_933e_38d2665305fe
ELIN-691827-2016 | EL-398768-2016 | 10/27/2016 11:54:43 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Energized_conductors.png | file://x:/photopub/docs/0000000506/09b03f2e-a2bb-4357-b44d-01bab4858d2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b58532e_bd92_43a2_908c_d54d48d4ead7
ELIN-695542-2016 | UW-461841-2016 | 11/1/2016 2:59:06 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL143 | Installation of electrical equipment Inadequate wiring or bending space provided for conductors inside boxes or cabinets | 3 | 3 | This assessment found conductors at receptacle boxes to be approximately half required 150mm in length. Without the length to make a solid splice there is the possibility of the joint overheating presenting a fire hazard. | 3 | Installation of electrical equipment Inadequate wiring or bending space provided for conductors inside boxes or cabinets | Free_conductor.png | file://x:/photopub/docs/0000000509/064af693-2d3d-4bf1-a037-5530258f2b35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f88fc2a_658e_4ff7_93cd_250f3f57384f
ELIN-695542-2016 | UW-461841-2016 | 11/1/2016 2:59:06 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL143 | Installation of electrical equipment Inadequate wiring or bending space provided for conductors inside boxes or cabinets | 3 | 3 | This assessment found conductors at receptacle boxes to be approximately half required 150mm in length. Without the length to make a solid splice there is the possibility of the joint overheating presenting a fire hazard. | 3 | Installation of electrical equipment Inadequate wiring or bending space provided for conductors inside boxes or cabinets | Cover.png | file://x:/photopub/docs/0000000509/055d23db-b4cd-476d-a449-18e48a0eee38.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f88fc2a_658e_4ff7_93cd_250f3f57384f
ELIN-700316-2016 | UW-465254-2016 | 11/8/2016 4:35:11 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized receptacles are required to have cover plates installed on them. This is required to prevent accidental contact with energized terminals on receptacles. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation has energized terminals exposed to contact at a receptacle, and it's wiring/connections are exposed to contact and damage because the required cover plate is not installed. This is a potential shock and fire hazard if persons or objects contact energized terminals/wiring or if wiring or equipment fails and boxes do not contain thermal energy as intended. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exterior_of_building.png | file://x:/photopub/docs/0000000514/89499393-a77c-43fc-b9e5-f22686d8bff4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e3edb59_aeb2_4894_933a_85d3e285bc65
ELIN-701499-2016 | EL-452773-2016 | 11/24/2016 11:28:38 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Improper use of electrical equipment. Meterbase pole mounting hardware not installed. Dry type connectors used in wet locations. Box fill in excess of code requirements. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | GAMBA_Rd_Pan_boxes.png | file://x:/photopub/docs/0000000521/f160c5a0-a7f8-46b7-b38f-84dcab5f33fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00f1ab64_01cb_4d53_ae8b_cd9410ed74f7
ELIN-701499-2016 | EL-452773-2016 | 11/24/2016 11:28:38 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Improper use of electrical equipment. Meterbase pole mounting hardware not installed. Dry type connectors used in wet locations. Box fill in excess of code requirements. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | GAMBA_Rd_Telephone_Box.png | file://x:/photopub/docs/0000000521/e947c34a-803e-48bc-8f92-957da7bf0a89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00f1ab64_01cb_4d53_ae8b_cd9410ed74f7
ELIN-702855-2016 | EL-443445-2016 | 11/15/2016 12:29:59 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 200 amp, 120/240 volt main distribution panel rated for indoor conditions only installed where panel is exposed to outdoor elements. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_exposed_to_weather.png | file://x:/photopub/docs/0000000516/550f6848-5064-40d6-8227-72b3802c29a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f730e5c8_acd2_4d15_94fa_6b1170d15b0e
ELIN-693886-2016 | EL-456610-2016 | 11/1/2016 3:20:16 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | NMD-90 cable installed in PVC conduit under concrete slab is in a wet location. This is a shock hazard condition. 120 Volt. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD-90_cable_in_wet_location_.png | file://x:/photopub/docs/0000000510/16bec831-2e72-46ad-9442-dbd9acd4e555.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf511b8f_0623_482f_91db_b2d081d3fa34
ELIN-693886-2016 | EL-456610-2016 | 11/1/2016 3:20:16 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | NMD-90 cable installed in PVC conduit under concrete slab is in a wet location. This is a shock hazard condition. 120 Volt. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD-90_cable_in_contact_with_heating_duct_.png | file://x:/photopub/docs/0000000510/6a17b8d6-f97a-4820-9bb0-ac6658e5d435.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf511b8f_0623_482f_91db_b2d081d3fa34
AMOP-711864-2016 | AM-103899-2014 | 11/29/2016 8:00:50 PM | ASSESS: AM OP: Periodic | png | #asFound | AM037 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Seat belt in need of repair, child could slip out of PCU | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Tug_seat_belt.png | file://x:/photopub/docs/0000000523/a7810e0d-f54b-4e9e-bc8a-1d1731d39377.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6f9912f_2047_438e_93b9_e7d7a26dea0e
AMOP-711874-2016 | AM-103902-2014 | 11/29/2016 8:22:41 PM | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | Speed pot set high for empty load at time of inspection, could remain at a higher setting for public if not properly documented in procedures. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Control_desk.png | file://x:/photopub/docs/0000000523/6d80e738-163b-4f53-80a3-c94cc0ac6e9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29d08830_0aab_41d5_bf57_5b170440da4f
ELIN-706443-2016 | EL-466738-2016 | 11/25/2016 2:57:58 PM | ASSESS: EL: Service Connection | png | #asFound | EL040 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 3 | 3 | Labels above each Hydro meter does not match the panel it feeds. Could lead to isolation of wrong system when trying to de energize | 3 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | Meter_label.png | file://x:/photopub/docs/0000000522/6f8eb5c5-a1d4-4767-a87e-69cbf0a92945.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8762964_1ac8_4885_9aac_cc917e6a003e
ELIN-691655-2016 | EL-441315-2016 | 10/28/2016 8:48:05 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | NMD-90 cables not supported within 300mm of entering device boxes. This can lead to shock or thermal hazard. 120 Volt. | 3 | Conductors Equipment is not approved for the specific use. | No_cable_supports_on_NMD_cable_entering_device_boxes_.png | file://x:/photopub/docs/0000000507/f8528131-16e1-4e3a-a82f-5be55eabddb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb7c064f_89fb_4c58_ad79_ba9867116e6d
GAIN-714010-2016 | GA-453062-2016 | 11/30/2016 1:40:31 PM | ASSESS: GA: Final | png | #asFound | GA082 | Vent limiter style regulator not installed in a ventilated space | 3 | 3 | 2 PSI regulator is located in an unventilated space. | 3 | Vent limiter style regulator not installed in a ventilated space | Regulator_located_in_lower_furnace_cabinet_.png | file://x:/photopub/docs/0000000524/d1cda42b-db83-48e9-9cf5-51db4b631503.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6588add9_cce1_433b_9656_bbe07261c2fe
ELOP-652391-2016 | EL-411636-2016 | 11/30/2016 11:59:21 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Service conductors have a branch tangled through them. If left the branch weight and position will cause abrasion creating a thermal and shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Hard_usage_wiring_with_cab_tire__.png | file://x:/photopub/docs/0000000524/6fa4e6a1-07d5-4ffe-b5d9-77b5a35b54d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__F96657D8_2170_487A_91BB_D7372999FC17
ELOP-652391-2016 | EL-411636-2016 | 11/30/2016 11:59:21 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Service conductors have a branch tangled through them. If left the branch weight and position will cause abrasion creating a thermal and shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Exterior_box_with_dry_connectors_.png | file://x:/photopub/docs/0000000524/f3da5c5f-61ec-42c1-8c67-db2ac8f044d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__F96657D8_2170_487A_91BB_D7372999FC17
ELIN-708920-2016 | EL-155883-2014 | 11/24/2016 8:15:18 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Found approved single phase 120/240 volt 200 amp rated 4 terminal lugged breaker has a 3 conductor feeder cable (feeder that has two hot or two current carrying conductors) had 2 hot conductors altered into 4 single conductors to terminate onto 4 terminal breaker. When approved electrical equipment or conductor is altered from original approved electrical equipment use, the electrical equipment is not approved and is not rated to carry the current originally designed, approved and rated for and is a possible electrical fire hazard for people and property. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 200_amp_breaker_and_conductors_altered_to_4_terminal_lug_2.png | file://x:/photopub/docs/0000000524/d6f842e5-a30f-4c9d-a865-8dd9a7bf7001.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__16edc672_7807_475a_8ca6_76b41f1d98e4
ELIN-708920-2016 | EL-155883-2014 | 11/24/2016 8:15:18 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Found approved single phase 120/240 volt 200 amp rated 4 terminal lugged breaker has a 3 conductor feeder cable (feeder that has two hot or two current carrying conductors) had 2 hot conductors altered into 4 single conductors to terminate onto 4 terminal breaker. When approved electrical equipment or conductor is altered from original approved electrical equipment use, the electrical equipment is not approved and is not rated to carry the current originally designed, approved and rated for and is a possible electrical fire hazard for people and property. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 200_amp_breaker_and_conductors_altered_to_4_terminal_lug_1.png | file://x:/photopub/docs/0000000524/6efd9520-7cab-424f-9167-9a28fc9b68fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__16edc672_7807_475a_8ca6_76b41f1d98e4
BPOP-698603-2016 | BPV-404723-2015 | 11/6/2016 7:28:37 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Service valve is not plugged. Valve could be left open or vandalized allowing high pressure gas to escape.if ignition source found a fire or explosion could occur resulting with property damage or loss of life. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Service_valve_with_wasp_nest.png | file://x:/photopub/docs/0000000512/b7fd6042-d38d-4588-9cca-42acbf5b7731.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__926df990_4655_414c_96d2_ffcaaefd2fd6
BPOP-698603-2016 | BPV-404723-2015 | 11/6/2016 7:28:37 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Service valve is not plugged. Valve could be left open or vandalized allowing high pressure gas to escape.if ignition source found a fire or explosion could occur resulting with property damage or loss of life. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Service_valve_not_plugged.png | file://x:/photopub/docs/0000000512/71d104a3-d0ce-4338-8b8c-a5ae166ab1a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__926df990_4655_414c_96d2_ffcaaefd2fd6
GAOP-698173-2016 | 2170952 | 11/8/2016 2:21:39 PM | ASSESS: GA OP: Periodic | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Clearance to combustible material not met. Clearance must be maintained to prevent a fire from affecting the propane storage tank. | 3 | Clearance to combustibles not maintained | Clearance_to_combustible_material_not_met_.png | file://x:/photopub/docs/0000000513/bec4b8c3-3d6a-4f6d-9f03-bfc7aeb2b203.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__122f5aeb_e900_4407_b74a_10aa0a09148d
GAIN-702338-2016 | GA-383379-2016 | 11/29/2016 11:44:56 AM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Copper_gas_line_unprotected.png | file://x:/photopub/docs/0000000523/c16db236-095d-45b5-8810-156966e9bd94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__50f102f9_1919_414c_84a2_4ac5f23a6ebc
ELIN-711973-2016 | EL-229037-2015 | 11/28/2016 7:55:56 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Service_disconnec__Service_disconnected_from_utility_and_electrically_safe.png | file://x:/photopub/docs/0000000522/c53f229e-ec51-447a-8cd8-694fcef92c03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__174a0c5a_a67c_404f_8f37_bbb82f02e248
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | 17.png | file://x:/photopub/docs/0000000524/fe708f55-feaa-4653-add7-917e7235871e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_13.png | file://x:/photopub/docs/0000000524/9ae1455a-3186-4fcd-9a78-75744eb75c08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_10.png | file://x:/photopub/docs/0000000524/b2697075-7f58-469e-9c64-de55e8701e22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_7.png | file://x:/photopub/docs/0000000524/246dcbef-b992-423d-b031-93b329040dc4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_15.png | file://x:/photopub/docs/0000000524/e2468098-f6bd-44f9-a4ed-bcb43ef886dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_2.png | file://x:/photopub/docs/0000000524/11c4f627-1012-4080-a3d5-ec7624138e9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_9.png | file://x:/photopub/docs/0000000524/3911f3fd-3686-4c5a-8298-343e0c548307.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_16.png | file://x:/photopub/docs/0000000524/c77fcf9a-b53d-4c55-81ac-de03deda8a1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_1.png | file://x:/photopub/docs/0000000524/54c94403-9741-4a93-82e7-086ba4561be7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_20.png | file://x:/photopub/docs/0000000524/da22563a-b01a-43bc-b7c5-81ce77471854.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | 19.png | file://x:/photopub/docs/0000000524/a9a16aa2-adea-4520-a709-8949845091de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_3.png | file://x:/photopub/docs/0000000524/cd196a50-8c67-4f40-9d64-dc6cb03d88a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_18.png | file://x:/photopub/docs/0000000524/293e77b9-c3f2-4930-ac20-5ce4dfeffa66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_8.png | file://x:/photopub/docs/0000000524/6eedc94f-6677-499a-8f85-965c8e84ae75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_4.png | file://x:/photopub/docs/0000000524/57175834-5019-49d0-a942-469126857807.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_5.png | file://x:/photopub/docs/0000000524/146ceef4-1bad-4355-8842-f4020a13db61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_6.png | file://x:/photopub/docs/0000000524/4c0a77db-6912-4076-808e-052c40c47063.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_21.png | file://x:/photopub/docs/0000000524/d835228c-dbfe-49c2-b748-d606b9631a75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-708321-2016 | HE-470191-2016 | 11/18/2016 3:03:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Bare, live parts of electrical equipment are to be guarded against accidental contact by persons or equipment by approved cabinets or enclosures. During an assessment at a hotel, the safety officer identified electrical equipment in the electrical, sprinkler, mechanical and boiler rooms that did not have the protective barriers or covers installed. A shock hazard exists for persons that could come in contact with the live terminals of this equipment. A fire hazard also exists if a fault condition was to occur at the equipment and there was no cover installed to contain the electrical energy. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_pressure_switch.png | file://x:/photopub/docs/0000000519/2226018e-e44f-4ba3-a994-078d5b36023a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc1eaea3_2065_4b3c_8cee_451c0c5eac6f
ELHE-708321-2016 | HE-470191-2016 | 11/18/2016 3:03:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Bare, live parts of electrical equipment are to be guarded against accidental contact by persons or equipment by approved cabinets or enclosures. During an assessment at a hotel, the safety officer identified electrical equipment in the electrical, sprinkler, mechanical and boiler rooms that did not have the protective barriers or covers installed. A shock hazard exists for persons that could come in contact with the live terminals of this equipment. A fire hazard also exists if a fault condition was to occur at the equipment and there was no cover installed to contain the electrical energy. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_time_clock_boiler_rm.png | file://x:/photopub/docs/0000000519/eda30c4c-39d1-4784-8898-761985773ab3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc1eaea3_2065_4b3c_8cee_451c0c5eac6f
ELHE-708321-2016 | HE-470191-2016 | 11/18/2016 3:03:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Bare, live parts of electrical equipment are to be guarded against accidental contact by persons or equipment by approved cabinets or enclosures. During an assessment at a hotel, the safety officer identified electrical equipment in the electrical, sprinkler, mechanical and boiler rooms that did not have the protective barriers or covers installed. A shock hazard exists for persons that could come in contact with the live terminals of this equipment. A fire hazard also exists if a fault condition was to occur at the equipment and there was no cover installed to contain the electrical energy. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_Starter__boiler_room.png | file://x:/photopub/docs/0000000519/f164938f-36ee-4db1-94a1-50d9a5696233.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc1eaea3_2065_4b3c_8cee_451c0c5eac6f
ELHE-708321-2016 | HE-470191-2016 | 11/18/2016 3:03:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Bare, live parts of electrical equipment are to be guarded against accidental contact by persons or equipment by approved cabinets or enclosures. During an assessment at a hotel, the safety officer identified electrical equipment in the electrical, sprinkler, mechanical and boiler rooms that did not have the protective barriers or covers installed. A shock hazard exists for persons that could come in contact with the live terminals of this equipment. A fire hazard also exists if a fault condition was to occur at the equipment and there was no cover installed to contain the electrical energy. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_starter_electrical_rm.png | file://x:/photopub/docs/0000000519/2b27efbd-3584-4a8c-8c85-bfb695a5b669.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc1eaea3_2065_4b3c_8cee_451c0c5eac6f
ELHE-708321-2016 | HE-470191-2016 | 11/18/2016 3:03:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Bare, live parts of electrical equipment are to be guarded against accidental contact by persons or equipment by approved cabinets or enclosures. During an assessment at a hotel, the safety officer identified electrical equipment in the electrical, sprinkler, mechanical and boiler rooms that did not have the protective barriers or covers installed. A shock hazard exists for persons that could come in contact with the live terminals of this equipment. A fire hazard also exists if a fault condition was to occur at the equipment and there was no cover installed to contain the electrical energy. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | No_device_cover.png | file://x:/photopub/docs/0000000519/8f37f8c6-7e0e-4024-a701-fb99f02c3872.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc1eaea3_2065_4b3c_8cee_451c0c5eac6f
EDMA-710381-2016 | ED-200664-2015 | 11/23/2016 4:30:44 PM | ASSESS: ED MA: Partial Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | Ensure multi panel car door is linked mechanically | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Car_door.png | file://x:/photopub/docs/0000000520/9952c5da-c60c-431b-a946-84bd8a2fe6f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3ef87d5_e876_4fab_90e3_9818751b9cb6
ELIN-672146-2016 | EL-439913-2016 | 9/27/2016 1:43:06 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Service supply bare neutral is in contact with service EMT. Possibility for service conduit to carry portion of unbalanced load as bonded electrical equipment. Potential for equipment damage or shock. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 100Amp_service_EMT_is_27mm.png | file://x:/photopub/docs/0000000491/c008d1c2-5293-4f83-9de4-5d1e0a03bae7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67043f12_9110_4b9f_ab54_e2b2179c0690
ELOP-652391-2016 | EL-411636-2016 | 11/30/2016 11:59:21 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Service conductors have a branch tangled through them. If left the branch weight and position will cause abrasion creating a thermal and shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Tree_branch_on_service_conductors_.png | file://x:/photopub/docs/0000000524/b597c656-7546-47e7-80e5-d1b8584ff656.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__F96657D8_2170_487A_91BB_D7372999FC17
PROP-598658-2016 | 2224197 | 11/16/2016 7:38:54 PM | ASSESS: PR OP: RAP | png | #asFound | PR046 | Non-Safety Critical monitoring bypassed or failed in manner reasonably detectable by maintenance/operation program Brake system pressure GB over temp Brake pad wear | 1 | 1 | Safety gate unable to move freely away from passenger. | 1 | Non-Safety Critical monitoring bypassed or failed in manner reasonably detectable by maintenance/operation program Brake system pressure GB over temp Brake pad wear | Safety_gate.png | file://x:/photopub/docs/0000000519/47a0de9e-221a-465d-9c2d-2ad6712b03f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__EB35BF13_3F3C_4072_AE35_856D358503E0
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_11.png | file://x:/photopub/docs/0000000524/0a984404-4497-4c91-bfe2-4054f71caa74.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_14.png | file://x:/photopub/docs/0000000524/b1cbb205-489a-49e0-998f-5bf54900ba47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | fire_damaged_subpanel_and_its_electrical_equipment_wiring_and_breakers_22.png | file://x:/photopub/docs/0000000524/84854320-d755-41ea-bd36-aed338726e2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
ELHE-715090-2016 | HE-474902-2016 | 12/1/2016 7:53:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Found 120/240 volt 100 amp rated panelboard and its distribution electrical equipment (such as branch circuit breakers, cables and conductors) to be fire and smoke damaged from an electrical fire within this distribution compartment. The damaged electrical equipment is still connected to power supply system and is electrical equipment that is not safe, compliant or approved for the use as connected. When approved electrical equipment is fire and smoke damaged, the damaged electrical equipment has lost its approval and is a possible electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | 12.png | file://x:/photopub/docs/0000000524/f3558c93-255c-446c-ad31-245f7f7c721f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff53a2ed_6b22_432a_83d8_eca6f2017a18
BPVOP-699046-2016 | 2254345 | 11/8/2016 1:54:28 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Log_book_entry_.png | file://x:/photopub/docs/0000000513/804acc3c-cfb7-4b4f-a573-bfbc8f627fc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d795b431_dde3_44e5_8228_099ba7fdc538
BPVOP-699046-2016 | 2254345 | 11/8/2016 1:54:28 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Log_book_entry_2.png | file://x:/photopub/docs/0000000513/09f1dc02-9f29-4772-b9b1-cb2de7578e62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d795b431_dde3_44e5_8228_099ba7fdc538
BPVOP-699046-2016 | 2254345 | 11/8/2016 1:54:28 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Posted_Operator_certificates_.png | file://x:/photopub/docs/0000000513/9119cf3b-3a14-4e51-a525-0c3a81f5262c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d795b431_dde3_44e5_8228_099ba7fdc538
ELIN-684178-2016 | EL-445827-2016 | 10/17/2016 11:35:50 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | Bond strap in place in sub distribution, straps are to be removed to provide an equipotential plane for fault currents to clear themselves, leaving strap in place would provide alternate paths to be created for a fault. Thus putting persons and property at risk of shock and fire. | 3 | Continuity Bonding; method for equipment is not adequate. | Bond_strap_in_place_in_sub_distribution_.png | file://x:/photopub/docs/0000000501/bfd2fd54-59d5-4fb8-8fc8-6a613e685836.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32efb264_3065_4ebb_a290_e02ca43365bf
ELIN-693940-2016 | EL-445408-2016 | 11/1/2016 7:31:04 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 3 | Service equipment is not protected from the effects of weather (rainwater ingress into service equipment). This poses a serious risk of personal injury (shock) or property damage (thermal event) due to energized equipment coming in contact with water. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Detail02_service_conductors.png | file://x:/photopub/docs/0000000509/8c755ad9-991b-4e4c-9eb4-71d01cf80aec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7528969a_bb27_44ea_8a2e_1f303a96ec94
ELIN-693733-2016 | EL-458803-2016 | 10/31/2016 7:55:28 AM | ASSESS: EL: Service Connection | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | View01_service.png | file://x:/photopub/docs/0000000509/bacd7aff-66ba-4c4e-97fc-5d066aac3643.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a70f033_639d_4943_ab0d_52360c0c696f
ELIN-693940-2016 | EL-445408-2016 | 11/1/2016 7:31:04 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 3 | Service equipment is not protected from the effects of weather (rainwater ingress into service equipment). This poses a serious risk of personal injury (shock) or property damage (thermal event) due to energized equipment coming in contact with water. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | View01_service_equipment.png | file://x:/photopub/docs/0000000509/0f97a368-8cb8-4418-b9cb-b7d354d00f32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7528969a_bb27_44ea_8a2e_1f303a96ec94
ELIN-666687-2016 | UW-265372-2015 | 9/19/2016 1:32:10 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical service and distribution has been exposed to weather and not maintained. This is a equipment damage condition. 120/240 Volt, 400 Amp. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Weathered_and_deteriorated_electrical_service.png | file://x:/photopub/docs/0000000489/baaf1d58-322e-4224-ae3c-e1c7cbc16c7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d325d109_49e2_45cf_ae92_968544b2f53a
ELIN-666687-2016 | UW-265372-2015 | 9/19/2016 1:32:10 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical service and distribution has been exposed to weather and not maintained. This is a equipment damage condition. 120/240 Volt, 400 Amp. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Exposed_unprotected_feeder_cable_for_home_sub_service.png | file://x:/photopub/docs/0000000489/f14db9e7-161a-4d82-bca4-cd4fce537aa7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d325d109_49e2_45cf_ae92_968544b2f53a
ELIN-666687-2016 | UW-265372-2015 | 9/19/2016 1:32:10 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical service and distribution has been exposed to weather and not maintained. This is a equipment damage condition. 120/240 Volt, 400 Amp. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Photos_at_8508_Clerke_Rd__Vernon_BC.png | file://x:/photopub/docs/0000000489/f3d9e29f-5710-489e-8c78-dfd90b09bf72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d325d109_49e2_45cf_ae92_968544b2f53a
ELIN-666687-2016 | UW-265372-2015 | 9/19/2016 1:32:10 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical service and distribution has been exposed to weather and not maintained. This is a equipment damage condition. 120/240 Volt, 400 Amp. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Weathered_and_deteriorated_electrical_service_at_8508_Clerke_Rd__Vernon.png | file://x:/photopub/docs/0000000489/9565123d-384a-42f7-9447-f8e92489331d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d325d109_49e2_45cf_ae92_968544b2f53a
ELIN-667251-2016 | EL-406679-2016 | 9/20/2016 6:04:25 AM | ASSESS: EL: Service Connection | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | HPS Ballast has been attached directly to a combustible material, if a failure in the core were to occur, or just the heat created form the ballast could ignite plywood if not mitigated. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | Core_against_plywood.png | file://x:/photopub/docs/0000000489/e305cd34-b952-4e62-9806-02ed429ceeb5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b5e5271_d44a_430c_83d8_d253e771423d
ELIN-665748-2016 | EL-421119-2016 | 9/20/2016 10:11:06 AM | ASSESS: EL: Final | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Sheath currents will result from not bonding ACWU armour, this will cause a thermal and possible shock hazard. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | ACWU_sheath_not_bonded.png | file://x:/photopub/docs/0000000489/07861b2b-d53b-4471-bf88-924f8bf45a3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08e3fd7e_2e4b_4b7d_9d3b_b4e243952247
ELIN-667251-2016 | EL-406679-2016 | 9/20/2016 6:04:25 AM | ASSESS: EL: Service Connection | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | HPS Ballast has been attached directly to a combustible material, if a failure in the core were to occur, or just the heat created form the ballast could ignite plywood if not mitigated. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | Conduit_with_no_drainage_.png | file://x:/photopub/docs/0000000489/3ac54032-feb2-4b84-94cb-eb1e33e56f0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b5e5271_d44a_430c_83d8_d253e771423d
ELIN-666343-2016 | EL-378949-2016 | 9/29/2016 12:44:22 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Outlet covers on receptacles operating on circuits up to 30 amps 240 volts have not been installed. Persons can be injured if they accidentally contact live exposed terminals. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Covers_missing_throughout.png | file://x:/photopub/docs/0000000492/f51f9048-4d52-491a-9d61-329a2846d680.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d6f9210_2146_4b6d_abc5_d1a97774c4d5
BPOP-670566-2016 | BPV-405316-2015 | 10/19/2016 9:15:37 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Dual port service valve on 1000 gallon propane tank was in closed position but not plugged. Vandal could open valve and release high pressure gas into the atmosphere. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 38615-_107_St__Oliver.png | file://x:/photopub/docs/0000000503/08690c96-f68d-40b3-860c-f39f0ec93aba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cad9f315_ad7e_4f59_b62a_697b9444f3a2
BPOP-670567-2016 | BPV-405317-2015 | 10/20/2016 7:13:10 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Vapour outlet on service valve is valved off but is not plugged. Valve could be opened allowing high pressure propane gas to escape. If ignition took place this could cause a fire resulting in property loss or loss of life. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 38615_107_St__Oliver_unit_13.png | file://x:/photopub/docs/0000000503/9a44f21b-4f81-4fbb-b8e8-b53d9de20969.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7a4eb7fc_a520_4ad8_82fe_c52bcd684ee1
ELIN-706938-2016 | EL-453608-2016 | 11/29/2016 5:21:24 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found main panel-board, rated 120/240 volt 100 amp with #3 AWG copper feeder, has bonding conductor bonded to panelboard using wood screw (screwed into panelboard metal and into wood backing behind panelboard) and a 3/4" EMT galvanized strap used as a washer for wood screw, for bonding feeder bond conductor to panelboard enclosure. When electrical equipment is not bonded properly using appropriate and approved electrical equipment as required by code, the electrical equipment could be a possible electrical fire or shock hazard to people and property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | bonding_of_feeder_not_effective5.png | file://x:/photopub/docs/0000000523/e55f91a3-9d66-41da-98c8-dcb68cbf4e6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5785631f_3381_45f4_926d_8651cf4614f3
ELIN-706938-2016 | EL-453608-2016 | 11/29/2016 5:21:24 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found main panel-board, rated 120/240 volt 100 amp with #3 AWG copper feeder, has bonding conductor bonded to panelboard using wood screw (screwed into panelboard metal and into wood backing behind panelboard) and a 3/4" EMT galvanized strap used as a washer for wood screw, for bonding feeder bond conductor to panelboard enclosure. When electrical equipment is not bonded properly using appropriate and approved electrical equipment as required by code, the electrical equipment could be a possible electrical fire or shock hazard to people and property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | bonding_of_feeder_not_effective3.png | file://x:/photopub/docs/0000000523/4bff0f1c-d40f-43ff-82d7-9dd4b4db3968.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5785631f_3381_45f4_926d_8651cf4614f3
ELIN-706938-2016 | EL-453608-2016 | 11/29/2016 5:21:24 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found main panel-board, rated 120/240 volt 100 amp with #3 AWG copper feeder, has bonding conductor bonded to panelboard using wood screw (screwed into panelboard metal and into wood backing behind panelboard) and a 3/4" EMT galvanized strap used as a washer for wood screw, for bonding feeder bond conductor to panelboard enclosure. When electrical equipment is not bonded properly using appropriate and approved electrical equipment as required by code, the electrical equipment could be a possible electrical fire or shock hazard to people and property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | bonding_of_feeder_not_effective1.png | file://x:/photopub/docs/0000000523/6b1f259a-96fc-4a87-b198-0e7e5f8542e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5785631f_3381_45f4_926d_8651cf4614f3
ELIN-706938-2016 | EL-453608-2016 | 11/29/2016 5:21:24 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found main panel-board, rated 120/240 volt 100 amp with #3 AWG copper feeder, has bonding conductor bonded to panelboard using wood screw (screwed into panelboard metal and into wood backing behind panelboard) and a 3/4" EMT galvanized strap used as a washer for wood screw, for bonding feeder bond conductor to panelboard enclosure. When electrical equipment is not bonded properly using appropriate and approved electrical equipment as required by code, the electrical equipment could be a possible electrical fire or shock hazard to people and property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | bonding_of_feeder_not_effective4.png | file://x:/photopub/docs/0000000523/946f27a4-cc6f-4000-aa45-a897b4488891.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5785631f_3381_45f4_926d_8651cf4614f3
ELIN-706938-2016 | EL-453608-2016 | 11/29/2016 5:21:24 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found main panel-board, rated 120/240 volt 100 amp with #3 AWG copper feeder, has bonding conductor bonded to panelboard using wood screw (screwed into panelboard metal and into wood backing behind panelboard) and a 3/4" EMT galvanized strap used as a washer for wood screw, for bonding feeder bond conductor to panelboard enclosure. When electrical equipment is not bonded properly using appropriate and approved electrical equipment as required by code, the electrical equipment could be a possible electrical fire or shock hazard to people and property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | bonding_of_feeder_not_effective2.png | file://x:/photopub/docs/0000000523/243aecfc-7014-4569-908c-ec9b1c07834e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5785631f_3381_45f4_926d_8651cf4614f3
ELIN-675402-2016 | EL-443662-2016 | 10/14/2016 11:52:02 AM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | On a routine Silver label inspection, a. 120/240volt 60amp sub-panel was found with no covers installed or anywhere to be found. This could lead to a shock hazard . Pic attached. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Open_panel.png | file://x:/photopub/docs/0000000501/71a33a27-5aa3-4331-a98d-b306b124bb70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b2601275_d7b6_48e9_a3b7_ac50129a855f
ELHE-712026-2016 | HE-472953-2016 | 11/25/2016 1:53:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Electrical equipment has not been approved by a certification body recognized by the standards council of Canada there is a likelihood or possibility of an electrical incident is high. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Certification_Mark__certification_mark_for_generato.png | file://x:/photopub/docs/0000000521/0a0175ac-b75e-40e6-acc9-f099298cf5da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23149630_5e42_4ab9_a626_b072bdfb295c
ELHE-712026-2016 | HE-472953-2016 | 11/25/2016 1:53:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Electrical equipment has not been approved by a certification body recognized by the standards council of Canada there is a likelihood or possibility of an electrical incident is high. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Certification_Mark_for__certification_mark_for_coding_stripper.png | file://x:/photopub/docs/0000000521/cf983e8c-ec02-4047-871c-758a4ec443bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23149630_5e42_4ab9_a626_b072bdfb295c
ELHE-712026-2016 | HE-472953-2016 | 11/25/2016 1:53:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Electrical equipment has not been approved by a certification body recognized by the standards council of Canada there is a likelihood or possibility of an electrical incident is high. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Certification_Mark__certification_mark_for_polisher.png | file://x:/photopub/docs/0000000521/b138bc03-1e6a-4842-b686-d31152076ef9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23149630_5e42_4ab9_a626_b072bdfb295c
ELIN-665748-2016 | EL-421119-2016 | 9/20/2016 10:11:06 AM | ASSESS: EL: Final | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Sheath currents will result from not bonding ACWU armour, this will cause a thermal and possible shock hazard. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Out_door_cover.png | file://x:/photopub/docs/0000000489/8aad9229-0508-4544-adf9-35c457d1548b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08e3fd7e_2e4b_4b7d_9d3b_b4e243952247
ELIN-667251-2016 | EL-406679-2016 | 9/20/2016 6:04:25 AM | ASSESS: EL: Service Connection | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | HPS Ballast has been attached directly to a combustible material, if a failure in the core were to occur, or just the heat created form the ballast could ignite plywood if not mitigated. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | 2_pole_40_Amp_breaker.png | file://x:/photopub/docs/0000000489/b21024c8-3970-43bb-912b-d43136942a1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b5e5271_d44a_430c_83d8_d253e771423d
ELIN-665748-2016 | EL-421119-2016 | 9/20/2016 10:11:06 AM | ASSESS: EL: Final | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Sheath currents will result from not bonding ACWU armour, this will cause a thermal and possible shock hazard. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Exterior_light.png | file://x:/photopub/docs/0000000489/467eadc8-cbb9-4e69-878f-04616f5b3bc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08e3fd7e_2e4b_4b7d_9d3b_b4e243952247
ELIN-667251-2016 | EL-406679-2016 | 9/20/2016 6:04:25 AM | ASSESS: EL: Service Connection | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | HPS Ballast has been attached directly to a combustible material, if a failure in the core were to occur, or just the heat created form the ballast could ignite plywood if not mitigated. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | Guy_direction_going_the_wrong_way.png | file://x:/photopub/docs/0000000489/01186615-bab5-4ab2-88e3-179193aec40b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b5e5271_d44a_430c_83d8_d253e771423d
ELIN-667251-2016 | EL-406679-2016 | 9/20/2016 6:04:25 AM | ASSESS: EL: Service Connection | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | HPS Ballast has been attached directly to a combustible material, if a failure in the core were to occur, or just the heat created form the ballast could ignite plywood if not mitigated. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | Branch_circuits_that_are_protected_by_40_Amp.png | file://x:/photopub/docs/0000000489/f1457f3b-434e-4419-ac23-84b0e8a88b11.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b5e5271_d44a_430c_83d8_d253e771423d
ELIN-668404-2016 | EL-423194-2016 | 9/22/2016 1:39:14 PM | ASSESS: EL: Final | png | #asFound | EL093 | Continuity Grounding conductor has been spliced | 2 | 2 |  | 2 | Continuity Grounding conductor has been spliced | Ground_connections_in_splitter_before_txformer.png | file://x:/photopub/docs/0000000489/8203649f-23b4-49f9-ba80-5b2f69db11f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e2697e0_42c3_45dd_9127_d0e7d9e1803d
GAIN-693382-2016 | GA-429333-2016 | 11/8/2016 11:42:04 AM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | Gas leak in piping. Possible fire hazard. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Wilmot.png | file://x:/photopub/docs/0000000513/99143d21-9cdb-4dbc-82be-72487c0bd0ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd1d15d4_bcb9_4cf8_9767_e43378c6961a
ELIN-699859-2016 | EL-464172-2016 | 11/9/2016 11:24:42 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | # 8 awg terminated under wire binding screw, termination of the bond conductor in this manner does not make conctact with all of the stranded conductors due to its size. Inadequate bonding may cause overcurrent devices to not clear a fault, thus providing a risk of fire and shock. | 3 | Continuity Bonding; method for equipment is not adequate. | 8_awg_terminated_with_wire_binding_screw.png | file://x:/photopub/docs/0000000514/173d29e7-2514-45bc-8d3b-76693f874446.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a25b9385_e422_4844_8147_fe7021605414
ELIN-699874-2016 | EL-464155-2016 | 11/9/2016 12:51:50 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #8 stranded terminated under wire binding screw, #8 is too large to terminate in this manner, not all conductors are in contact. Insufficient bonding may lead to overcurrent devices not clearing a fault. A risk of fire and shock are present if a fault were to occur. | 3 | Continuity Bonding; method for equipment is not adequate. | 8awg_under_wire_binding_screw.png | file://x:/photopub/docs/0000000514/b92fb694-0cef-4f39-899c-4a48e7614ae9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53a3be36_ca20_4442_b05a_9651b1fdb44b
ELIN-687495-2016 | EL-371713-2016 | 10/21/2016 3:47:05 PM | ASSESS: EL: Final | png | #asFound | EL274 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | 3 | 3 | Hydromassage tubs that are connected to electrical components are required to be protected by a class A ground fault circuit interrupter (GFCI). This is because a person submerged in water is at a high risk if exposed to even a small amount of electrical current. In this installation, a homeowner connected a hydromassage tub to an electrical circuit that was not GFCI protected. This could create a possible shock hazard to persons using this tub if an electrical short was to occur. | 3 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | No_GFCI_for_jetted_tub.png | file://x:/photopub/docs/0000000504/688d3d2c-32d4-4978-8bf7-5ce5dd871119.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2eb9108d_c3cc_4689_b521_02804afd25f1
EDMA-689276-2016 | ED-291959-2015 | 10/23/2016 2:17:42 PM | ASSESS: ED MA: Partial Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 |  | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Governor1.png | file://x:/photopub/docs/0000000504/8db8123d-e6bc-4bab-a2ce-16248da27c8c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__221e8503_9259_4fbf_89c3_ff47697c0b55
BPVOP-709061-2016 | 2263618 | 11/23/2016 9:34:46 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 3 years as well as the NDE required was not done as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Safety_order_not_followed.png | file://x:/photopub/docs/0000000520/145b93ac-b494-4b00-a197-f4e0c199efaa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac43c8c1_9184_412f_81d1_e01e81d75cd4
BPOP-670679-2016 | BPV-404806-2015 | 12/1/2016 11:31:21 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA032 | Tank, containing propane located with-in an enclosure, no sources of ignition present. | 3 | 3 | The ass found hazard was a 1000USWG propane tank which had been located within a structure composed of three non-combustible walls and a non-combustible roof with no evident sources of ignition present at the time of inspection. This is a hazard because if propane were to be released from the vessel there is a high risk of the propane vapour being trapped within the structure and accumulating. Risk of fire or explosion. | 3 | Tank, containing propane located with-in an enclosure, no sources of ignition present. | propane_tank.png | file://x:/photopub/docs/0000000524/94d7e576-b430-43be-a2aa-32d8b522120c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29f55617_7b39_43a4_ac8c_23f5103b14c6
BPOP-670679-2016 | BPV-404806-2015 | 12/1/2016 11:31:21 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA032 | Tank, containing propane located with-in an enclosure, no sources of ignition present. | 3 | 3 | The ass found hazard was a 1000USWG propane tank which had been located within a structure composed of three non-combustible walls and a non-combustible roof with no evident sources of ignition present at the time of inspection. This is a hazard because if propane were to be released from the vessel there is a high risk of the propane vapour being trapped within the structure and accumulating. Risk of fire or explosion. | 3 | Tank, containing propane located with-in an enclosure, no sources of ignition present. | Data_tag.png | file://x:/photopub/docs/0000000524/e71127b2-b8e9-46f6-9f21-e5688e41c6c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29f55617_7b39_43a4_ac8c_23f5103b14c6
BPOP-670679-2016 | BPV-404806-2015 | 12/1/2016 11:31:21 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA032 | Tank, containing propane located with-in an enclosure, no sources of ignition present. | 3 | 3 | The ass found hazard was a 1000USWG propane tank which had been located within a structure composed of three non-combustible walls and a non-combustible roof with no evident sources of ignition present at the time of inspection. This is a hazard because if propane were to be released from the vessel there is a high risk of the propane vapour being trapped within the structure and accumulating. Risk of fire or explosion. | 3 | Tank, containing propane located with-in an enclosure, no sources of ignition present. | Tank_location.png | file://x:/photopub/docs/0000000524/6e2d261a-083c-4297-baae-119e38539d44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29f55617_7b39_43a4_ac8c_23f5103b14c6
BPOP-670679-2016 | BPV-404806-2015 | 12/1/2016 11:31:21 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA032 | Tank, containing propane located with-in an enclosure, no sources of ignition present. | 3 | 3 | The ass found hazard was a 1000USWG propane tank which had been located within a structure composed of three non-combustible walls and a non-combustible roof with no evident sources of ignition present at the time of inspection. This is a hazard because if propane were to be released from the vessel there is a high risk of the propane vapour being trapped within the structure and accumulating. Risk of fire or explosion. | 3 | Tank, containing propane located with-in an enclosure, no sources of ignition present. | Relief_valve.png | file://x:/photopub/docs/0000000524/79c5c75d-73b2-4be8-9292-ad7cef7d9fb4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29f55617_7b39_43a4_ac8c_23f5103b14c6
ELIN-715858-2016 | UW-475428-2016 | 12/1/2016 3:09:30 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | AC90 emitting from 480V splitter with ends of conductor not properly housed. Conductors are required to be housed in suitable enclosures. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | F.png | file://x:/photopub/docs/0000000524/88d436b5-f8ca-4a74-ba7d-a0b59af5bf5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7caa8e5_46da_4d97_ae43_a8ca3fc235b4
ELIN-715858-2016 | UW-475428-2016 | 12/1/2016 3:09:30 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | AC90 emitting from 480V splitter with ends of conductor not properly housed. Conductors are required to be housed in suitable enclosures. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | E.png | file://x:/photopub/docs/0000000524/f686246d-79b6-42e6-814f-bdf88345ddd2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7caa8e5_46da_4d97_ae43_a8ca3fc235b4
ELIN-715858-2016 | UW-475428-2016 | 12/1/2016 3:09:30 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | AC90 emitting from 480V splitter with ends of conductor not properly housed. Conductors are required to be housed in suitable enclosures. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C.png | file://x:/photopub/docs/0000000524/d3166a27-26c4-4e46-a69a-160e221bac51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7caa8e5_46da_4d97_ae43_a8ca3fc235b4
ELIN-715858-2016 | UW-475428-2016 | 12/1/2016 3:09:30 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | AC90 emitting from 480V splitter with ends of conductor not properly housed. Conductors are required to be housed in suitable enclosures. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000524/09ecb057-0e2d-4b28-8d6e-27925f6dbdcc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7caa8e5_46da_4d97_ae43_a8ca3fc235b4
ELIN-715858-2016 | UW-475428-2016 | 12/1/2016 3:09:30 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | AC90 emitting from 480V splitter with ends of conductor not properly housed. Conductors are required to be housed in suitable enclosures. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | B.png | file://x:/photopub/docs/0000000524/354a5719-80e4-4d08-80b5-3ad9ace75303.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7caa8e5_46da_4d97_ae43_a8ca3fc235b4
ELIN-715858-2016 | UW-475428-2016 | 12/1/2016 3:09:30 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | AC90 emitting from 480V splitter with ends of conductor not properly housed. Conductors are required to be housed in suitable enclosures. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | D.png | file://x:/photopub/docs/0000000524/e9537f55-4584-42c3-88b7-ccc8d98d933f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7caa8e5_46da_4d97_ae43_a8ca3fc235b4
GAUP-705867-2016 | UW-468989-2016 | 11/24/2016 12:13:14 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA071 | Improperly sized gas piping or tubing for single/multiple appliances resulting in hazardous appliance operation | 4 | 4 | Line pressure regulator missing on the 1 inch black iron pipe gas line. Overpressure to the appliances could cause the appliances to fail. | 4 | Improperly sized gas piping or tubing for single/multiple appliances resulting in hazardous appliance operation | Meter_set_8716_Hofer_Drive.png | file://x:/photopub/docs/0000000521/2535e0b0-c06f-41b2-9fdf-4c27e339be6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d32f11e_5b15_41c2_b7ce_a4915217f92c
ELIN-559084-2016 | EL-349524-2016 | 10/24/2016 10:36:23 AM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | No light fixture or cover plate on 120v exterior light outlet, with exposed conductors in outlet box that may be energized from an interior wall switch, creating a risk of electrical shock. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Exterior_light_outlet_on_addition.png | file://x:/photopub/docs/0000000504/5fed3574-6a71-4d68-9595-35d3b8e1ccb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__60d8f8ba_8ff8_451c_afdb_856494521746
ELIN-678761-2016 | UW-447823-2016 | 10/5/2016 12:24:46 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | The main distribution has been located in a flood area. Neighbour has declared area floods annually in the fall . Supporting documents from survey company confirm that location is not suitable for distribution. If left in current location the hazard that will return will be shock, equipment damage, and thermal damage. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Water_damage_from_previous__flood_.png | file://x:/photopub/docs/0000000496/26e8ffa6-d2bc-4cce-a038-db831369234e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7f62d37_cc0a_470a_8608_cb3954e36b1a
ELIN-666923-2016 | EL-436307-2016 | 9/28/2016 12:54:49 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 2 | A sub-feed cable from the main service panel was entered into the compartment of the panel reserved for the entrance of the service conductors. The utility overcurrent protection for these conductors is not sufficient to protect an individual should one contact any uninsulated live parts within this compartment. To avoid this possibility, all branch circuit and sub-feed cables enter into the panel outside of the service conductor compartment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Sub-feed_cable_enters_service_compartment_of_panel_.png | file://x:/photopub/docs/0000000492/ba60044a-cec9-479c-a380-27b2f33c0411.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d334676_cd28_408b_872a_e02c8190ef75
GAIN-709023-2016 | GA-470293-2016 | 12/1/2016 1:25:49 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | Sidewall vent termination cannot terminate where a hazard is created by moisture or frost buildup. Moisture accumulation on stairs could lead to a slipping hazard. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Moisture_accumulation_from_vent_termination_.png | file://x:/photopub/docs/0000000524/bc97a1a4-6de1-41f0-8a15-4c3e474bc360.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b79f805f_147c_448c_8bc0_3ed3231f1321
GAIN-668502-2016 | GA-440439-2016 | 12/1/2016 1:34:21 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | Venting system non in compliance with the manufacturers installation instructions. Venting system will not operate properly when not installed as per instructions causing improper removal of flue products and improper combustion. | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Non_compliant_venting_system.png | file://x:/photopub/docs/0000000524/aebb07cf-f099-4718-a9f3-728eda784fce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__16c3b776_afe9_4cde_8398_3ac8505285bd
ELIN-713647-2016 | EL-473225-2016 | 12/1/2016 2:21:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | The 200 amp 120/240 volt pole mounted meter/disconnect does not have grounding installed, this presents an electrical shock hazard with the possibility of a potential difference between the identified conductor/ service equipment and to earth. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Sub-DISTRIBUTION_end_of_feeder.png | file://x:/photopub/docs/0000000524/2fdd88bd-8971-4b8e-a8f8-73dc090278d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd9b0a7b_8541_439a_91e5_01d3893d94b6
ELIN-713647-2016 | EL-473225-2016 | 12/1/2016 2:21:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | The 200 amp 120/240 volt pole mounted meter/disconnect does not have grounding installed, this presents an electrical shock hazard with the possibility of a potential difference between the identified conductor/ service equipment and to earth. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Main_switch.png | file://x:/photopub/docs/0000000524/3b6a00d6-6355-4df2-be69-ba4a870d2ceb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd9b0a7b_8541_439a_91e5_01d3893d94b6
ELIN-713647-2016 | EL-473225-2016 | 12/1/2016 2:21:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | The 200 amp 120/240 volt pole mounted meter/disconnect does not have grounding installed, this presents an electrical shock hazard with the possibility of a potential difference between the identified conductor/ service equipment and to earth. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Bond_screw_in_place_main_switch.png | file://x:/photopub/docs/0000000524/93bdb981-1e18-4d2e-9d6c-372dec1ddfac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd9b0a7b_8541_439a_91e5_01d3893d94b6
ELIN-713071-2016 | EL-437747-2016 | 11/30/2016 1:38:14 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Armoured cable are required to have the armor electrically and mechanically continuous when installed between equipment. This is required to maintain a bonding path on the conductive armour and to protect the conductors within the cable. This installation for a sub-feed cable installed during the renovation of a house had an armored cable that did not have the armour installed where the cable entered the house from the exterior to terminate at a sub-panel. This is a potential shock and fire hazard if the armour of the cable becomes energized or the conductors get mechanically damaged. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Armoured_cable_does_not_have_a_continuous_armor.png | file://x:/photopub/docs/0000000524/ed23bb67-2201-4011-bc9f-edad23c68b4e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fde902cf_c0b8_4182_bcb1_4ff7195e098f
GAOP-660175-2016 | 2172137 | 11/25/2016 2:11:40 PM | ASSESS: GA OP: Periodic | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | 1) All combustible materials are to be kept clear of a propane container at all times. 2) Permit owner has not maintained the weed and grass growth around the propane dispenser. 3) Weeds and long grasses can be ignited possibly subjecting the propane container to fire or heat that could lead to the venting of Propane gas. | 3 | Clearance to combustibles not maintained | Weed_growth_around_dispenser__.png | file://x:/photopub/docs/0000000522/c4adce49-ed52-46b4-a504-72684ad7845a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C1559FFD_43D1_451F_BFE7_7829E58590F0
GAOP-661121-2016 | 5435312 | 11/25/2016 2:51:00 PM | ASSESS: GA OP: Periodic | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | 1) long grasses and weed are to be kept clear of a propane container. 2) Permit holder has not maintained the weeds and grasses around the propane dispenser. 3) weeds and long grasses can be ignited and possibly subject the propane container to excessive heat that may cause the release and possible ignition of propane gas. | 3 | Clearance to combustibles not maintained | Weed_growth_around_propane_container.png | file://x:/photopub/docs/0000000522/923db948-6108-4493-8b60-a3b5946ec4cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__F8819A14_1C1C_4DA6_BB93_949FA09052AE
ELIN-689283-2016 | EL-434828-2016 | 10/24/2016 11:19:57 AM | ASSESS: EL: Final | png | #asFound | EL066 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Electrical_panel__electrical_panel_with_knockouts_missing_and_incorrect_panel_directory.png | file://x:/photopub/docs/0000000504/5d84da41-db67-4863-89ff-8e526bc3fced.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41eadf08_e242_4270_8813_f7524648b259
PROP-599966-2016 | 2224061 | 11/30/2016 10:07:59 AM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Limited travel of tensioning system. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Limited_travel_carriage.png | file://x:/photopub/docs/0000000524/a83b9f81-cec8-4dfb-bd05-266990657748.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22155642_30B7_4EAF_9D0F_8456087CC53E
PROP-599966-2016 | 2224061 | 11/30/2016 10:07:59 AM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Limited travel of tensioning system. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Counterweight_close_to_ground.png | file://x:/photopub/docs/0000000524/c8cf34e7-30bd-48d8-ac13-d61a10854869.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22155642_30B7_4EAF_9D0F_8456087CC53E
ELIN-678437-2016 | EL-416188-2016 | 10/6/2016 2:05:12 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Standard overcurrent device installed to protect receptacle circuit. Current code requires arc fault protection of receptacle circuits. Normal circuit breakers my not detect arcing fault. Undetected arc faults may increase wire failure thus resulting in fire and shock hazards to persons and property. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Standard_overcurrent_device_on_circuit_34_.png | file://x:/photopub/docs/0000000496/13b76ff9-fe4c-4fd6-845c-f02b18afdaf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f242facf_2131_45f9_b2a7_62873ab5c157
GAIN-675195-2016 | GA-398268-2016 | 10/21/2016 2:59:03 PM | ASSESS: GA: Final | png | #asFound | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 5 | Found gas line energized and feeding relief style regulator with vent not piped to a safe location outdoors. This creates the potential for raw gas to vent inside the home and could lead to an explosion. | 5 | Relief style regulator/device allowed to vent within building/confined space | Relief_reg.png | file://x:/photopub/docs/0000000504/04dda9ed-538c-4a32-ae48-a1635dbc2344.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d19353e6_9af6_4fb1_94c9_e4e7286c46d9
ELIN-679736-2016 | EL-374324-2016 | 10/7/2016 12:17:13 PM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | The breaker installed in the main service panel to supply a sub service in a new garage was not tested and approved for installation into that panel. This results in potential for failure of the equipment due to incompatibility leading to equipment damage or personal injury. | 3 | General Equipment is not approved for the specific use | Eaton_BR_breaker_in_Siemens_EQ_panel.png | file://x:/photopub/docs/0000000497/87068ff1-4bfb-42fb-831d-53122bd10819.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07c4295b_b190_4a01_a4db_aa3159d053b7
ELIN-713213-2016 | EL-466992-2016 | 11/29/2016 2:48:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | No protection plate in place to protect 3" PVC and ACWU raceways under meter base on outside wall. This is an equipment damage condition. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | No_protection_plate_in_place_to_protect_service_conductor_raceways.png | file://x:/photopub/docs/0000000523/b6a3e173-518a-4e3b-922f-d9955e562bc4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58fd2270_3903_4559_abf4_bfa4c6162ba1
PRIN-708645-2016 | PR-371859-2016 | 11/25/2016 1:23:17 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR041 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 1 | 1 | Conveyor structure to foundation anchor configuration consists of a 1/4" swaged eye connection. It was observed that the swage sleeve was compressed at 2 locations. The manufacture of the swage sleeve indicates that the sleeve is to be compressed at 4 points (rather than 2 points) along the length of the sleeve. There is a risk that the wire rope eyes may not have the structure strength required to meet the designers specification. | 1 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Swaged_cable_connection_compressed_at_2_locations.png | file://x:/photopub/docs/0000000522/626ae9df-45ad-4208-acbf-fbce42d89435.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e80bbe5d_125b_4d9a_8090_c145a0f3e3ed
PROP-599965-2016 | 2224060 | 11/30/2016 3:41:09 PM | ASSESS: PR OP: RAP | png | #asFound | PR035 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 |  | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Blue_2016_loadtest.png | file://x:/photopub/docs/0000000524/11c676c7-a28c-4239-8e32-be69d2edeaec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__446DC429_2C38_4B67_8DF8_FBE61AB023D8
ELHE-681737-2016 | HE-450143-2016 | 10/11/2016 3:40:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | The 15 amp 120 volt lighting circuits mounted to the existing 6' wooden fence are coming apart due to the wooden fence falling apart, this is creating a shock hazard | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Fence_3.png | file://x:/photopub/docs/0000000498/4851355e-81df-44f2-b4d8-3db5961eae15.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd069446_6f93_4545_8b0d_cff1ab735ab2
ELHE-681737-2016 | HE-450143-2016 | 10/11/2016 3:40:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | The 15 amp 120 volt lighting circuits mounted to the existing 6' wooden fence are coming apart due to the wooden fence falling apart, this is creating a shock hazard | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Fence_2.png | file://x:/photopub/docs/0000000498/01c2b856-4e5e-4bba-acfb-80c11980d706.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd069446_6f93_4545_8b0d_cff1ab735ab2
ELHE-681737-2016 | HE-450143-2016 | 10/11/2016 3:40:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | The 15 amp 120 volt lighting circuits mounted to the existing 6' wooden fence are coming apart due to the wooden fence falling apart, this is creating a shock hazard | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Fence_5.png | file://x:/photopub/docs/0000000498/f26a902c-2bf3-4e62-aa14-a465ec0823b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd069446_6f93_4545_8b0d_cff1ab735ab2
ELHE-681737-2016 | HE-450143-2016 | 10/11/2016 3:40:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | The 15 amp 120 volt lighting circuits mounted to the existing 6' wooden fence are coming apart due to the wooden fence falling apart, this is creating a shock hazard | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Fence_1.png | file://x:/photopub/docs/0000000498/b7ada15f-8007-4526-b54d-2361d5856dd3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd069446_6f93_4545_8b0d_cff1ab735ab2
ELHE-681737-2016 | HE-450143-2016 | 10/11/2016 3:40:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | The 15 amp 120 volt lighting circuits mounted to the existing 6' wooden fence are coming apart due to the wooden fence falling apart, this is creating a shock hazard | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Fence_4.png | file://x:/photopub/docs/0000000498/5df5b6c5-3da8-4d0c-b9eb-ee8db2f9d2fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd069446_6f93_4545_8b0d_cff1ab735ab2
ELIN-708485-2016 | EL-431152-2016 | 11/29/2016 3:13:21 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not approved to be used as permanent building wiring and are not to be installed in openings through floors and walls. In this installation at a building to be used for educational purposes, a sump pump was installed below grade. The flexible cord for the sump pump was run through an opening through the floor and up inside the exterior wall. The cord then exited the wall through an opening and was plugged into a 15 amp, 120V receptacle. The method in which the cord was installed could cause damage to the insulation of the conductors which could create a potential fire hazard with in the building. | 4 | Conductors, Misuse of flexible cords. | Sump_pump_connection.png | file://x:/photopub/docs/0000000523/f51a9b77-f2c2-4ee0-84d6-2a66f4d6ceca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29569e72_da50_479a_8148_9f12692cc6b6
GAIN-715011-2016 | GA-471313-2016 | 11/30/2016 3:05:00 PM | ASSESS: GA: Rough-In | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | The as found condition was a combined gas range\oven installed within the minimum side wall clearance to combustible wood cabinets. The as found hazard is heat transfer from the oven side wall or range top can lead to pyrolysis of the wood and potential fire when the minimum clearances are not maintained. | 3 | Clearance to combustible not met | Instalation_clearances.png | file://x:/photopub/docs/0000000523/e212f1d9-b6a5-4f38-99c1-9df7671da840.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30fccda9_0207_4f6b_805f_155d3017f894
GAIN-695975-2016 | GA-433231-2016 | 11/4/2016 8:37:05 AM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Physical protection of piping or tubing absent. Copper tubing must be protected from damage when passing through a masonry wall. | 2 | Physical protection of piping and tubing absent. | Copper_tunbing_passing_through_a_masonry_wall_with_no_protection.png | file://x:/photopub/docs/0000000511/ef3d3a0b-a628-472a-a85b-b21099be9c78.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__870f931a_044f_4846_835e_f624f7e0dbe9
BPVOP-671245-2016 | 2269311 | 9/26/2016 4:04:24 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | This boiler never had a low water fuel cut off installed, also it never had an emergency shut-down switch installed. Combustion air supply grille was found to be choked with debris. Masonry chimney has a 12 inch round hole that should have been blocked off when the flue duct was removed. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | DHW_Tube_Bundle_Gasket_Corrosion.png | file://x:/photopub/docs/0000000491/84b4f392-781d-46df-9998-1a2e00ea19a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbe44191_985a_4d93_8f7b_5b55220499d9
BPVOP-671245-2016 | 2269311 | 9/26/2016 4:04:24 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | This boiler never had a low water fuel cut off installed, also it never had an emergency shut-down switch installed. Combustion air supply grille was found to be choked with debris. Masonry chimney has a 12 inch round hole that should have been blocked off when the flue duct was removed. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Furnace_Floor_Refractory_Debris.png | file://x:/photopub/docs/0000000491/814372cb-8f1d-40e3-a46d-cd47fa8c1662.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbe44191_985a_4d93_8f7b_5b55220499d9
BPVOP-671245-2016 | 2269311 | 9/26/2016 4:04:24 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | This boiler never had a low water fuel cut off installed, also it never had an emergency shut-down switch installed. Combustion air supply grille was found to be choked with debris. Masonry chimney has a 12 inch round hole that should have been blocked off when the flue duct was removed. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | External_Piping_Corrosion.png | file://x:/photopub/docs/0000000491/3d78ee9e-a986-4c30-b88e-a65232b6848d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbe44191_985a_4d93_8f7b_5b55220499d9
BPVOP-671245-2016 | 2269311 | 9/26/2016 4:04:24 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | This boiler never had a low water fuel cut off installed, also it never had an emergency shut-down switch installed. Combustion air supply grille was found to be choked with debris. Masonry chimney has a 12 inch round hole that should have been blocked off when the flue duct was removed. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_Nameplate.png | file://x:/photopub/docs/0000000491/d125bb6e-bfb5-4e9d-9752-dc160cd291c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbe44191_985a_4d93_8f7b_5b55220499d9
ELIN-692813-2016 | EL-457011-2016 | 11/9/2016 1:53:57 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | A new 100 amp 240 volt service for commercial use has been installed. The utility meter has been secured to the pole lacking approved outdoor mounting hardware designed to provide solid mounting and prevent or prohibit entry of water into equipment. Equipment can become damaged by water entry or become loose on the pole leading to property damage or injury to persons. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Meter_secured_to_pole_with_screws__approved_outdoor_hardware_not_provided.png | file://x:/photopub/docs/0000000514/94f1170f-aaf7-472f-9ebc-0e2044a2a313.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__787ccfa2_52d2_4fab_b070_6a928b162152
ELIN-709389-2016 | EL-454730-2016 | 11/25/2016 1:55:25 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Standard type receptacle installed within 1.5 meters of a sink or wash basin. The receptacle requirements for this location is that the receptacle has to be GFCI protected, in the case of a splash or stream of water a GFCI receptacle would recognize an unbalanced situation in the circuit and trip the receptacle to de-energize it. Standard receptacles do not detect this unbalanced circuit situation and may cause a risk of fire and shock to property and persons | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Standard_receptacle_installed_within_one_and_a_half_meters_of_a_sink.png | file://x:/photopub/docs/0000000522/30aaec64-4534-44be-ab2f-b188984adf7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cefc9200_a05f_4280_a679_da703c33450d
ELIN-709919-2016 | EL-187283-2014 | 11/25/2016 12:46:13 PM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Main distribution panel breaker locations do not have fillers or spare breakers in empty locations. Panel fillers or spare breakers protect accidental contact with energized bussing inside the panel. Accidental contact with energized equipment may cause shock and fire to persons and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Empty_breaker_locations_not_filled_in_energized_panel.png | file://x:/photopub/docs/0000000522/087e3b4d-dc74-4177-848e-4242c83cca1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9779d8bd_2ca9_43b5_8022_c480eb9c2ec0
GAIN-697401-2016 | GA-462863-2016 | 11/14/2016 3:36:34 PM | ASSESS: GA: Final | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | Installation clearances not maintained for propane cylinder. 10 ft clearance to source of ignition must be maintained to prevent ignition of gas in the event propane leak. | 2 | Installation clearances or set backs to propane containers not met | Clearance_to_source_of_ignition_not_maintained.png | file://x:/photopub/docs/0000000516/f266b19f-f7fc-4d2a-b9e1-26ab53defcab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55770d9c_887b_4839_8446_90c0dbf1a9f7
ELIN-701371-2016 | EL-466028-2016 | 11/14/2016 3:07:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical equipment intended and approved for installation in dry locations is not permitted to get wet. Water on or inside electrical equipment intended for installation in dry locations can damage equipment by causing it to rust, corrode, short out and fail. This installation has a new 200A 120/240V service panel, main breaker, 15A branch circuit breakers, and 15A, 120V ground fault circuit interrupter (GFCI) receptacles that are installed in a new house under construction. The roofing material has not been installed on the house yet and rain water has entered the house and the electrical equipment. This is a potential shock and fire hazard if the wetted electrical equipment is energized. Circuit breakers and GFCI receptacles that have been wet may be damaged and fail to operate correctly at the time they are energized or in the future due to corrosion, rust, and internal component damage. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Service_panel_in_basement.png | file://x:/photopub/docs/0000000515/e13db304-3ad2-448d-a617-eb72b5c750d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1dc3170_0164_4cb5_85d3_16ea4d1f8d13
ELIN-701371-2016 | EL-466028-2016 | 11/14/2016 3:07:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical equipment intended and approved for installation in dry locations is not permitted to get wet. Water on or inside electrical equipment intended for installation in dry locations can damage equipment by causing it to rust, corrode, short out and fail. This installation has a new 200A 120/240V service panel, main breaker, 15A branch circuit breakers, and 15A, 120V ground fault circuit interrupter (GFCI) receptacles that are installed in a new house under construction. The roofing material has not been installed on the house yet and rain water has entered the house and the electrical equipment. This is a potential shock and fire hazard if the wetted electrical equipment is energized. Circuit breakers and GFCI receptacles that have been wet may be damaged and fail to operate correctly at the time they are energized or in the future due to corrosion, rust, and internal component damage. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Service_panel_wet_inside_.png | file://x:/photopub/docs/0000000515/a26ed1e3-d3ad-480a-b5b6-35b8f39c9924.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1dc3170_0164_4cb5_85d3_16ea4d1f8d13
ELIN-701371-2016 | EL-466028-2016 | 11/14/2016 3:07:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical equipment intended and approved for installation in dry locations is not permitted to get wet. Water on or inside electrical equipment intended for installation in dry locations can damage equipment by causing it to rust, corrode, short out and fail. This installation has a new 200A 120/240V service panel, main breaker, 15A branch circuit breakers, and 15A, 120V ground fault circuit interrupter (GFCI) receptacles that are installed in a new house under construction. The roofing material has not been installed on the house yet and rain water has entered the house and the electrical equipment. This is a potential shock and fire hazard if the wetted electrical equipment is energized. Circuit breakers and GFCI receptacles that have been wet may be damaged and fail to operate correctly at the time they are energized or in the future due to corrosion, rust, and internal component damage. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Water_on_floor_above_panel.png | file://x:/photopub/docs/0000000515/6d161995-7b7d-459f-8164-293830ddd7c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1dc3170_0164_4cb5_85d3_16ea4d1f8d13
ELIN-701371-2016 | EL-466028-2016 | 11/14/2016 3:07:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical equipment intended and approved for installation in dry locations is not permitted to get wet. Water on or inside electrical equipment intended for installation in dry locations can damage equipment by causing it to rust, corrode, short out and fail. This installation has a new 200A 120/240V service panel, main breaker, 15A branch circuit breakers, and 15A, 120V ground fault circuit interrupter (GFCI) receptacles that are installed in a new house under construction. The roofing material has not been installed on the house yet and rain water has entered the house and the electrical equipment. This is a potential shock and fire hazard if the wetted electrical equipment is energized. Circuit breakers and GFCI receptacles that have been wet may be damaged and fail to operate correctly at the time they are energized or in the future due to corrosion, rust, and internal component damage. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Front_of_house_.png | file://x:/photopub/docs/0000000515/6e51b1fe-ff6f-49f2-979d-e4aa430f2d17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1dc3170_0164_4cb5_85d3_16ea4d1f8d13
ELIN-701371-2016 | EL-466028-2016 | 11/14/2016 3:07:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical equipment intended and approved for installation in dry locations is not permitted to get wet. Water on or inside electrical equipment intended for installation in dry locations can damage equipment by causing it to rust, corrode, short out and fail. This installation has a new 200A 120/240V service panel, main breaker, 15A branch circuit breakers, and 15A, 120V ground fault circuit interrupter (GFCI) receptacles that are installed in a new house under construction. The roofing material has not been installed on the house yet and rain water has entered the house and the electrical equipment. This is a potential shock and fire hazard if the wetted electrical equipment is energized. Circuit breakers and GFCI receptacles that have been wet may be damaged and fail to operate correctly at the time they are energized or in the future due to corrosion, rust, and internal component damage. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Main_breaker_and_terminations_wet.png | file://x:/photopub/docs/0000000515/64d9f4e1-f47f-4be7-9c42-73ad25ddfadb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1dc3170_0164_4cb5_85d3_16ea4d1f8d13
ELIN-701371-2016 | EL-466028-2016 | 11/14/2016 3:07:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical equipment intended and approved for installation in dry locations is not permitted to get wet. Water on or inside electrical equipment intended for installation in dry locations can damage equipment by causing it to rust, corrode, short out and fail. This installation has a new 200A 120/240V service panel, main breaker, 15A branch circuit breakers, and 15A, 120V ground fault circuit interrupter (GFCI) receptacles that are installed in a new house under construction. The roofing material has not been installed on the house yet and rain water has entered the house and the electrical equipment. This is a potential shock and fire hazard if the wetted electrical equipment is energized. Circuit breakers and GFCI receptacles that have been wet may be damaged and fail to operate correctly at the time they are energized or in the future due to corrosion, rust, and internal component damage. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Water_collecting_on_sub-floor_above_service_panel.png | file://x:/photopub/docs/0000000515/236e51f1-0c99-4432-9a2b-507aaff990cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1dc3170_0164_4cb5_85d3_16ea4d1f8d13
ELIN-701371-2016 | EL-466028-2016 | 11/14/2016 3:07:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical equipment intended and approved for installation in dry locations is not permitted to get wet. Water on or inside electrical equipment intended for installation in dry locations can damage equipment by causing it to rust, corrode, short out and fail. This installation has a new 200A 120/240V service panel, main breaker, 15A branch circuit breakers, and 15A, 120V ground fault circuit interrupter (GFCI) receptacles that are installed in a new house under construction. The roofing material has not been installed on the house yet and rain water has entered the house and the electrical equipment. This is a potential shock and fire hazard if the wetted electrical equipment is energized. Circuit breakers and GFCI receptacles that have been wet may be damaged and fail to operate correctly at the time they are energized or in the future due to corrosion, rust, and internal component damage. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Service_panel_.png | file://x:/photopub/docs/0000000515/74c2020d-3606-42fb-a78d-e2e741792684.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1dc3170_0164_4cb5_85d3_16ea4d1f8d13
ELIN-669696-2016 | EL-424072-2016 | 9/28/2016 4:36:57 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Permit holder is residing in dwelling while construction is on going, several covers missing on electrical outlets increases the possibility of a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outlets_not_protected_.png | file://x:/photopub/docs/0000000491/04832058-c8b9-48a2-a1ef-3a9f136fc533.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__addfa22b_a4a1_465a_b53d_9539b3e4e096
ELIN-669696-2016 | EL-424072-2016 | 9/28/2016 4:36:57 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Permit holder is residing in dwelling while construction is on going, several covers missing on electrical outlets increases the possibility of a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Gas_range_has_no_120_volt_receptacle.png | file://x:/photopub/docs/0000000491/4e76aa8c-307f-475f-b928-0bb5380d7908.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__addfa22b_a4a1_465a_b53d_9539b3e4e096
ELIN-693676-2016 | EL-459273-2016 | 11/2/2016 2:14:27 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 3 | This assessment found a potential fire hazard with conductors being too short in the device boxes. When affixing the devices during the final stage of construction, stress on the connection due to the shortened length of wire could cause excessive heat at the joint. | 3 | Conductors, No expansion joint or not installed correctly. | Conductors_length_.png | file://x:/photopub/docs/0000000510/ee11ad51-5dda-40fd-9c7d-0bb6c5fa02ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9cff6e00_e421_4583_a155_78552d46f654
ELIN-664248-2016 | EL-438082-2016 | 9/20/2016 7:14:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Armoured cable concealed in stud walls is required to be installed a minimum distance of 32mm from the nearest edge of the framing member or mechanical protection is to be provided. This requirement is to protect the concealed cable from penetration from screws and nails. During a a service inspection for a 200A, 120/240V service panel in a single family dwelling, the safety officer found the armoured service cable underneath the panel was installed within 15 mm of the nearest edge of the framing member with no mechanical protection. With no mechanical protection, there is the potential for mechanical damage from screws or nails to the cable. If the cable is energized, this mechanical damage could result in a shock hazard to persons, a fire hazard within the walls of the structure, or electrical equipment failure. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Panel_in_Garage.png | file://x:/photopub/docs/0000000488/dc090d97-1d0f-4c3d-b135-3d9517e3f73d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6379dc5_eb9f_4804_bfec_b1fdc7a099eb
ELIN-664248-2016 | EL-438082-2016 | 9/20/2016 7:14:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Armoured cable concealed in stud walls is required to be installed a minimum distance of 32mm from the nearest edge of the framing member or mechanical protection is to be provided. This requirement is to protect the concealed cable from penetration from screws and nails. During a a service inspection for a 200A, 120/240V service panel in a single family dwelling, the safety officer found the armoured service cable underneath the panel was installed within 15 mm of the nearest edge of the framing member with no mechanical protection. With no mechanical protection, there is the potential for mechanical damage from screws or nails to the cable. If the cable is energized, this mechanical damage could result in a shock hazard to persons, a fire hazard within the walls of the structure, or electrical equipment failure. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Service_cable_not_protected.png | file://x:/photopub/docs/0000000488/f3360636-5065-4b40-8e09-c428b942fe44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6379dc5_eb9f_4804_bfec_b1fdc7a099eb
ELIN-664248-2016 | EL-438082-2016 | 9/20/2016 7:14:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Armoured cable concealed in stud walls is required to be installed a minimum distance of 32mm from the nearest edge of the framing member or mechanical protection is to be provided. This requirement is to protect the concealed cable from penetration from screws and nails. During a a service inspection for a 200A, 120/240V service panel in a single family dwelling, the safety officer found the armoured service cable underneath the panel was installed within 15 mm of the nearest edge of the framing member with no mechanical protection. With no mechanical protection, there is the potential for mechanical damage from screws or nails to the cable. If the cable is energized, this mechanical damage could result in a shock hazard to persons, a fire hazard within the walls of the structure, or electrical equipment failure. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Service_cable_close_up.png | file://x:/photopub/docs/0000000488/cde7f011-9eb7-4035-a836-62c28631572b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6379dc5_eb9f_4804_bfec_b1fdc7a099eb
ELIN-709068-2016 | EL-420413-2016 | 11/24/2016 1:43:08 PM | ASSESS: EL: Final | png | #asFound | EL179 | General Construction Indoor: Inadequate spacing from walls for transformer. | 4 | 4 | Transformer is too close to combustible wall surface. This is a possible fire hazard. | 4 | General Construction Indoor: Inadequate spacing from walls for transformer. | Load_centres.png | file://x:/photopub/docs/0000000521/2b4ab331-5dc9-480b-83f3-2d9d7d3637d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f21adce4_df5e_432c_89ac_f20b1469660e
ELIN-709068-2016 | EL-420413-2016 | 11/24/2016 1:43:08 PM | ASSESS: EL: Final | png | #asFound | EL179 | General Construction Indoor: Inadequate spacing from walls for transformer. | 4 | 4 | Transformer is too close to combustible wall surface. This is a possible fire hazard. | 4 | General Construction Indoor: Inadequate spacing from walls for transformer. | Transformer.png | file://x:/photopub/docs/0000000521/3a22cf23-ef25-414d-925f-1043105160eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f21adce4_df5e_432c_89ac_f20b1469660e
ELIN-701371-2016 | EL-466028-2016 | 11/14/2016 3:07:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical equipment intended and approved for installation in dry locations is not permitted to get wet. Water on or inside electrical equipment intended for installation in dry locations can damage equipment by causing it to rust, corrode, short out and fail. This installation has a new 200A 120/240V service panel, main breaker, 15A branch circuit breakers, and 15A, 120V ground fault circuit interrupter (GFCI) receptacles that are installed in a new house under construction. The roofing material has not been installed on the house yet and rain water has entered the house and the electrical equipment. This is a potential shock and fire hazard if the wetted electrical equipment is energized. Circuit breakers and GFCI receptacles that have been wet may be damaged and fail to operate correctly at the time they are energized or in the future due to corrosion, rust, and internal component damage. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Service_panel_wet_inside.png | file://x:/photopub/docs/0000000515/ef656bff-8664-4de4-88e6-297aab95545c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1dc3170_0164_4cb5_85d3_16ea4d1f8d13
ELIN-701371-2016 | EL-466028-2016 | 11/14/2016 3:07:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical equipment intended and approved for installation in dry locations is not permitted to get wet. Water on or inside electrical equipment intended for installation in dry locations can damage equipment by causing it to rust, corrode, short out and fail. This installation has a new 200A 120/240V service panel, main breaker, 15A branch circuit breakers, and 15A, 120V ground fault circuit interrupter (GFCI) receptacles that are installed in a new house under construction. The roofing material has not been installed on the house yet and rain water has entered the house and the electrical equipment. This is a potential shock and fire hazard if the wetted electrical equipment is energized. Circuit breakers and GFCI receptacles that have been wet may be damaged and fail to operate correctly at the time they are energized or in the future due to corrosion, rust, and internal component damage. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Service_panel_wet_inside__.png | file://x:/photopub/docs/0000000515/7b033e2a-d318-474c-a5cd-53db89cb2b3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1dc3170_0164_4cb5_85d3_16ea4d1f8d13
ELIN-669696-2016 | EL-424072-2016 | 9/28/2016 4:36:57 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Permit holder is residing in dwelling while construction is on going, several covers missing on electrical outlets increases the possibility of a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_conductors_near_bathtub.png | file://x:/photopub/docs/0000000491/d4cfa777-1d5d-4ecf-85cb-d9ba9e04fca1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__addfa22b_a4a1_465a_b53d_9539b3e4e096
ELIN-669696-2016 | EL-424072-2016 | 9/28/2016 4:36:57 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Permit holder is residing in dwelling while construction is on going, several covers missing on electrical outlets increases the possibility of a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | AC_90_without_bushings.png | file://x:/photopub/docs/0000000491/c4af85d5-e6a9-4b2a-b1e1-1ed2b181b61b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__addfa22b_a4a1_465a_b53d_9539b3e4e096
ELIN-645347-2016 | EL-424436-2016 | 9/28/2016 5:45:40 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | Bond bushing was not installed , this would not ensure proper bonding leaving a increased risk of thermal or shock hazards. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Main_service.png | file://x:/photopub/docs/0000000491/339c267c-d338-402d-a126-ad52e2d8e3d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e859f79c_7975_40e5_8423_bcf33fd78c5c
ELIN-676637-2016 | EL-441608-2016 | 10/4/2016 7:33:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumers service conductors are beyond 1.5 meters inside of building. This could be a fire/shock hazard if these conductors were to be pierced or broken due to possible nails or screws from construction. These conductors are over fused by the supply service, it would take a long time for the fuse to interrupt these conductors if they were compromised. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Beyond_1_5_metes_2.png | file://x:/photopub/docs/0000000495/1e844082-3df7-44a3-abc5-be45602bad44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8450995f_8512_457e_b93d_85cb4a539be7
ELIN-676637-2016 | EL-441608-2016 | 10/4/2016 7:33:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumers service conductors are beyond 1.5 meters inside of building. This could be a fire/shock hazard if these conductors were to be pierced or broken due to possible nails or screws from construction. These conductors are over fused by the supply service, it would take a long time for the fuse to interrupt these conductors if they were compromised. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Beyond_1_5_meters_.png | file://x:/photopub/docs/0000000495/28e48434-9f9c-438f-928e-6173afb95b5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8450995f_8512_457e_b93d_85cb4a539be7
ELIN-671168-2016 | EL-423128-2016 | 9/27/2016 10:19:06 AM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 1 | Incomplete electrical system work. Inspection called to early. No electrical energized and available for contact. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Sales_counter.png | file://x:/photopub/docs/0000000491/377c6bd8-100d-4ec6-8dba-e5e751663398.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48d5396e_1ab1_4e90_8d1b_a0608eeec6b7
ELIN-671168-2016 | EL-423128-2016 | 9/27/2016 10:19:06 AM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 1 | Incomplete electrical system work. Inspection called to early. No electrical energized and available for contact. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Counter_2.png | file://x:/photopub/docs/0000000491/dd0483bd-6e52-423f-a281-91e8ed9b75cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48d5396e_1ab1_4e90_8d1b_a0608eeec6b7
ELIN-674513-2016 | EL-439797-2016 | 10/3/2016 1:21:04 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Live plug pins can shock a person. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Plug.png | file://x:/photopub/docs/0000000494/ec3fd3e4-5a67-498c-afb9-d481a79014ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0f7da48_679c_427a_bd09_6df6bc272898
ELIN-675585-2016 | UW-445790-2016 | 9/30/2016 3:09:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Secondary private pole has failed, the pole set in 1964 has excessive rot and is likely broken at the base. This is a fire and shock hazard. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | B.png | file://x:/photopub/docs/0000000494/22010e9a-b277-41de-86cb-8b5c1c1957b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f90200c1_e861_4f43_bba0_8a283ada1c2e
ELIN-675585-2016 | UW-445790-2016 | 9/30/2016 3:09:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Secondary private pole has failed, the pole set in 1964 has excessive rot and is likely broken at the base. This is a fire and shock hazard. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | A.png | file://x:/photopub/docs/0000000494/dbdad731-b27c-4239-8f32-9def2ec2a1b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f90200c1_e861_4f43_bba0_8a283ada1c2e
ELIN-675585-2016 | UW-445790-2016 | 9/30/2016 3:09:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Secondary private pole has failed, the pole set in 1964 has excessive rot and is likely broken at the base. This is a fire and shock hazard. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | C.png | file://x:/photopub/docs/0000000494/d898eeaf-4aa7-4335-a143-23ba7b8d8e28.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f90200c1_e861_4f43_bba0_8a283ada1c2e
BPVOP-667499-2016 | 4116224 | 9/20/2016 10:26:55 AM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All safety relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on a 30 psi hot water boiler for the last 8 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 2008_safety_valve_.png | file://x:/photopub/docs/0000000487/169771e3-7351-4f06-bcbb-3be73436ec51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7847652_c76c_412d_a687_33db6b2f41ea
ELOP-655623-2016 | 4749499 | 9/27/2016 12:27:51 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | During a routine Operating Permit assessment at a waste water treatment plant, a 120/240volt 200amp service pole was observed in a defective state without a guy-wire support assembly in place. This could lead to a thermal effect. Pic attached. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Power_pole_leaning.png | file://x:/photopub/docs/0000000493/f5f5540c-20ed-4fe3-9184-34355f26f12a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7AF56BFA_4E1C_4D50_8DEA_DFBE23A825D1
ELOP-655623-2016 | 4749499 | 9/27/2016 12:27:51 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | During a routine Operating Permit assessment at a waste water treatment plant, a 120/240volt 200amp service pole was observed in a defective state without a guy-wire support assembly in place. This could lead to a thermal effect. Pic attached. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Panel_filler_missing_.png | file://x:/photopub/docs/0000000493/19b1537d-8bb7-4ba3-b41c-f1d52b3b2188.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7AF56BFA_4E1C_4D50_8DEA_DFBE23A825D1
ELIN-675251-2016 | EL-437324-2016 | 10/4/2016 3:10:05 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Meter.png | file://x:/photopub/docs/0000000494/298824e3-b264-4ef3-9643-0049676ab17d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f26e758f_2738_470e_83ed_120d45378599
ELIN-675251-2016 | EL-437324-2016 | 10/4/2016 3:10:05 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Panel.png | file://x:/photopub/docs/0000000494/23179645-5e1c-4c6f-89b8-84e4c38eb9e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f26e758f_2738_470e_83ed_120d45378599
ELIN-681081-2016 | EL-449751-2016 | 10/11/2016 4:33:33 PM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | In a residential electrical service the grounded service conductor is required to be connected to a ground electrode at the supply side of the service disconnect only. This is to prevent neutral currents from circulating through the bonding system and to carry any unbalanced fault currents back to the source. In this installation, a 200 amp service was installed in a residential dwelling. The ground conductor for the new panel was connected to a bonding lug instead of the neutral lug on the service side of the panel. If an electrical fault was to occur, there is the potential for unbalanced fault currents to flow through the metal of the service panel and create a shock hazard for any persons in contact with the panel. | 4 | Installation Grounding; conductor is not continuous. | Ground_on_bonding_lug.png | file://x:/photopub/docs/0000000498/d621db08-da67-44c8-928a-4504b38b5fab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb273e38_3890_4448_b019_6dbb850d33a5
ELIN-681081-2016 | EL-449751-2016 | 10/11/2016 4:33:33 PM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | In a residential electrical service the grounded service conductor is required to be connected to a ground electrode at the supply side of the service disconnect only. This is to prevent neutral currents from circulating through the bonding system and to carry any unbalanced fault currents back to the source. In this installation, a 200 amp service was installed in a residential dwelling. The ground conductor for the new panel was connected to a bonding lug instead of the neutral lug on the service side of the panel. If an electrical fault was to occur, there is the potential for unbalanced fault currents to flow through the metal of the service panel and create a shock hazard for any persons in contact with the panel. | 4 | Installation Grounding; conductor is not continuous. | Interior_of_panel.png | file://x:/photopub/docs/0000000498/baf188db-6c02-4ad2-868f-eaf948816c12.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb273e38_3890_4448_b019_6dbb850d33a5
GAIN-683280-2016 | GA-431108-2016 | 10/14/2016 2:30:28 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Tubing must be protected when passing through a masonry wall, damage can occur to the tubing from the masonry. | 2 | Physical protection of piping and tubing absent. | Unprotected_copper_tube_through_masonry_.png | file://x:/photopub/docs/0000000501/6d67fa2e-d8f8-47cd-8826-0f59b8b234fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d99948e7_acba_472f_ae39_6022afb5f890
ELIN-705501-2016 | EL-352988-2016 | 11/17/2016 12:45:11 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacles and switches installed in bathrooms are required to be located 1 meter horizontally where practicable away from the location where water will be present while the tub or shower is in use. This is required to make it less likely for the occupant to operate switches or plug portable equipment into the receptacle while standing in the tub or shower. This installation for a new row home under construction has a 15A 120V receptacle located on the wall above the tub intended for a TV to plug into. This is a potential shock hazard if persons use the receptacle while in the tub. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | New_three_unit_row_house_under_construction.png | file://x:/photopub/docs/0000000518/47929305-cecc-491f-9284-8fbd9e88bd34.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd75aec3_40a3_42ec_b551_7e9c406d09ff
ELIN-705501-2016 | EL-352988-2016 | 11/17/2016 12:45:11 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacles and switches installed in bathrooms are required to be located 1 meter horizontally where practicable away from the location where water will be present while the tub or shower is in use. This is required to make it less likely for the occupant to operate switches or plug portable equipment into the receptacle while standing in the tub or shower. This installation for a new row home under construction has a 15A 120V receptacle located on the wall above the tub intended for a TV to plug into. This is a potential shock hazard if persons use the receptacle while in the tub. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Receptacle_installed_above_the_tub_for_a_TV__.png | file://x:/photopub/docs/0000000518/c521de96-b3d8-427b-ba9d-8ad1e4594723.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd75aec3_40a3_42ec_b551_7e9c406d09ff
ELIN-705501-2016 | EL-352988-2016 | 11/17/2016 12:45:11 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacles and switches installed in bathrooms are required to be located 1 meter horizontally where practicable away from the location where water will be present while the tub or shower is in use. This is required to make it less likely for the occupant to operate switches or plug portable equipment into the receptacle while standing in the tub or shower. This installation for a new row home under construction has a 15A 120V receptacle located on the wall above the tub intended for a TV to plug into. This is a potential shock hazard if persons use the receptacle while in the tub. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Receptacle_installed_above_the_tub_for_a_TV.png | file://x:/photopub/docs/0000000518/caf3c3a2-aebd-4b7a-ac24-6e1e84dcb1a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd75aec3_40a3_42ec_b551_7e9c406d09ff
ELIN-675970-2016 | EL-442748-2016 | 10/4/2016 2:31:48 PM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | Junction box cover not installed. Conductors in junction box are exposed to accidental contact, providing a risk of shock and fire to persons and property. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Covers_or_Luminaires_not_installed_at_time_of_final__.png | file://x:/photopub/docs/0000000495/26235a49-248c-4b9a-af54-586bf2788ea6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc79f1b2_b98f_4f6c_854e_c1c09afecc52
GAIN-664484-2016 | GA-386083-2016 | 9/21/2016 9:57:43 AM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Found built in BBQ installed in a combustible surround. This could lead to a fire hazard. | 3 | Clearance to combustible not met | Bbq_combustible_surround.png | file://x:/photopub/docs/0000000488/4b2f58a4-e228-4659-bc32-e330afd9d88d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb67faf6_145f_4de3_abd5_b9d47ee1a63d
PROP-688222-2016 | 2224042 | 10/20/2016 10:25:57 PM | ASSESS: PR OP: Annual | png | #asFound | PR036 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 1 | 1 | Chair and/or passengers may get hooked on other side of handrail. | 1 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Chair_clearance_of_railing.png | file://x:/photopub/docs/0000000504/53d5bdce-af79-4b4a-aa42-a56127d59094.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e73ac86_b90b_4149_a576_ec8c71f58c86
PROP-688222-2016 | 2224042 | 10/20/2016 10:25:57 PM | ASSESS: PR OP: Annual | png | #asFound | PR036 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 1 | 1 | Chair and/or passengers may get hooked on other side of handrail. | 1 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | No_front_carriage_switch.png | file://x:/photopub/docs/0000000504/f72ad78b-f12c-4a09-8362-c3eaa55f5a0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e73ac86_b90b_4149_a576_ec8c71f58c86
ELIN-706120-2016 | EL-447921-2016 | 11/18/2016 6:05:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | 200 amp, 120/240 volt main distribution has grounding conductor passing through service conductor compartment to be terminated. This is a cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Ground_conductor_terminated_outside_of_service_conductor_compartment.png | file://x:/photopub/docs/0000000518/7a6b039c-e86a-44db-af20-052bea4d7225.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f13d4725_7b36_4d4c_a94d_47c05cc818d2
ELIN-703594-2016 | EL-467096-2016 | 11/25/2016 12:59:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The temporary service using a 100 amp 120/240 volt rated loadcentre does not include overcurrent (main breaker) protection exposing the panel bussing to a fault in excess of equipment rating, this is an equipment damage issue | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Non_service_rated_label.png | file://x:/photopub/docs/0000000521/ba36235c-11de-44a8-9592-a442e6e68d07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ed21a08_1b28_405b_8337_1b15811bb486
ELIN-703594-2016 | EL-467096-2016 | 11/25/2016 12:59:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The temporary service using a 100 amp 120/240 volt rated loadcentre does not include overcurrent (main breaker) protection exposing the panel bussing to a fault in excess of equipment rating, this is an equipment damage issue | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Loadcentre.png | file://x:/photopub/docs/0000000521/739d56b6-bf4e-4b39-ba50-89f3ac93cde9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ed21a08_1b28_405b_8337_1b15811bb486
GAHE-693243-2016 | HE-459107-2016 | 10/28/2016 11:43:28 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Piping.png | file://x:/photopub/docs/0000000507/7c5a8aae-f4de-4d59-b974-a274c5a29bfc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96876905_616e_4ff2_bfe6_0fb106d2ae2c
GAHE-693243-2016 | HE-459107-2016 | 10/28/2016 11:43:28 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Piping_not_supported.png | file://x:/photopub/docs/0000000507/90d8cad1-0193-439d-af3c-097c9eb70390.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96876905_616e_4ff2_bfe6_0fb106d2ae2c
GAHE-693243-2016 | HE-459107-2016 | 10/28/2016 11:43:28 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Piping_in_meter_cage.png | file://x:/photopub/docs/0000000507/029ad868-7337-41ad-acc9-d63727f232fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96876905_616e_4ff2_bfe6_0fb106d2ae2c
ELIN-684027-2016 | UW-451642-2016 | 10/14/2016 11:45:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | A new residence has had a service installed in a remote service building on the site. Multiple extension cords operating at 120 volts and 20 amps are run across grade from the service building approximately 35 meters, penetrate the wall of the building, and male cord caps are providing power to permanent wiring with live power fed into system from exposed energized cords. Flexible cord is not to be used in lieu of permanent wiring and male cord caps with live terminals provide for serious potential for injury to persons. Flexible cord used for permanent wiring run through walls or attached to permanent construction can lead to property damage | 4 | Conductors, Misuse of flexible cords. | Outlets_showing_wiring_fed_from_live_ends_of_male_cord_caps.png | file://x:/photopub/docs/0000000503/6f91cf4f-ffc8-4ea9-8eb7-73af68701451.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de524f84_578f_4954_925f_952064e8bd52
ELIN-708954-2016 | EL-452947-2016 | 11/24/2016 5:06:35 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Light fixtures connected without boxes and energized. Possibility for fire and shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Circuits_16_21_tagged_off.png | file://x:/photopub/docs/0000000521/66fbb6aa-b437-4fa5-b41f-f5378996610e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6feb9fdc_ad39_4a68_94e9_f5fde44b0233
ELIN-708954-2016 | EL-452947-2016 | 11/24/2016 5:06:35 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Light fixtures connected without boxes and energized. Possibility for fire and shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Light_fixture_no_box.png | file://x:/photopub/docs/0000000521/508bd73d-cb6d-440d-83e5-d94604be9aed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6feb9fdc_ad39_4a68_94e9_f5fde44b0233
ELIN-708962-2016 | EL-452947-2016 | 11/24/2016 3:59:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | Service conduit is not sealed effectively against weather. Water is present in conduit and distribution panel. Possibility of shock. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Water_in_panel_and_service_conduit.png | file://x:/photopub/docs/0000000521/fdda0a2f-3c32-4b19-9629-1dd3e43e22e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbf526d7_2a25_4e27_a76f_6ed44fd30318
ELIN-708954-2016 | EL-452947-2016 | 11/24/2016 5:06:35 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Light fixtures connected without boxes and energized. Possibility for fire and shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | NMD90_energized_not_terminated.png | file://x:/photopub/docs/0000000521/5181dec3-c19a-4869-9fd4-a09695bdb2b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6feb9fdc_ad39_4a68_94e9_f5fde44b0233
ELIN-709979-2016 | EL-424221-2016 | 11/24/2016 2:42:55 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | AC90 is not bonded. When a fault occurs to armour, over current device will not operate. | 3 | Continuity Bonding; method for equipment is not adequate. | AC90_into_PVC_raceway.png | file://x:/photopub/docs/0000000521/eab65de6-354f-47ee-8c1b-ead1fe9b79c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d36ea62c_c4c0_4c62_b621_10e6b45293d2
ELIN-708954-2016 | EL-452947-2016 | 11/24/2016 5:06:35 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Light fixtures connected without boxes and energized. Possibility for fire and shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Receptacle_energized.png | file://x:/photopub/docs/0000000521/174913cb-b1dc-4864-89e8-2eecbc79a922.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6feb9fdc_ad39_4a68_94e9_f5fde44b0233
ELIN-708962-2016 | EL-452947-2016 | 11/24/2016 3:59:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | Service conduit is not sealed effectively against weather. Water is present in conduit and distribution panel. Possibility of shock. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | PVC_connector_threaded_into_a_metal_hub_.png | file://x:/photopub/docs/0000000521/ff1df451-eaa5-4a1c-91d0-f1127d6c8d5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbf526d7_2a25_4e27_a76f_6ed44fd30318
ELIN-708954-2016 | EL-452947-2016 | 11/24/2016 5:06:35 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Light fixtures connected without boxes and energized. Possibility for fire and shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | NMD90_not_supported_.png | file://x:/photopub/docs/0000000521/ede20a95-e7a5-4ffa-a4bd-52c934b9740d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6feb9fdc_ad39_4a68_94e9_f5fde44b0233
ELIN-709979-2016 | EL-424221-2016 | 11/24/2016 2:42:55 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | AC90 is not bonded. When a fault occurs to armour, over current device will not operate. | 3 | Continuity Bonding; method for equipment is not adequate. | AC90_not_bonded_.png | file://x:/photopub/docs/0000000521/886c7c99-daaa-462f-a057-0e8e48afdf0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d36ea62c_c4c0_4c62_b621_10e6b45293d2
BPOP-670472-2016 | BPV-405988-2015 | 10/17/2016 4:30:48 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | gauge unreadable so unable to determine how or if any propane is within tank | 0 | No Created Hazard Identified | Fannybaygauge.png | file://x:/photopub/docs/0000000503/7d746313-5ad8-45ed-98bb-ab37c20679a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__681204e7_6512_4a71_a928_7c1b14f7526a
BPOP-670472-2016 | BPV-405988-2015 | 10/17/2016 4:30:48 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | gauge unreadable so unable to determine how or if any propane is within tank | 0 | No Created Hazard Identified | Fannybaytempo.png | file://x:/photopub/docs/0000000503/b19c9452-708e-4528-b86c-bb25d722960a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__681204e7_6512_4a71_a928_7c1b14f7526a
EDMA-693766-2016 | ED-421345-2016 | 10/28/2016 9:57:50 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | The platform steadies and the platform steady brackets to support the platform are used to keep the elevator supported and levelled. During an elevator modernization acceptance inspection, it was found that both the platform steadies and the platform steady brackets were both damaged. This damage was caused by the slack hoisting ropes of a twin post hydraulic elevator getting caught on the steadies and allowed to continue running. The compromising of the structural integrity of the platform steady system can lead to catastrophic consequences if left unrepaired. The platform may go out of level and collide with any number of hoistway devices causing serious damage and possible injuries of any occupants. It was found the lack of maintenance allowed the ropes to become slack to cause the damage. This twin post hydraulic elevator is located in an existing 6 stop commercial building. | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Right_hand_rear_platform_steady.png | file://x:/photopub/docs/0000000507/a9e89de2-e3f1-4093-a236-0ee3d3bde631.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f4a19b0_50c5_4b60_95ad_e82e986622b6
EDMA-693766-2016 | ED-421345-2016 | 10/28/2016 9:57:50 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | The platform steadies and the platform steady brackets to support the platform are used to keep the elevator supported and levelled. During an elevator modernization acceptance inspection, it was found that both the platform steadies and the platform steady brackets were both damaged. This damage was caused by the slack hoisting ropes of a twin post hydraulic elevator getting caught on the steadies and allowed to continue running. The compromising of the structural integrity of the platform steady system can lead to catastrophic consequences if left unrepaired. The platform may go out of level and collide with any number of hoistway devices causing serious damage and possible injuries of any occupants. It was found the lack of maintenance allowed the ropes to become slack to cause the damage. This twin post hydraulic elevator is located in an existing 6 stop commercial building. | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Improper_unengineered_car_door_clutch.png | file://x:/photopub/docs/0000000507/c83e5d70-7a09-46b4-96c4-3b6e8730f972.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f4a19b0_50c5_4b60_95ad_e82e986622b6
EDMA-693766-2016 | ED-421345-2016 | 10/28/2016 9:57:50 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | The platform steadies and the platform steady brackets to support the platform are used to keep the elevator supported and levelled. During an elevator modernization acceptance inspection, it was found that both the platform steadies and the platform steady brackets were both damaged. This damage was caused by the slack hoisting ropes of a twin post hydraulic elevator getting caught on the steadies and allowed to continue running. The compromising of the structural integrity of the platform steady system can lead to catastrophic consequences if left unrepaired. The platform may go out of level and collide with any number of hoistway devices causing serious damage and possible injuries of any occupants. It was found the lack of maintenance allowed the ropes to become slack to cause the damage. This twin post hydraulic elevator is located in an existing 6 stop commercial building. | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Left_hand_rear_platform_steady.png | file://x:/photopub/docs/0000000507/def33543-7772-4cbe-9d4c-e256becaa756.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f4a19b0_50c5_4b60_95ad_e82e986622b6
ELIN-677154-2016 | EL-437324-2016 | 10/4/2016 11:51:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Service has many non-compliances. Homeowner has not completed the repairs. Energization is not possible at this time. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Panel.png | file://x:/photopub/docs/0000000495/af1508b5-d275-4a6b-8f93-43c2bf7c5402.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2dfa656b_a6fb_4c47_87ad_5a11b84bed6d
ELIN-677154-2016 | EL-437324-2016 | 10/4/2016 11:51:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Service has many non-compliances. Homeowner has not completed the repairs. Energization is not possible at this time. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Meter.png | file://x:/photopub/docs/0000000495/f26f7571-16c0-4500-9d9f-c721a4adacc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2dfa656b_a6fb_4c47_87ad_5a11b84bed6d
EDIN-713043-2016 | ED-400833-2016 | 11/28/2016 7:07:05 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED005 | Suspected wear or defects that are: Unlikely to progress | 1 | 1 | Ensure traveling cable is suspended properly under the car | 1 | Suspected wear or defects that are: Unlikely to progress | Travel_cable_suspension.png | file://x:/photopub/docs/0000000522/1ef526b7-fb45-40b2-aa33-39735a5c10bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98993a30_b824_4505_83bc_9ed94e235d0a
EDIN-713043-2016 | ED-400833-2016 | 11/28/2016 7:07:05 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED005 | Suspected wear or defects that are: Unlikely to progress | 1 | 1 | Ensure traveling cable is suspended properly under the car | 1 | Suspected wear or defects that are: Unlikely to progress | Toe_guard_support.png | file://x:/photopub/docs/0000000522/8f660df2-d274-4b93-a69a-40bfd5ed97fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98993a30_b824_4505_83bc_9ed94e235d0a
ELIN-704606-2016 | EL-396789-2016 | 11/28/2016 2:29:02 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | A new 100 amp 240 volt residential service has been installed on an existing residence as a service upgrade. The service mast installed is not recognized as an approved overhead service support and lacks sufficient strength to adequately support the weight of service conductors under duress such as wind and snow. This can lead to power outage or damage to structure or injury to persons. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 1_1_4__rigid_pipe_nast_with_emt_clips_into_lathe.png | file://x:/photopub/docs/0000000523/2d787a57-00d2-4875-a127-cfdf6c947008.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c7a5695_a78c_497e_a117_618a15f8f89d
ELHE-706223-2016 | HE-466243-2016 | 11/22/2016 12:24:00 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Unapproved and disengaged mid-span points of attachment on a residential overhead line wiring system. The wire is subject to mechanical damage from excess friction or contact from a vehicle which could lead to a short circuit or fire. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Unapproved_support.png | file://x:/photopub/docs/0000000520/0fc22b64-ea30-4b74-ace4-00668d59fe16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__861180c9_7f89_4775_9c81_b31081e95006
ELIN-675024-2016 | EL-445408-2016 | 9/30/2016 5:45:22 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | View01_meter_base.png | file://x:/photopub/docs/0000000493/38c147aa-bf45-4775-bcd8-40759b657e79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a76af93a_3e6b_4377_8b93_bcd11e46e5ef
ELIN-672334-2016 | EL-442747-2016 | 9/28/2016 9:37:49 AM | ASSESS: EL: Final | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | In the single family home with a 150A 120/240V main panel, existing receptacles and lights are not provided with proper cover plates or fastened properly to the outlet boxes. This poses a shock hazard to persons using the devices in the home as the energized terminals and wiring are not protected from contact. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Receptacle.png | file://x:/photopub/docs/0000000492/bc15bddc-96d6-4629-a5aa-b74ca216605f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10012809_5b7a_43b6_8a07_299c8e05a9f0
ELIN-672334-2016 | EL-442747-2016 | 9/28/2016 9:37:49 AM | ASSESS: EL: Final | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | In the single family home with a 150A 120/240V main panel, existing receptacles and lights are not provided with proper cover plates or fastened properly to the outlet boxes. This poses a shock hazard to persons using the devices in the home as the energized terminals and wiring are not protected from contact. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Broken_Light.png | file://x:/photopub/docs/0000000492/dc07a264-e8c2-4511-891d-439be8a8c542.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10012809_5b7a_43b6_8a07_299c8e05a9f0
ELIN-672334-2016 | EL-442747-2016 | 9/28/2016 9:37:49 AM | ASSESS: EL: Final | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | In the single family home with a 150A 120/240V main panel, existing receptacles and lights are not provided with proper cover plates or fastened properly to the outlet boxes. This poses a shock hazard to persons using the devices in the home as the energized terminals and wiring are not protected from contact. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Light_Fixture.png | file://x:/photopub/docs/0000000492/58a04a41-6581-4a00-b5bf-a28113bd6f39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10012809_5b7a_43b6_8a07_299c8e05a9f0
ELIN-672334-2016 | EL-442747-2016 | 9/28/2016 9:37:49 AM | ASSESS: EL: Final | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | In the single family home with a 150A 120/240V main panel, existing receptacles and lights are not provided with proper cover plates or fastened properly to the outlet boxes. This poses a shock hazard to persons using the devices in the home as the energized terminals and wiring are not protected from contact. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | NMD.png | file://x:/photopub/docs/0000000492/48d89513-24d8-455f-bea4-fe10ec4094c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10012809_5b7a_43b6_8a07_299c8e05a9f0
ELIN-674752-2016 | UW-445214-2016 | 10/3/2016 3:53:01 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Door to main disconnect was left open, if not corrected would leave risk of shock or the possibility of an arc blast. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Door_left_open_.png | file://x:/photopub/docs/0000000494/170d921b-c649-4b06-a9b6-2fc59f4358b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d84fbc25_5238_4992_9a56_65da7d75ddc1
ELIN-674752-2016 | UW-445214-2016 | 10/3/2016 3:53:01 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Door to main disconnect was left open, if not corrected would leave risk of shock or the possibility of an arc blast. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Electrical_room_being_used_for_storage_.png | file://x:/photopub/docs/0000000494/e8eb0fe5-323f-4cf5-8047-f04b2409471e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d84fbc25_5238_4992_9a56_65da7d75ddc1
ELHE-706223-2016 | HE-466243-2016 | 11/22/2016 12:24:00 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Unapproved and disengaged mid-span points of attachment on a residential overhead line wiring system. The wire is subject to mechanical damage from excess friction or contact from a vehicle which could lead to a short circuit or fire. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Disengaged_attachment.png | file://x:/photopub/docs/0000000520/1fe8f0e3-ee8c-4391-8845-7bae0805c486.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__861180c9_7f89_4775_9c81_b31081e95006
ELIN-706322-2016 | EL-413969-2016 | 11/22/2016 10:22:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Service conduit is not adequately bonded to ground. Service wires are only protected by the upstream utility over current protection and therefore have high fault current potential. This creates a higher potential for a fire under a fault condition. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Meter_base_service_conduit.png | file://x:/photopub/docs/0000000520/0865e517-7160-40d2-a1a8-ffec4f7c2d2d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34fdfcad_c0bd_49a6_bb6e_757fde797ec3
ELOP-681748-2016 | 5241203 | 10/21/2016 8:55:02 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | High voltage switches must be properly maintained in order to operate safely and function properly. Damaged equipment must be repaired as soon as practicable to ensure safe operation of the equipment. This installation has a 25KV 3 phase gang operated load break switch installed on the first pole on the property. The switch handle is damaged which has left the switch unoperable. This is a shock and fire hazard because it does not allow the disconnection of the electrical supply in the event of an emergency or to facilitate de-energization for safe maintenance of equipment. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Load_break_switch_handle.png | file://x:/photopub/docs/0000000504/0321acc1-b06b-4af2-93fd-12572cc964e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c0c8b11_d242_46c1_af86_7a0e603146c2
ELIN-709599-2016 | EL-470846-2016 | 11/25/2016 3:13:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | This assessment found the service ground and outlet boxes to be without the required bond connection. When properly connected this conductor provides a path back to the source, reducing the shock hazard by creating an equipotential plane. It also allows the over-current device to operate as intended, thereby reducing the fire hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Ground.png | file://x:/photopub/docs/0000000521/8e3d3119-3038-4f0e-ada9-8ed92a875122.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d45972d1_3165_4b63_9dd8_841ddbae00b1
ELIN-709599-2016 | EL-470846-2016 | 11/25/2016 3:13:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | This assessment found the service ground and outlet boxes to be without the required bond connection. When properly connected this conductor provides a path back to the source, reducing the shock hazard by creating an equipotential plane. It also allows the over-current device to operate as intended, thereby reducing the fire hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Protect_.png | file://x:/photopub/docs/0000000521/5bcda888-1dc8-4d6b-b84b-ebba8e37677d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d45972d1_3165_4b63_9dd8_841ddbae00b1
ELIN-712429-2016 | EL-470380-2016 | 11/28/2016 1:51:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | The service conductors at the weather head are within 1 meter distance of a window. This is a shock hazard condition. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_conductors_are_within_1_meter_of_window_.png | file://x:/photopub/docs/0000000522/b70747b9-0547-45b9-9a3f-db0155d866c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3419219_0915_4582_9af7_cb0805cd4a96
PRIN-712547-2016 | PR-449679-2016 | 11/28/2016 4:22:29 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR026 | Fall safety devices inadequate for hazards in area. | 3 | 2 | It was observed that no skirting was installed along the length of either sides of the conveyor. The purpose of skirting is to prevent a hazard from developing where snowmelt could create a cavern beneath the surface along the edges of the belt surface or walkway. | 3 | Fall safety devices inadequate for hazards in area. | No_Skirting_Intalled.png | file://x:/photopub/docs/0000000523/726e4241-9f53-48a2-8c67-5d872801d387.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6436012_7d4e_45c0_8e62_2b55e3fd536a
PROP-598657-2016 | 2224195 | 11/16/2016 5:49:08 PM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Safe working load not posted on rigging gantry, the gantry could fail if loaded over its capacity | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | SWL_gantry.png | file://x:/photopub/docs/0000000518/a051ce9b-6523-4ce0-b66b-59dda5d35a4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__D804FAEE_920F_4AED_BE4A_E68C3715B318
PROP-598645-2016 | 3125263 | 11/18/2016 12:36:34 PM | ASSESS: PR OP: RAP | png | #asFound | PR031 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | 1 | 1 | Lights in operators hut have no guarding, lights could be struck and luminaries could shatter. | 1 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | Guarding_required.png | file://x:/photopub/docs/0000000518/858ef7d4-dd10-4c66-a3e5-ae9eee4985d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__D612C7A0_33F0_442B_8DCD_D2537F9802DB
PROP-598659-2016 | 2224146 | 11/18/2016 1:19:40 PM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Carriage limit actuator out of position after cable shortening. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Carriage_limit_actuator.png | file://x:/photopub/docs/0000000518/8a8f771f-9dd6-4977-b5f1-25284b7fdde5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DD2274F2_BF28_429C_8E62_4CCE1E1F4B1F
GAIN-681444-2016 | GA-433942-2016 | 10/12/2016 10:11:27 AM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | Appliance connector not approved for application. Certified installation instructions prohibit passing through partition walls with appliance connectors as damage could occur at the point of contact. | 2 | Certified appliance connector installed but not approved for application | Appliance_connector_passing_through_wall_of_appliance_.png | file://x:/photopub/docs/0000000499/30d4a234-2c95-4bc5-8517-d955d18bfd3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a6c247d_408a_4fc0_b6e4_e617c69d6cdd
ELOP-681748-2016 | 5241203 | 10/21/2016 8:55:02 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | High voltage switches must be properly maintained in order to operate safely and function properly. Damaged equipment must be repaired as soon as practicable to ensure safe operation of the equipment. This installation has a 25KV 3 phase gang operated load break switch installed on the first pole on the property. The switch handle is damaged which has left the switch unoperable. This is a shock and fire hazard because it does not allow the disconnection of the electrical supply in the event of an emergency or to facilitate de-energization for safe maintenance of equipment. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Load_break_switch_handle_is_damaged.png | file://x:/photopub/docs/0000000504/08b29075-62ec-47f0-8abf-0ea0760f85bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c0c8b11_d242_46c1_af86_7a0e603146c2
ELOP-655665-2016 | 4000379 | 10/24/2016 2:19:28 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Cables are required to be properly entered and terminated into connectors at motor connection boxes. This is required to prevent damage to the conductors where they enter the equipment. This installation has a 20A, 480V armoured cable that enters a connector at a motor connection box that has been pulled out of the connector. This has exposed the cable's internal conductors to mechanical damage at the connection box. Left uncorrected this is a potential shock and fire hazard if the conductor insulation is damaged and the internal conductors are contacted by persons or objects. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Cable_pulled_out_of_motor_connection_box_.png | file://x:/photopub/docs/0000000504/6c37141b-893b-4828-803d-b98e1b50ef03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__EC612938_C19F_463C_8FA6_CBDA71B72F9D
ELOP-655665-2016 | 4000379 | 10/24/2016 2:19:28 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Cables are required to be properly entered and terminated into connectors at motor connection boxes. This is required to prevent damage to the conductors where they enter the equipment. This installation has a 20A, 480V armoured cable that enters a connector at a motor connection box that has been pulled out of the connector. This has exposed the cable's internal conductors to mechanical damage at the connection box. Left uncorrected this is a potential shock and fire hazard if the conductor insulation is damaged and the internal conductors are contacted by persons or objects. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Cable_pulled_out_of_motor_connection_box.png | file://x:/photopub/docs/0000000504/93fbfd50-4707-4afb-8c1e-635882d448d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__EC612938_C19F_463C_8FA6_CBDA71B72F9D
ELOP-681748-2016 | 5241203 | 10/21/2016 8:55:02 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | High voltage switches must be properly maintained in order to operate safely and function properly. Damaged equipment must be repaired as soon as practicable to ensure safe operation of the equipment. This installation has a 25KV 3 phase gang operated load break switch installed on the first pole on the property. The switch handle is damaged which has left the switch unoperable. This is a shock and fire hazard because it does not allow the disconnection of the electrical supply in the event of an emergency or to facilitate de-energization for safe maintenance of equipment. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Load_break_switch_on_pole.png | file://x:/photopub/docs/0000000504/15ae6b9a-a9a0-40a0-88fb-145ecc4c61c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c0c8b11_d242_46c1_af86_7a0e603146c2
GAIN-684746-2016 | GA-389012-2016 | 11/28/2016 10:23:31 AM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 |  | 2 | Certified appliance connector installed but not approved for application | Connector.png | file://x:/photopub/docs/0000000523/6864889f-ccfb-442c-9637-80a646d591d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b0b2bbc_43a1_4cc3_ba23_4821274a1d39
BPVOP-710942-2016 | 2265151 | 11/24/2016 11:10:22 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Hot Water Boiler with Heating Surface (HS) of 35 square meters, Maximum Allowable Working Pressure (MAWP) of 30psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_room_without_boiler_emergency_shutdown_switch_at_door.png | file://x:/photopub/docs/0000000523/ec065a98-136f-4675-b9a1-7e6dda712f64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__751cf710_a2b8_4e49_9cde_350f93527243
GAHE-708015-2016 | HE-470007-2016 | 11/21/2016 10:06:27 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Plug missing in service valve accessible to the public, if the valve were to be turned on it would release propane vapour into the atmosphere potentially causing a fire or explosion and causing property damage or harm to the public or employees. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | service_valve_.png | file://x:/photopub/docs/0000000519/28ea79c6-ba88-4b32-9a6f-1b41f8609ec5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4d8470f_7214_491c_ab2c_ae8375252df2
BPVOP-699961-2016 | 2260128 | 11/8/2016 10:35:56 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP196 | 5.1.0 In service proc/process - Scale and deposit build up on fireside (fire tubes or furnace tubes) | 3 | 3 | During the internal inspection of a Scotch Dryback with MAWP of 30 psig, lots of soot was found on the fireside and signigicant scale on the waterside. | 3 | 5.1.0 In service proc/process - Scale and deposit build up on fireside (fire tubes or furnace tubes) | Scale_and_pit.png | file://x:/photopub/docs/0000000514/72fc7bae-e27c-42c5-98f0-97f367826359.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d803fbd_578d_4b75_b59d_9d615542f86a
BPVOP-699961-2016 | 2260128 | 11/8/2016 10:35:56 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP196 | 5.1.0 In service proc/process - Scale and deposit build up on fireside (fire tubes or furnace tubes) | 3 | 3 | During the internal inspection of a Scotch Dryback with MAWP of 30 psig, lots of soot was found on the fireside and signigicant scale on the waterside. | 3 | 5.1.0 In service proc/process - Scale and deposit build up on fireside (fire tubes or furnace tubes) | Soot.png | file://x:/photopub/docs/0000000514/9551ed05-81f6-4a1d-84dc-6777ff6d8bee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d803fbd_578d_4b75_b59d_9d615542f86a
GAHE-710280-2016 | HE-471414-2016 | 11/23/2016 3:12:12 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA158 | Un repairable appliance in operation | 4 | 4 | The internal baffle inside of the draft hood for the venting system of the boiler was severely corroded. If the baffle fell off it would block the heat exchanger and possibly lead to the production of carbon monoxide. | 4 | Un repairable appliance in operation | Draft_hood.png | file://x:/photopub/docs/0000000520/e3cf9622-5d8b-48c7-91b1-d73b02cfeb3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20e466df_03f4_416a_9db0_9bb174d8db04
GAHE-710280-2016 | HE-471414-2016 | 11/23/2016 3:12:12 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA158 | Un repairable appliance in operation | 4 | 4 | The internal baffle inside of the draft hood for the venting system of the boiler was severely corroded. If the baffle fell off it would block the heat exchanger and possibly lead to the production of carbon monoxide. | 4 | Un repairable appliance in operation | Boiler.png | file://x:/photopub/docs/0000000520/6f4da0de-9158-4c0a-bab3-e32141f5f8b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20e466df_03f4_416a_9db0_9bb174d8db04
GAHE-710280-2016 | HE-471414-2016 | 11/23/2016 3:12:12 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA158 | Un repairable appliance in operation | 4 | 4 | The internal baffle inside of the draft hood for the venting system of the boiler was severely corroded. If the baffle fell off it would block the heat exchanger and possibly lead to the production of carbon monoxide. | 4 | Un repairable appliance in operation | Draft_hood_baffle.png | file://x:/photopub/docs/0000000520/7701f055-2252-40dc-91b6-c88ae550ae6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20e466df_03f4_416a_9db0_9bb174d8db04
GAIN-712822-2016 | GA-393929-2016 | 11/30/2016 2:32:46 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | The as found hazard was a venting system serving a new boiler which had been installed without the barometric damper Required by the appliance manufacturer. This is a hazard because excessive draft could cause the appliance combustion chamber to experience a high negative pressure leading to appliance damage and premature failure. | 3 | Appliance not installed according to installation instructions | Missing_Barometrics.png | file://x:/photopub/docs/0000000524/a79e2af9-39ba-4b8a-8fe9-de2fe2521dfe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2889842e_1e8d_481b_8313_d53f374a2014
ELIN-695099-2016 | EL-454098-2016 | 11/2/2016 11:19:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | If a service mast is not supported correctly the cantilever for the mast due to the weight of the supply conductors and snow load could pull the mast away from the building and create a potential hazard with unprotected supply conductors being stressed. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Support_clamps_for_mast.png | file://x:/photopub/docs/0000000510/e7224350-1258-47e1-89ea-4b47e28bb572.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e5885bc_c69f_48c4_b586_836bf2a5a8bd
ELHE-695575-2016 | HE-461867-2016 | 11/2/2016 11:47:38 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL245 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 4 | Rain water is leaking through light fixtures from a leaky flat roof. | 4 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | Interior_light_fixture.png | file://x:/photopub/docs/0000000510/bf809db4-6a85-4d78-b6d5-39bfd8779f7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c6a916b_6c0b_429d_9c03_6dc8c1c36c07
ELHE-695575-2016 | HE-461867-2016 | 11/2/2016 11:47:38 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL245 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 4 | Rain water is leaking through light fixtures from a leaky flat roof. | 4 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | Ceiling_water_damage.png | file://x:/photopub/docs/0000000510/961b7fa0-faed-49a9-a16d-0e406645e092.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c6a916b_6c0b_429d_9c03_6dc8c1c36c07
ELIN-695353-2016 | UW-461711-2016 | 11/1/2016 3:38:04 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead supply conductors for temporary construction service not installed properly with service head above supply conductors attachment device and supply conductors are hanging down the pole. When service supply conductors and equipment is not installed properly and is hanging downwards to the ground the electrical equipment is a possible electrical fire or shock hazard to people and property. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 100.png | file://x:/photopub/docs/0000000509/3cbc6930-c0f6-4e3f-b89d-0ded3b8bc50d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47a2737c_b727_42ef_9c13_2662f54dd223
ELIN-695353-2016 | UW-461711-2016 | 11/1/2016 3:38:04 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead supply conductors for temporary construction service not installed properly with service head above supply conductors attachment device and supply conductors are hanging down the pole. When service supply conductors and equipment is not installed properly and is hanging downwards to the ground the electrical equipment is a possible electrical fire or shock hazard to people and property. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 103.png | file://x:/photopub/docs/0000000509/4b0fe454-b892-4518-8f4d-6446921e587d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47a2737c_b727_42ef_9c13_2662f54dd223
ELIN-695353-2016 | UW-461711-2016 | 11/1/2016 3:38:04 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead supply conductors for temporary construction service not installed properly with service head above supply conductors attachment device and supply conductors are hanging down the pole. When service supply conductors and equipment is not installed properly and is hanging downwards to the ground the electrical equipment is a possible electrical fire or shock hazard to people and property. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 101.png | file://x:/photopub/docs/0000000509/792263cc-2172-4bfd-a346-ae07f517914e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47a2737c_b727_42ef_9c13_2662f54dd223
ELIN-680619-2016 | EL-449551-2016 | 10/12/2016 2:36:55 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | The feeder over current protection does not adequately protect the feeder conductors. With increased load the wiring could heat up beyond the tolerable amount. This could create a fire hazard. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Feeders_OC_protection.png | file://x:/photopub/docs/0000000500/89e997a7-9219-4832-b63e-a5643d53b502.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__139a3caa_af8d_498a_9d87_4b487d7c5020
ELIN-680621-2016 | EL-449551-2016 | 10/12/2016 12:17:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | The service over current protection does not adequately protect the service conductors. With increased load the wiring could heat up beyond the tolerable amount. This could create a fire hazard. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Main_service.png | file://x:/photopub/docs/0000000500/e6855851-2c94-47c6-922c-6d04af74d20a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b812492_de67_41de_b6c6_dbe11e416102
BPVOP-684083-2016 | 2299538 | 10/14/2016 10:24:48 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP042 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | 1 | 1 | Moisture and corrosion at base of vessel support leg | 1 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | Lower_vessel_support_leg.png | file://x:/photopub/docs/0000000500/549026cd-125b-4b08-919a-d662f7d776e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__241f40c0_ccab_4462_81fe_201db326d8d0
ELIN-702983-2016 | EL-401839-2016 | 11/15/2016 11:55:40 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Photo_to__Photo_to_unable_to_get_access_to_house.png | file://x:/photopub/docs/0000000516/9e945733-1fb3-4655-8b42-01ed63de2259.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcdb6be0_6fae_4067_95d9_830dda8f3a9b
ELIN-702983-2016 | EL-401839-2016 | 11/15/2016 11:55:40 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Property_secure.png | file://x:/photopub/docs/0000000516/ddabba1a-6c4b-45d0-9a93-d44acd19920e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcdb6be0_6fae_4067_95d9_830dda8f3a9b
ELIN-703259-2016 | EL-464774-2016 | 11/15/2016 10:01:34 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Exposed conductors leave the junction box and are connected to a device which is not approved for the purpose. This is a possible shock/fire hazard. | 3 | Conductors Equipment is not approved for the specific use. | Outside_receptacle.png | file://x:/photopub/docs/0000000516/768ad805-ab9d-4542-b86f-8a7b8480e286.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b80d64c_b759_4d94_ba21_02cad43857c7
GAIN-689483-2016 | GA-455972-2016 | 11/23/2016 11:59:10 AM | ASSESS: GA: Final | png | #asFound | GA079 | Over ½ psig inlet line pressure regulator of the non-positive shut off type | 3 | 3 | Over 1/2 PSI inlet pressure to poppet style regulator. Exceeding manufacturers maximum inlet pressure can cause damage to regulator and/or appliance connected downstream. | 3 | Over ½ psig inlet line pressure regulator of the non-positive shut off type | Regulator_not_certified_for_application.png | file://x:/photopub/docs/0000000520/3e66d646-eed8-481c-9908-9d540430d492.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce73e201_a12d_4404_9f81_902d24ca982d
EDIN-701817-2016 | ED-107206-2014 | 11/18/2016 5:25:48 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED000 | No Created Hazard Identified | 0 | 0 | Previous non compliance still not resolved | 0 | No Created Hazard Identified | Fastening_method.png | file://x:/photopub/docs/0000000518/0055239f-e795-43c5-b49e-6e74e63338bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cce4c127_ee6f_4689_957a_ac50f7639ce1
EDIN-701817-2016 | ED-107206-2014 | 11/18/2016 5:25:48 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED000 | No Created Hazard Identified | 0 | 0 | Previous non compliance still not resolved | 0 | No Created Hazard Identified | Wiring_method.png | file://x:/photopub/docs/0000000518/f83ea5d9-3ac2-48dd-b728-8b94d02f150b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cce4c127_ee6f_4689_957a_ac50f7639ce1
ELOP-696041-2016 | 5112236 | 11/8/2016 12:31:03 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL236 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | 3 | 3 | Accumulation of dust greater than 1/8 of an inch have been observed in multiple locations around the facility, dust cloud have been observed at the cyclone and multi trim saw. If the wood dust where to catch on fire a catastrophic explosion would occur due to the accumulation of wood dust in the air. | 3 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | Airborne_dust__airborne_dust_from_cyclone_ventilation_system.png | file://x:/photopub/docs/0000000513/d8c8476c-feed-4835-9b3f-ccc88dacb699.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf6488e0_5e37_47fb_9b11_a8411f25293b
ELIN-694554-2016 | EL-305398-2015 | 11/4/2016 10:43:00 AM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | Counter receptacle in bathroom located in dwelling must be tamper resistant to provide required protection from incorrect insertion of non-electrical device into energized receptacle, which could increase the possibility of electric shock. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Non_TR_rated_GFCI_receptacle_at_bathroom_counter.png | file://x:/photopub/docs/0000000511/a8e75d11-aa6c-4803-ba2c-c4f692365207.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__113bd1ee_e74a_4ece_9ba4_2cc20f47dd00
ELIN-706665-2016 | EL-468583-2016 | 11/21/2016 1:58:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Type one panel installed temporarily in a wet location. This is a shock hazard as this class of panel is not approved for use in wet locations. | 3 | Category 1 Equipment is not approved for the specific use or location. | A.png | file://x:/photopub/docs/0000000519/06fd4f8e-9dd2-428c-9f24-82bcc32936ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99dff281_cdff_4b7b_8f85_94e135c7f8c1
BPOP-670640-2016 | BPV-405336-2015 | 11/10/2016 12:54:16 PM | ASSESS: Propane PV: Periodic | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | Propane tank is too close to building. | 0 | No Created Hazard Identified | 10065_Finlay.png | file://x:/photopub/docs/0000000514/c74ea1ca-fa9a-42d9-9437-9fdca4fae49a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__19984627_f00e_40a2_9f51_bf689d9e62dc
ELIN-708059-2016 | EL-461780-2016 | 11/29/2016 11:24:57 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 2 | A newly renovated mobile home has had new circuits feeding receptacles installed feeding a washing machine, nook receptacles and the living room areas, operating at 120 volts and 15 amps. These circuits were not protected by Combination type arc fault circuit interrupters intended to reduce or eliminate the potential for fire caused by the building wiring or any cord connected equipment. The resultant installation puts persons and property at risk due to potential for fire or equipment damage. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3_circuits_for_washing_machine__living_room_and_nook_no_afci.png | file://x:/photopub/docs/0000000523/c2414d2e-e51d-49c1-a7ac-3d68d8ad8db9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49d99ccd_33f2_428b_8266_f3e1f6aa3d6a
ELIN-690502-2016 | EL-430725-2016 | 10/26/2016 11:02:42 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 3 | The device boxes were set into the wall approximately 25 Millimeters from the surface of the wall. This condition leads to energized wire and terminals being outside of the protective device box exposing occupants to a potential shock or fire hazard. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | Drywall_installed_prior_to_rw_inspection_.png | file://x:/photopub/docs/0000000506/a8232de6-fe31-4e1f-b071-10532a83595f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f12e472_a9f3_4ae0_bcd2_7cae4115814f
ELIN-692178-2016 | EL-442713-2016 | 11/2/2016 10:09:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | A new residential service rated 200 apps and 240 V has been installed. The enclosure is allowing water to enter the panelboard and all circuit breakers including main circuit breaker in panel. Circuit breakers are damaged when water enters them and can fail unpredictably in the future causing property damage or injury to persons | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Main_breaker_soaked_water_running_through_panel_and_all_breakers.png | file://x:/photopub/docs/0000000510/b1e76412-2bf6-407c-a88c-b226cdc7a8f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__747de612_e2cb_4b3f_bc18_7ec63ed1c8aa
ELIN-683976-2016 | EL-450441-2016 | 11/1/2016 12:07:31 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | A 120 volt 15 amp circuit dedicated for the furnace has a remote disconnect switch mounted 2 meters above floor and directly over the furnace. The furnace switch is for emergency use and when located too close to the furnace or is difficult to access can lead to injury to persons | 0 | No Created Hazard Identified | Furnace_switch_over_furnace_too_high_to_reach.png | file://x:/photopub/docs/0000000510/01a7c235-9510-4751-bd0f-a92665e74ef2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2572d764_1713_4447_835c_9d8d023d1d0b
ELIN-691944-2016 | EL-456821-2016 | 11/2/2016 11:50:38 AM | ASSESS: EL: Service Connection | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | A 200 amp 240 volt service upgrade is being done in a single dwelling. The main service fusible disconnect has been installed and only 60 cm of clearance has been provided in front of switch. Electrical equipment with renewable parts or parts that require examination are required to have a minimum of 1 m unobstructed access for safety of workers persons and operators of equipment. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | New_main_switch_not_enough_clearance.png | file://x:/photopub/docs/0000000510/fbaa9199-acae-474e-91d3-2be84cc9be66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5d0edc8_ab0b_4295_aae5_3062a2516f48
ELIN-707879-2016 | EL-461811-2016 | 11/22/2016 11:52:38 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | Service upgrade for existing barn. Metal service conduits have been installed and not properly bonded. This can lead to overcurrent devices not being able to function in a fault. Potential shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Bonding.png | file://x:/photopub/docs/0000000519/ce872229-0a48-4bce-a529-583d8c01f87b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0653512e_c13f_4f7a_9d33_fecabba22075
ELOP-709341-2016 | EL-086468-2014 | 11/24/2016 12:26:46 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Two extension cords plugged into general 15 amp receptacles have been permanently placed over a doorway and through a ceiling to feed fixed equipment. This poses a shock hazard and possible damage to the equipment as the cords are not approved for permanent use and are installed in such a way that the cords could become damaged. | 4 | Conductors, Misuse of flexible cords. | Extension_Cord_2.png | file://x:/photopub/docs/0000000521/e0ec1478-56db-46c6-8979-f6dfb251fa31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__368c7f8e_1c2e_4e74_ae9e_95b440b0f6e1
ELOP-709341-2016 | EL-086468-2014 | 11/24/2016 12:26:46 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Two extension cords plugged into general 15 amp receptacles have been permanently placed over a doorway and through a ceiling to feed fixed equipment. This poses a shock hazard and possible damage to the equipment as the cords are not approved for permanent use and are installed in such a way that the cords could become damaged. | 4 | Conductors, Misuse of flexible cords. | Extension_Cord_1.png | file://x:/photopub/docs/0000000521/f4a82670-a572-4479-b525-09984696a521.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__368c7f8e_1c2e_4e74_ae9e_95b440b0f6e1
ELIN-707159-2016 | EL-415255-2016 | 11/21/2016 12:18:32 PM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | FINAL assessment on new single family dwelling. Insufficient kitchen counter receptacles installed in lower floor front and rear kitchens. This can lead to circuit overloading. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Kitchen_counter.png | file://x:/photopub/docs/0000000519/ca1b0413-3f8f-49ab-b15a-a88c205a1dcc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__181c81a3_c6b7_44bb_b0bd_fd6abee68a4c
ELOP-694731-2016 | 5194150 | 11/30/2016 1:21:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 2 | Access to the 100 amp 120/240 volt service installed on pole is hindered by the utilities installation of a guy anchor. This is Botha thermal and operation issue. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Utility_guy_anchor_2.png | file://x:/photopub/docs/0000000524/2985cbb1-fe46-4e7c-a472-7188038eb54b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d199991_c320_4bf2_9d43_efb0e538e4a2
ELOP-694731-2016 | 5194150 | 11/30/2016 1:21:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 2 | Access to the 100 amp 120/240 volt service installed on pole is hindered by the utilities installation of a guy anchor. This is Botha thermal and operation issue. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Utility_guy_anchor_1.png | file://x:/photopub/docs/0000000524/861e0313-e8f9-45f9-bf0a-be6caac67d22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d199991_c320_4bf2_9d43_efb0e538e4a2
ELOP-696041-2016 | 5112236 | 11/8/2016 12:31:03 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL236 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | 3 | 3 | Accumulation of dust greater than 1/8 of an inch have been observed in multiple locations around the facility, dust cloud have been observed at the cyclone and multi trim saw. If the wood dust where to catch on fire a catastrophic explosion would occur due to the accumulation of wood dust in the air. | 3 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | Just_a__dust_accumulation_under_stocker.png | file://x:/photopub/docs/0000000513/703ea5c3-ac64-443e-94e4-b39ad48e4a69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf6488e0_5e37_47fb_9b11_a8411f25293b
ELOP-696041-2016 | 5112236 | 11/8/2016 12:31:03 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL236 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | 3 | 3 | Accumulation of dust greater than 1/8 of an inch have been observed in multiple locations around the facility, dust cloud have been observed at the cyclone and multi trim saw. If the wood dust where to catch on fire a catastrophic explosion would occur due to the accumulation of wood dust in the air. | 3 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | Just_accumulat__just_accumulating_as_a_result_of_hole_in_conveyor_system.png | file://x:/photopub/docs/0000000513/243f9c39-f908-4720-a5d5-06b7be56de4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf6488e0_5e37_47fb_9b11_a8411f25293b
ELOP-696041-2016 | 5112236 | 11/8/2016 12:31:03 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL236 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | 3 | 3 | Accumulation of dust greater than 1/8 of an inch have been observed in multiple locations around the facility, dust cloud have been observed at the cyclone and multi trim saw. If the wood dust where to catch on fire a catastrophic explosion would occur due to the accumulation of wood dust in the air. | 3 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | Cable_tray__Cable_tray_and_wood_desk_at_head_saw.png | file://x:/photopub/docs/0000000513/c585722c-f13a-4a5b-b34d-9e7736e21702.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf6488e0_5e37_47fb_9b11_a8411f25293b
ELOP-696041-2016 | 5112236 | 11/8/2016 12:31:03 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL236 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | 3 | 3 | Accumulation of dust greater than 1/8 of an inch have been observed in multiple locations around the facility, dust cloud have been observed at the cyclone and multi trim saw. If the wood dust where to catch on fire a catastrophic explosion would occur due to the accumulation of wood dust in the air. | 3 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | Dry_dust__dry_dust_accumulation_at_lawn_waste_conveyor.png | file://x:/photopub/docs/0000000513/d903f06a-5805-4df8-b479-b3c3288731a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf6488e0_5e37_47fb_9b11_a8411f25293b
ELOP-696041-2016 | 5112236 | 11/8/2016 12:31:03 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL236 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | 3 | 3 | Accumulation of dust greater than 1/8 of an inch have been observed in multiple locations around the facility, dust cloud have been observed at the cyclone and multi trim saw. If the wood dust where to catch on fire a catastrophic explosion would occur due to the accumulation of wood dust in the air. | 3 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | Dust_accumulat__dust_accumulation_at_Long_waste_conveyor_photo_to.png | file://x:/photopub/docs/0000000513/37f00198-5d80-44e7-a3da-7a0a3cb18fba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf6488e0_5e37_47fb_9b11_a8411f25293b
ELOP-696041-2016 | 5112236 | 11/8/2016 12:31:03 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL236 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | 3 | 3 | Accumulation of dust greater than 1/8 of an inch have been observed in multiple locations around the facility, dust cloud have been observed at the cyclone and multi trim saw. If the wood dust where to catch on fire a catastrophic explosion would occur due to the accumulation of wood dust in the air. | 3 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | Hole_in__hole_in_dust_collection_system.png | file://x:/photopub/docs/0000000513/c4feb91e-3334-44b3-a869-059a8d65c212.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf6488e0_5e37_47fb_9b11_a8411f25293b
ELOP-696041-2016 | 5112236 | 11/8/2016 12:31:03 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL236 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | 3 | 3 | Accumulation of dust greater than 1/8 of an inch have been observed in multiple locations around the facility, dust cloud have been observed at the cyclone and multi trim saw. If the wood dust where to catch on fire a catastrophic explosion would occur due to the accumulation of wood dust in the air. | 3 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | Dust_accumulat__dust_accumulation_on_cyclone_dust_collector.png | file://x:/photopub/docs/0000000513/17fb9dd3-2038-47c0-bde7-735baa2c969a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf6488e0_5e37_47fb_9b11_a8411f25293b
ELOP-696041-2016 | 5112236 | 11/8/2016 12:31:03 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL236 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | 3 | 3 | Accumulation of dust greater than 1/8 of an inch have been observed in multiple locations around the facility, dust cloud have been observed at the cyclone and multi trim saw. If the wood dust where to catch on fire a catastrophic explosion would occur due to the accumulation of wood dust in the air. | 3 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | Dust_accumula__dust_accumulation_exiting_from_multi_trim_saw.png | file://x:/photopub/docs/0000000513/aea4ec6f-8c12-4201-b1ef-c4fcdeb27dc6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf6488e0_5e37_47fb_9b11_a8411f25293b
ELOP-696041-2016 | 5112236 | 11/8/2016 12:31:03 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL236 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | 3 | 3 | Accumulation of dust greater than 1/8 of an inch have been observed in multiple locations around the facility, dust cloud have been observed at the cyclone and multi trim saw. If the wood dust where to catch on fire a catastrophic explosion would occur due to the accumulation of wood dust in the air. | 3 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | Typical_observati__typical_observation_of_cable_tray_no_dust_observed.png | file://x:/photopub/docs/0000000513/0d5ab7dd-6b21-4986-96ec-272afabad376.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf6488e0_5e37_47fb_9b11_a8411f25293b
ELOP-696041-2016 | 5112236 | 11/8/2016 12:31:03 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL236 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | 3 | 3 | Accumulation of dust greater than 1/8 of an inch have been observed in multiple locations around the facility, dust cloud have been observed at the cyclone and multi trim saw. If the wood dust where to catch on fire a catastrophic explosion would occur due to the accumulation of wood dust in the air. | 3 | Class II, all locations Area is classified, accumulations of combustible dust or explosive clouds are observed | Dust_accumulat_a.png | file://x:/photopub/docs/0000000513/9acd127e-a98c-46cc-9a51-c37f12085083.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf6488e0_5e37_47fb_9b11_a8411f25293b
ELIN-700365-2016 | EL-454019-2016 | 11/10/2016 1:11:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | A service connection for a new shop has found that the electrical service was not grounded. This can result in shock or not allow circuit protective devices to trip in case of overload. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Meter_base_used_for_grounding.png | file://x:/photopub/docs/0000000514/3168dc58-c6e0-4619-a9ac-d50c25d495b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4129be0e_faa1_4a19_a5e8_095512589b2c
GAIN-706011-2016 | GA-428164-2016 | 11/21/2016 3:36:41 PM | ASSESS: GA: Final | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | Combustion air intake on appliance installed with less than the required clearance to meter regulator relief. If a failure of the meter regulator were to occur while the appliance was in operation,fuel could be drawn into the appliance intake. Over fire condition could occur. Possible fire and carbon monoxide risk. | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Davidson.png | file://x:/photopub/docs/0000000520/b962dcac-acca-4c44-a120-a3b6f2610d2d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2911d87d_1e5b_4244_9175_f31c19798867
GAIN-702996-2016 | GA-464219-2016 | 11/22/2016 4:16:20 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | George.png | file://x:/photopub/docs/0000000520/db838d70-b3a9-47b1-910b-4205e1fc2067.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e20fca97_a730_4e2c_93ef_3555354a9c33
BPVIN-699309-2016 | BPV-464481-2016 | 11/7/2016 1:44:49 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP018 | 1.0.2 Clearances/Maintenance - Pipe supports not compliant but in place | 2 | 2 |  | 2 | 1.0.2 Clearances/Maintenance - Pipe supports not compliant but in place | Vessel_supports.png | file://x:/photopub/docs/0000000513/9f1abaf9-0f77-4dbb-bb9d-fb57f7a72f6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba21d7d9_c657_4e92_a950_296f3a78492d
EDIN-667522-2016 | ED-329742-2015 | 9/20/2016 10:12:55 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | Ensure horizontal safety activating arm is clear of any obstruction for the compensating rope shackles | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Safety_activating_arm_1.png | file://x:/photopub/docs/0000000488/efd765d2-312c-408b-a217-bea99c8bc461.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c8ad14d_98d1_40d0_8620_8da6c37aea61
EDIN-667522-2016 | ED-329742-2015 | 9/20/2016 10:12:55 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | Ensure horizontal safety activating arm is clear of any obstruction for the compensating rope shackles | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Safety_activating_arm_2.png | file://x:/photopub/docs/0000000488/d18d1fbd-079d-4141-9997-fe74c0375173.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c8ad14d_98d1_40d0_8620_8da6c37aea61
ELOP-644441-2016 | 3798341 | 9/29/2016 6:52:16 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | The ACWU feeder from the 50KVA generator to the 400A transfer switch has not been properly connected to the equipment by means of a fitting and as such the cover to the breaker section can not be installed making the energized connections accessible to persons who maintain this equipment and room. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 50KVA_Generator.png | file://x:/photopub/docs/0000000495/129e0e00-60d5-445c-be20-6a272c481c46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7eec9262_7677_4e82_862e_852937189208
ELIN-692401-2016 | EL-421499-2016 | 10/27/2016 11:34:34 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 | #10 awg conductor nicked down to the copper creating a potential fire hazard. | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Black_wire_damaged.png | file://x:/photopub/docs/0000000507/6170397c-0e76-4979-a9ca-fd562ca8303e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f933657b_ed82_47a3_adea_0d8ab4a41a12
ELIN-700378-2016 | EL-435688-2016 | 11/9/2016 8:56:40 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | A 15 amp 120 volt standard receptacle has been installed within 1.5 meters of the laundry sink and has not been GFCI protected, this could pose a shock hazard to persons and damage to electrical components using this receptacle in close proximity of the sink. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Laundry_Receptacle.png | file://x:/photopub/docs/0000000514/b6fe8546-2e79-498d-80e4-4f1ec0b3c4d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56c0f568_1814_44ff_b687_319ffa42e03c
BPVIN-700871-2016 | BPV-465613-2016 | 11/9/2016 2:01:47 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | Upon assessment of pressurized expansion tank installed in Hot Water Heating system with Allowable Working Pressure (AWP) of 80psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it is determined that tank is non ASME. Non-ASME tank may fail due to lack of quality control and flashing hot water can lead to incident. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | Expansion_tank_not_built_to_code.png | file://x:/photopub/docs/0000000516/e4198150-f9ec-4a74-9956-221d415f9159.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a261546_19f9_428e_8c4d_fd22e37e3035
BPVIN-701863-2016 | BPV-466322-2016 | 11/10/2016 1:32:20 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | Upon assessment of pressurized expansion tank installed in Hot Water Heating system with Allowable Working Pressure (AWP) of 45psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it is determined that tank is non ASME. Non-ASME tank may fail due to lack of quality control and flashing hot water can lead to incident. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | Expansion_tank_not_built_and_stamped_to_code.png | file://x:/photopub/docs/0000000516/0ab25b9f-4a6a-4909-83a4-f02f6f764749.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e777eaa_7f54_444c_84e1_0a2bbeed49b3
GAIN-659529-2016 | GA-378184-2016 | 9/20/2016 9:58:51 AM | ASSESS: GA: Final | png | #asFound | GA039 | Painting of exterior piping | 1 | 1 |  | 1 | Painting of exterior piping | Rooftop_piping_unpainted.png | file://x:/photopub/docs/0000000488/e55f7df7-6d12-4310-8a58-63b1c52563d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48bb4b67_2f43_44c0_b6b1_bed3debf24cf
BPVIN-672376-2016 | BPV-384889-2016 | 9/27/2016 9:10:53 AM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 | The boiler safety valves have been mounted with the safety valve spindles in the horizontal position against the manufacturer instructions which state they must be mounted in the vertical, upright position. This is to insure no sediment builds up against the safety valve face which may impede its ability to function correctly in the event of excessive pressure build up in the boiler. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2.png | file://x:/photopub/docs/0000000491/89f3baed-b023-4a90-b262-a13aed6743cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__488ac612_3b63_4ed8_9312_3c80fc595b0a
BPVIN-672376-2016 | BPV-384889-2016 | 9/27/2016 9:10:53 AM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 | The boiler safety valves have been mounted with the safety valve spindles in the horizontal position against the manufacturer instructions which state they must be mounted in the vertical, upright position. This is to insure no sediment builds up against the safety valve face which may impede its ability to function correctly in the event of excessive pressure build up in the boiler. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Tag.png | file://x:/photopub/docs/0000000491/5fcdbb16-e0cd-4b0c-9f45-cde3e48461e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__488ac612_3b63_4ed8_9312_3c80fc595b0a
BPVIN-672376-2016 | BPV-384889-2016 | 9/27/2016 9:10:53 AM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 | The boiler safety valves have been mounted with the safety valve spindles in the horizontal position against the manufacturer instructions which state they must be mounted in the vertical, upright position. This is to insure no sediment builds up against the safety valve face which may impede its ability to function correctly in the event of excessive pressure build up in the boiler. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Safety_valve_mounting.png | file://x:/photopub/docs/0000000491/1219120d-a955-4cae-9afc-4c6b3306aa2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__488ac612_3b63_4ed8_9312_3c80fc595b0a
AMIN-675333-2016 | AM-444994-2016 | 9/29/2016 10:24:11 AM | ASSESS: AM IN: Acceptance | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | Participants entering and exiting the device are at risk of falling. There is no fall protection (padding) provided that would reduce the risk of injury | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | No_fall_protection_around_entrance_exit.png | file://x:/photopub/docs/0000000493/78e14f13-39ac-4f4b-8d0c-222ca4bf2600.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2efca087_dc1a_4b42_bd4e_13b4bb5fd659
BPVOP-674454-2016 | 2975498 | 9/29/2016 10:25:08 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Scale.png | file://x:/photopub/docs/0000000494/48423c6b-1812-403c-bd8d-f306be3b91bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4517d31a_047a_445c_8f94_abe43a013c2a
ELOP-640373-2016 | EL-423377-2016 | 10/15/2016 4:06:56 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL100 | Conductors, Mis-use of flexible cords. | 4 | 4 | An extension cord has been plugged into a 15A 120V receptacle and run under a storage cabinet door to the inside of the cabinet where extension cords from the TV and other components run through a hole in the top of the cabinet and connect to first extension cord. The poses a shock and fire hazard as the cords are being used in a permanent fashion and are not rated to be passed through holes in cabinets or under doors. The connections of these cords together is inside a storage cabinet where items can be placed in front or on top of the connections. | 4 | Conductors, Mis-use of flexible cords. | Extension_Cord.png | file://x:/photopub/docs/0000000500/589bd0b3-2510-4057-93e6-c58f5539a274.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e817117_7e6f_40c0_9bb2_bcbbe6ab2115
ELOP-640373-2016 | EL-423377-2016 | 10/15/2016 4:06:56 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL100 | Conductors, Mis-use of flexible cords. | 4 | 4 | An extension cord has been plugged into a 15A 120V receptacle and run under a storage cabinet door to the inside of the cabinet where extension cords from the TV and other components run through a hole in the top of the cabinet and connect to first extension cord. The poses a shock and fire hazard as the cords are being used in a permanent fashion and are not rated to be passed through holes in cabinets or under doors. The connections of these cords together is inside a storage cabinet where items can be placed in front or on top of the connections. | 4 | Conductors, Mis-use of flexible cords. | Extension_cord_2.png | file://x:/photopub/docs/0000000500/f7f42abe-e276-49a0-aa58-c84d8bc3afc9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e817117_7e6f_40c0_9bb2_bcbbe6ab2115
ELIN-706007-2016 | EL-468249-2016 | 11/18/2016 11:35:23 AM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | The ground conductor is terminated to the main distribution enclosure. The ground conductor shall be terminated to the neutral system. 120/240 Volt, 100 Amp. This is a thermal effect condition. | 4 | Installation Grounding; conductor is not continuous. | Ground_conductor_is_not_terminated_to_the_neutral_system.png | file://x:/photopub/docs/0000000518/5b98c642-9bb5-4f85-9dd0-8ef2feeab758.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc148321_ced9_4c42_ae76_cb6a945c612b
ELIN-707431-2016 | UW-469753-2016 | 11/17/2016 10:49:35 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 4 | Ungrounded conductors are required to be protected by correctly sized devices (usually fuses or circuit breakers) that de-energize the circuit if an overload or short-circuit occurs. Correctly sized devices prevent the overloading of conductors which can cause overheating and the breakdown of the conductor insulation. During an assessment for an incident notification at a single family dwelling, a #14/2 non-metallic sheathed cable for a 15A, 120V washer receptacle and an incandescent light where found connected to a 30A, 240V circuit for the dryer. The laundry area where these devices where located was in a covered area on the exterior of the dwelling. If an overload condition was to occur at the washer receptacle or light, the 30A breaker for the dryer would not protect the #14 conductors. The overloading of the conductor could break down the insulation which may lead to equipment damage. The breakdown of the insulation could also lead to a short circuit on the conductor which may create a shock hazard | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | Laundry_Room.png | file://x:/photopub/docs/0000000518/a451a991-3fc7-4bfb-95ce-508a945dd7e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ca1302d_ee3a_4596_9dbf_fa4e9775241c
ELIN-707431-2016 | UW-469753-2016 | 11/17/2016 10:49:35 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 4 | Ungrounded conductors are required to be protected by correctly sized devices (usually fuses or circuit breakers) that de-energize the circuit if an overload or short-circuit occurs. Correctly sized devices prevent the overloading of conductors which can cause overheating and the breakdown of the conductor insulation. During an assessment for an incident notification at a single family dwelling, a #14/2 non-metallic sheathed cable for a 15A, 120V washer receptacle and an incandescent light where found connected to a 30A, 240V circuit for the dryer. The laundry area where these devices where located was in a covered area on the exterior of the dwelling. If an overload condition was to occur at the washer receptacle or light, the 30A breaker for the dryer would not protect the #14 conductors. The overloading of the conductor could break down the insulation which may lead to equipment damage. The breakdown of the insulation could also lead to a short circuit on the conductor which may create a shock hazard | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | Washer_receptacle.png | file://x:/photopub/docs/0000000518/140fefe6-2d74-4579-b74b-3085ac86073f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ca1302d_ee3a_4596_9dbf_fa4e9775241c
ELIN-707431-2016 | UW-469753-2016 | 11/17/2016 10:49:35 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 4 | Ungrounded conductors are required to be protected by correctly sized devices (usually fuses or circuit breakers) that de-energize the circuit if an overload or short-circuit occurs. Correctly sized devices prevent the overloading of conductors which can cause overheating and the breakdown of the conductor insulation. During an assessment for an incident notification at a single family dwelling, a #14/2 non-metallic sheathed cable for a 15A, 120V washer receptacle and an incandescent light where found connected to a 30A, 240V circuit for the dryer. The laundry area where these devices where located was in a covered area on the exterior of the dwelling. If an overload condition was to occur at the washer receptacle or light, the 30A breaker for the dryer would not protect the #14 conductors. The overloading of the conductor could break down the insulation which may lead to equipment damage. The breakdown of the insulation could also lead to a short circuit on the conductor which may create a shock hazard | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | 10_3_teck_OS_dwelling.png | file://x:/photopub/docs/0000000518/eeabf1bd-b7e9-4226-8c02-09bd3f568e83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ca1302d_ee3a_4596_9dbf_fa4e9775241c
ELIN-707431-2016 | UW-469753-2016 | 11/17/2016 10:49:35 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 4 | Ungrounded conductors are required to be protected by correctly sized devices (usually fuses or circuit breakers) that de-energize the circuit if an overload or short-circuit occurs. Correctly sized devices prevent the overloading of conductors which can cause overheating and the breakdown of the conductor insulation. During an assessment for an incident notification at a single family dwelling, a #14/2 non-metallic sheathed cable for a 15A, 120V washer receptacle and an incandescent light where found connected to a 30A, 240V circuit for the dryer. The laundry area where these devices where located was in a covered area on the exterior of the dwelling. If an overload condition was to occur at the washer receptacle or light, the 30A breaker for the dryer would not protect the #14 conductors. The overloading of the conductor could break down the insulation which may lead to equipment damage. The breakdown of the insulation could also lead to a short circuit on the conductor which may create a shock hazard | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | Junction_box_laundry_room.png | file://x:/photopub/docs/0000000518/ced17aad-b3a3-46c3-a0f7-e058b7ed64af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ca1302d_ee3a_4596_9dbf_fa4e9775241c
ELIN-707431-2016 | UW-469753-2016 | 11/17/2016 10:49:35 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 4 | Ungrounded conductors are required to be protected by correctly sized devices (usually fuses or circuit breakers) that de-energize the circuit if an overload or short-circuit occurs. Correctly sized devices prevent the overloading of conductors which can cause overheating and the breakdown of the conductor insulation. During an assessment for an incident notification at a single family dwelling, a #14/2 non-metallic sheathed cable for a 15A, 120V washer receptacle and an incandescent light where found connected to a 30A, 240V circuit for the dryer. The laundry area where these devices where located was in a covered area on the exterior of the dwelling. If an overload condition was to occur at the washer receptacle or light, the 30A breaker for the dryer would not protect the #14 conductors. The overloading of the conductor could break down the insulation which may lead to equipment damage. The breakdown of the insulation could also lead to a short circuit on the conductor which may create a shock hazard | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | Dryer_receptacle.png | file://x:/photopub/docs/0000000518/78ae0b9f-6f7c-47b4-8fec-f56606937e65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ca1302d_ee3a_4596_9dbf_fa4e9775241c
ELIN-707431-2016 | UW-469753-2016 | 11/17/2016 10:49:35 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 4 | Ungrounded conductors are required to be protected by correctly sized devices (usually fuses or circuit breakers) that de-energize the circuit if an overload or short-circuit occurs. Correctly sized devices prevent the overloading of conductors which can cause overheating and the breakdown of the conductor insulation. During an assessment for an incident notification at a single family dwelling, a #14/2 non-metallic sheathed cable for a 15A, 120V washer receptacle and an incandescent light where found connected to a 30A, 240V circuit for the dryer. The laundry area where these devices where located was in a covered area on the exterior of the dwelling. If an overload condition was to occur at the washer receptacle or light, the 30A breaker for the dryer would not protect the #14 conductors. The overloading of the conductor could break down the insulation which may lead to equipment damage. The breakdown of the insulation could also lead to a short circuit on the conductor which may create a shock hazard | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | 30A_2P_breaker.png | file://x:/photopub/docs/0000000518/625cfc53-7f69-4557-b2b6-0713c33efcf7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ca1302d_ee3a_4596_9dbf_fa4e9775241c
ELHE-668153-2016 | HE-440668-2016 | 9/20/2016 6:20:57 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/240 volt 100 amp main combination consumer's service panelboard has exposed and energized conductors while all covers are removed and missing. When a service panelboard and its distribution has all covers missing and not installed, the power supply system is a possible electrical shock or fire hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | energized_main_service_panelboard_with_covers_missing_3.png | file://x:/photopub/docs/0000000488/f8a2bc14-8f03-4b2f-9d7e-c626a64bc14b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53698f41_806d_435d_bf5e_5e5a6fc40ff4
ELHE-668153-2016 | HE-440668-2016 | 9/20/2016 6:20:57 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/240 volt 100 amp main combination consumer's service panelboard has exposed and energized conductors while all covers are removed and missing. When a service panelboard and its distribution has all covers missing and not installed, the power supply system is a possible electrical shock or fire hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | energized_main_service_panelboard_with_covers_missing_1.png | file://x:/photopub/docs/0000000488/d59375fb-8e95-4cfa-ac1e-020a0b04b04b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53698f41_806d_435d_bf5e_5e5a6fc40ff4
PRIN-502535-2015 | PR-311231-2015 | 10/4/2016 8:08:05 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR018 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | Tower footing material is chipping in some areas, Could result in loss of foundation integrity | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Wapiti_tw8_footing.png | file://x:/photopub/docs/0000000496/6a33a6d3-f29b-42eb-8779-a5fe48977533.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fda681b1_1efb_44f9_b66e_329d07d68b2f
EDIN-679870-2016 | ED-415715-2016 | 10/6/2016 4:14:29 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED057 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 2 | 2 | The opening between the wall and the outer deck of the escalator installation was not closed and secured. | 2 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | Escalator_wall_and_outer_deck_opening_Oct_6_2016.png | file://x:/photopub/docs/0000000497/a5db40fa-0430-4390-a53a-67a1e54e090a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b9b425c_8a70_4836_aced_1901e0c3c16d
ELIN-690442-2016 | EL-455217-2016 | 11/3/2016 10:15:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | A 200 amp 240 volt consumer service main panel has been installed in the new residential dwelling. The panel has not been sufficiently made weatherproof during construction and may allow water to enter the electrical equipment. This can lead to property damage or injury to persons, or failure of equipment to operate predictably. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_not_properly_weatherproof.png | file://x:/photopub/docs/0000000513/a1b61f72-ac1d-4285-a9d5-3adc0904bbc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab6375f7_4cf7_4628_bf54_e47c5f04a7ff
ELIN-693627-2016 | EL-438430-2016 | 11/7/2016 3:03:48 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | A 200 amp 240 volt main service panel was energized for temporary use during construction. The panel was exposed to direct rain incursion and the enclosure was not installed with enough care to ensure water would not enter. Panel board overcurrent devices that have been wetted will be damaged and will fail to react predictably in the future. Damage to property or injury to persons could be the result of this particular hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Open_top_of_enclosure__no_sheathing_or_roof_above_panel__no_roof_membrane.png | file://x:/photopub/docs/0000000513/1867f3a8-deb7-4bae-9773-46a9fe0ab20e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__897f4a4a_0c17_460e_a810_10b0f9ef47e5
ELIN-695605-2016 | EL-408563-2016 | 11/3/2016 4:38:53 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Liquid-tight flexible conduit used as a general raceway in contravention of stated conditions of use. This poses a risk of property damage (thermal event). | 3 | Conductors Equipment is not approved for the specific use. | Detail02_conduit.png | file://x:/photopub/docs/0000000511/e49b4d50-1245-4d1c-b3dc-21998ce4b3cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c790bca_c945_4019_a690_d10185dcc66e
ELIN-695608-2016 | EL-408563-2016 | 11/3/2016 4:32:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unprotected portions of consumer service cabling exceed maximum allowable length inside structure. This poses a serious risk of personal injury (shock) or property damage (thermal event) due to mechanical damage occurring to service cabling. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View01_sub_distribution.png | file://x:/photopub/docs/0000000511/34f98798-29b3-4b46-a325-81de81342871.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__60f918a0_3f7d_4734_aa24_bf9f3c89de05
ELIN-695605-2016 | EL-408563-2016 | 11/3/2016 4:38:53 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Liquid-tight flexible conduit used as a general raceway in contravention of stated conditions of use. This poses a risk of property damage (thermal event). | 3 | Conductors Equipment is not approved for the specific use. | View01_conduit.png | file://x:/photopub/docs/0000000511/1d24e7a9-69d9-456d-bce5-74e36e95428e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c790bca_c945_4019_a690_d10185dcc66e
ELIN-695608-2016 | EL-408563-2016 | 11/3/2016 4:32:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unprotected portions of consumer service cabling exceed maximum allowable length inside structure. This poses a serious risk of personal injury (shock) or property damage (thermal event) due to mechanical damage occurring to service cabling. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View02_meter_base.png | file://x:/photopub/docs/0000000511/ebdde7e3-0191-435a-b595-13d2b0f02383.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__60f918a0_3f7d_4734_aa24_bf9f3c89de05
BPVOP-291221-2014 | 2285697 | 10/21/2016 12:32:37 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Domestic Hot Water Boiler with Heating Surface (HS) of 6 square meter, MaximumAllowable Working Pressure (MAWP) of 160psig and Maximum Allowable Working Temperature (MAWT) of 250*Fahrenheit , it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_room_exit_without_emergency_shutdown_switch.png | file://x:/photopub/docs/0000000507/a1aed832-a651-472b-8629-fc1bb957c303.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03E820E8_3ABB_4604_8BCF_568A96B3BA4B
BPVIN-693884-2016 | BPV-459283-2016 | 10/28/2016 9:57:43 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of High Pressure Boiler with Heating Surface (HS) of 8.6 square meter, MaximumAllowable Working Pressure (MAWP) of 150psig, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, steam or the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_emergency_shutdown_switch.png | file://x:/photopub/docs/0000000507/33693ded-9038-4e3e-82cd-a7a2ddc73318.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__989e1aa4_27c4_4391_b5de_82fa9921dea2
EDRI-712938-2016 | ED-459876-2016 | 11/25/2016 12:51:40 PM | ASSESS: ED RI: Initial | png | #asFound | ED052 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 2 | 2 | No hoarding was present on level 8 of the building where a mast brace is. Someone could walk out on the brace to the mast of the hoist and would be in contact with the counterweight rope. | 2 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | Missing_hoarding_L8.png | file://x:/photopub/docs/0000000522/a314f8b2-4ccd-4917-9071-834226d50b71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbbf77ba_df0e_4489_89e1_55083d8908e1
ELIN-706690-2016 | EL-468582-2016 | 11/21/2016 12:36:50 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Panel is not weatherproof. Possibility of damage from weather. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_not_weatherproff.png | file://x:/photopub/docs/0000000519/d39d35c8-9600-4362-b9eb-3b509ee91af1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e445bf9e_2dcc_4ba8_99b9_e32a3817d7b4
ELIN-682901-2016 | UW-451032-2016 | 10/12/2016 9:28:05 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Temporary electrical installations are required to have a permit and the work to be inspected before the equipment is energized. At this installation, the electrical safety officer was conducting an assessment for the reconnection of power to a shop that was used for semi-truck repairs. The safety officer discovered the tenants of the shop had connected a 14 kilowatt generator to the building without permits or an inspection. The generator was running and unapproved, unprotected conductors where used as a feed to power the building. These conductors provided a possible shock hazard to any persons that came in contact with the conductors. Also, a transfer switch was not installed to isolate the temporary power from the future permanent power. If the main fused disconnect switch was closed while the generator was running and permanent power was connected, a short circuit would occur that would cause damage to equipment and a possible shock hazard to persons or a fire hazard to to the building. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_wire_R90.png | file://x:/photopub/docs/0000000499/1f9d5ca5-e1dd-482f-bdb3-232611537bde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22a2e9d4_15a4_4500_9eb2_bb830fdb25b3
ELIN-682901-2016 | UW-451032-2016 | 10/12/2016 9:28:05 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Temporary electrical installations are required to have a permit and the work to be inspected before the equipment is energized. At this installation, the electrical safety officer was conducting an assessment for the reconnection of power to a shop that was used for semi-truck repairs. The safety officer discovered the tenants of the shop had connected a 14 kilowatt generator to the building without permits or an inspection. The generator was running and unapproved, unprotected conductors where used as a feed to power the building. These conductors provided a possible shock hazard to any persons that came in contact with the conductors. Also, a transfer switch was not installed to isolate the temporary power from the future permanent power. If the main fused disconnect switch was closed while the generator was running and permanent power was connected, a short circuit would occur that would cause damage to equipment and a possible shock hazard to persons or a fire hazard to to the building. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Electrical_room_.png | file://x:/photopub/docs/0000000499/062026e6-1f26-410f-a51e-5da245bd065f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22a2e9d4_15a4_4500_9eb2_bb830fdb25b3
ELIN-682901-2016 | UW-451032-2016 | 10/12/2016 9:28:05 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Temporary electrical installations are required to have a permit and the work to be inspected before the equipment is energized. At this installation, the electrical safety officer was conducting an assessment for the reconnection of power to a shop that was used for semi-truck repairs. The safety officer discovered the tenants of the shop had connected a 14 kilowatt generator to the building without permits or an inspection. The generator was running and unapproved, unprotected conductors where used as a feed to power the building. These conductors provided a possible shock hazard to any persons that came in contact with the conductors. Also, a transfer switch was not installed to isolate the temporary power from the future permanent power. If the main fused disconnect switch was closed while the generator was running and permanent power was connected, a short circuit would occur that would cause damage to equipment and a possible shock hazard to persons or a fire hazard to to the building. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Live_conductors.png | file://x:/photopub/docs/0000000499/e37abb9e-54f3-4599-99a3-cb1e13ad5317.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22a2e9d4_15a4_4500_9eb2_bb830fdb25b3
ELIN-682901-2016 | UW-451032-2016 | 10/12/2016 9:28:05 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Temporary electrical installations are required to have a permit and the work to be inspected before the equipment is energized. At this installation, the electrical safety officer was conducting an assessment for the reconnection of power to a shop that was used for semi-truck repairs. The safety officer discovered the tenants of the shop had connected a 14 kilowatt generator to the building without permits or an inspection. The generator was running and unapproved, unprotected conductors where used as a feed to power the building. These conductors provided a possible shock hazard to any persons that came in contact with the conductors. Also, a transfer switch was not installed to isolate the temporary power from the future permanent power. If the main fused disconnect switch was closed while the generator was running and permanent power was connected, a short circuit would occur that would cause damage to equipment and a possible shock hazard to persons or a fire hazard to to the building. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Main_disconnect_locked_out.png | file://x:/photopub/docs/0000000499/4ce142f3-a79d-44f1-ad48-c9c2e95c681d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22a2e9d4_15a4_4500_9eb2_bb830fdb25b3
ELIN-682901-2016 | UW-451032-2016 | 10/12/2016 9:28:05 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Temporary electrical installations are required to have a permit and the work to be inspected before the equipment is energized. At this installation, the electrical safety officer was conducting an assessment for the reconnection of power to a shop that was used for semi-truck repairs. The safety officer discovered the tenants of the shop had connected a 14 kilowatt generator to the building without permits or an inspection. The generator was running and unapproved, unprotected conductors where used as a feed to power the building. These conductors provided a possible shock hazard to any persons that came in contact with the conductors. Also, a transfer switch was not installed to isolate the temporary power from the future permanent power. If the main fused disconnect switch was closed while the generator was running and permanent power was connected, a short circuit would occur that would cause damage to equipment and a possible shock hazard to persons or a fire hazard to to the building. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | R90_connected_to_splitter_.png | file://x:/photopub/docs/0000000499/bac31239-10ab-46ad-903a-8673283818e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22a2e9d4_15a4_4500_9eb2_bb830fdb25b3
ELIN-682901-2016 | UW-451032-2016 | 10/12/2016 9:28:05 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Temporary electrical installations are required to have a permit and the work to be inspected before the equipment is energized. At this installation, the electrical safety officer was conducting an assessment for the reconnection of power to a shop that was used for semi-truck repairs. The safety officer discovered the tenants of the shop had connected a 14 kilowatt generator to the building without permits or an inspection. The generator was running and unapproved, unprotected conductors where used as a feed to power the building. These conductors provided a possible shock hazard to any persons that came in contact with the conductors. Also, a transfer switch was not installed to isolate the temporary power from the future permanent power. If the main fused disconnect switch was closed while the generator was running and permanent power was connected, a short circuit would occur that would cause damage to equipment and a possible shock hazard to persons or a fire hazard to to the building. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 14_kw_generator.png | file://x:/photopub/docs/0000000499/5180dc01-a467-49f9-a042-5687a4691241.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22a2e9d4_15a4_4500_9eb2_bb830fdb25b3
GAIN-675964-2016 | GA-416611-2016 | 10/12/2016 10:19:57 AM | ASSESS: GA: Final | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Mechanical_air_inlet.png | file://x:/photopub/docs/0000000499/6cd14fd3-bb14-41f2-b21b-d729f38b8ba9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4826518_5621_4c3f_aaf9_c3d10ea21324
ELIN-671445-2016 | EL-391766-2016 | 9/27/2016 11:15:03 AM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 4 | When overhead supply conductors are attached to a service mast for support, the service mast is required to be made up of suitable components of an approved mast kit or a rigid steel conduit of a minimum trade size of 63mm. The mast is also required to be secured to the structural members of the building with the use of three U-bolts. This requirement is so the service mast will have adequate strength to support the cable and will not bend or break under the weight of the cable or when high winds or snow loads are present. In this 600A, 120/240V installation, three 53mm electrical metallic tubing (EMT) conduits where installed for the connection of an overhead service. EMT has a thinner wall than rigid steel conduit and does not provide the same structural support. The EMT conduits extended 1.5m above the roof line of the building and two of the conduits where used as the point of attachment for the overhead lines. The conduits inside the building where connected with straps and screws. At the time of the | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Shed_with_service.png | file://x:/photopub/docs/0000000492/5d987917-8aed-4b23-89a1-22ed81eebc1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f1ad1df_228a_41f2_9c94_31b983c78c1a
ELIN-671445-2016 | EL-391766-2016 | 9/27/2016 11:15:03 AM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 4 | When overhead supply conductors are attached to a service mast for support, the service mast is required to be made up of suitable components of an approved mast kit or a rigid steel conduit of a minimum trade size of 63mm. The mast is also required to be secured to the structural members of the building with the use of three U-bolts. This requirement is so the service mast will have adequate strength to support the cable and will not bend or break under the weight of the cable or when high winds or snow loads are present. In this 600A, 120/240V installation, three 53mm electrical metallic tubing (EMT) conduits where installed for the connection of an overhead service. EMT has a thinner wall than rigid steel conduit and does not provide the same structural support. The EMT conduits extended 1.5m above the roof line of the building and two of the conduits where used as the point of attachment for the overhead lines. The conduits inside the building where connected with straps and screws. At the time of the | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Distance_to_hydro_pole.png | file://x:/photopub/docs/0000000492/6ce767fb-0279-496f-b37a-e45fa3d17288.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f1ad1df_228a_41f2_9c94_31b983c78c1a
ELIN-671445-2016 | EL-391766-2016 | 9/27/2016 11:15:03 AM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 4 | When overhead supply conductors are attached to a service mast for support, the service mast is required to be made up of suitable components of an approved mast kit or a rigid steel conduit of a minimum trade size of 63mm. The mast is also required to be secured to the structural members of the building with the use of three U-bolts. This requirement is so the service mast will have adequate strength to support the cable and will not bend or break under the weight of the cable or when high winds or snow loads are present. In this 600A, 120/240V installation, three 53mm electrical metallic tubing (EMT) conduits where installed for the connection of an overhead service. EMT has a thinner wall than rigid steel conduit and does not provide the same structural support. The EMT conduits extended 1.5m above the roof line of the building and two of the conduits where used as the point of attachment for the overhead lines. The conduits inside the building where connected with straps and screws. At the time of the | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Weatherheads.png | file://x:/photopub/docs/0000000492/6d950380-6d2a-4e2f-bfc9-bc1ed2c565d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f1ad1df_228a_41f2_9c94_31b983c78c1a
ELIN-671445-2016 | EL-391766-2016 | 9/27/2016 11:15:03 AM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 4 | When overhead supply conductors are attached to a service mast for support, the service mast is required to be made up of suitable components of an approved mast kit or a rigid steel conduit of a minimum trade size of 63mm. The mast is also required to be secured to the structural members of the building with the use of three U-bolts. This requirement is so the service mast will have adequate strength to support the cable and will not bend or break under the weight of the cable or when high winds or snow loads are present. In this 600A, 120/240V installation, three 53mm electrical metallic tubing (EMT) conduits where installed for the connection of an overhead service. EMT has a thinner wall than rigid steel conduit and does not provide the same structural support. The EMT conduits extended 1.5m above the roof line of the building and two of the conduits where used as the point of attachment for the overhead lines. The conduits inside the building where connected with straps and screws. At the time of the | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Not_attached_to_structure_with_Ubolts.png | file://x:/photopub/docs/0000000492/4f297bbc-d52a-4b9f-9d4b-46c5723c095e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f1ad1df_228a_41f2_9c94_31b983c78c1a
ELIN-691917-2016 | UW-458171-2016 | 10/25/2016 9:23:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Before any regulated electrical work begins, an electrical permit is required and inspection requests are to be submitted at each phase of work. In this installation at a barn being used for a horticultural project, the safety officer discovered an unpermitted energized electrical installation. The safety officer observed several non-compliances including an electrical panel not being grounded and the incorrect use of cables. These non-compliances pose a shock hazard to persons and a fire hazard to the structure. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | OH_conductors.png | file://x:/photopub/docs/0000000506/90a57f25-2f49-4f06-a6a9-0d258dca0a2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__960e1301_bd64_4f08_8a87_0ccecbaeba89
ELIN-691917-2016 | UW-458171-2016 | 10/25/2016 9:23:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Before any regulated electrical work begins, an electrical permit is required and inspection requests are to be submitted at each phase of work. In this installation at a barn being used for a horticultural project, the safety officer discovered an unpermitted energized electrical installation. The safety officer observed several non-compliances including an electrical panel not being grounded and the incorrect use of cables. These non-compliances pose a shock hazard to persons and a fire hazard to the structure. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Electrical_panel.png | file://x:/photopub/docs/0000000506/72f5f159-e7fc-40c7-9962-00eda66acd33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__960e1301_bd64_4f08_8a87_0ccecbaeba89
ELIN-698728-2016 | EL-461455-2016 | 11/10/2016 11:33:57 AM | ASSESS: EL: Final | png | #asFound | EL128 | Installation of electrical equipment Residential: branch circuit for kitchen counter receptacles is not split 15 A, or 20 A. | 3 | 3 | 15 amp, 120 volt receptacle installed on kitchen island not on a split branch circuit. This is a thermal issue. | 3 | Installation of electrical equipment Residential: branch circuit for kitchen counter receptacles is not split 15 A, or 20 A. | Receptacle_not_split.png | file://x:/photopub/docs/0000000516/b1041723-5b6c-4495-b791-ea0a0bb59e00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bea7a00_c28f_4e51_b560_935629067856
ELIN-708939-2016 | EL-274465-2015 | 11/23/2016 4:02:03 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | This assessment found receptacles in a dwelling unit to be without the required bond wire connection. When properly connected this conductor provides a path back to the source, reducing the shock hazard by creating an equipotential plane. It also allows the over-current device to operate as intended, thereby reducing the fire hazard. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Bond_not_connected.png | file://x:/photopub/docs/0000000520/cd77b5e7-f7ab-4092-9540-bf32797e7163.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29adf174_2c65_4f90_ac4d_4ded4eda0557
ELOP-655771-2016 | 5194150 | 10/5/2016 10:46:21 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | The 100 amp 120/240 volt wether proof service panel is located on a pole at entrance to cemetery and tree growth has encapsulated the service equipment and conductors. This is a thermal hazard | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Exterior_panel_on_pole_service_1.png | file://x:/photopub/docs/0000000496/c9c017b6-5c12-4001-b860-ed92c5808082.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84AC1A9B_F759_4BC3_BA19_45FBD528707D
ELOP-655771-2016 | 5194150 | 10/5/2016 10:46:21 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | The 100 amp 120/240 volt wether proof service panel is located on a pole at entrance to cemetery and tree growth has encapsulated the service equipment and conductors. This is a thermal hazard | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Utility_overhead_conductors.png | file://x:/photopub/docs/0000000496/ddb5a9e9-8ff1-4ee8-a919-069664e5b6a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84AC1A9B_F759_4BC3_BA19_45FBD528707D
ELOP-655771-2016 | 5194150 | 10/5/2016 10:46:21 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | The 100 amp 120/240 volt wether proof service panel is located on a pole at entrance to cemetery and tree growth has encapsulated the service equipment and conductors. This is a thermal hazard | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Main_pole_service_pole.png | file://x:/photopub/docs/0000000496/f43397f9-d1b7-4bf3-a076-4fd95ffaea66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84AC1A9B_F759_4BC3_BA19_45FBD528707D
ELOP-655771-2016 | 5194150 | 10/5/2016 10:46:21 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | The 100 amp 120/240 volt wether proof service panel is located on a pole at entrance to cemetery and tree growth has encapsulated the service equipment and conductors. This is a thermal hazard | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Main_pole_service_2.png | file://x:/photopub/docs/0000000496/3aa356ec-81ec-4bd4-bc17-cc0f2ffcf592.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84AC1A9B_F759_4BC3_BA19_45FBD528707D
ELIN-678761-2016 | UW-447823-2016 | 10/5/2016 12:24:46 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | The main distribution has been located in a flood area. Neighbour has declared area floods annually in the fall . Supporting documents from survey company confirm that location is not suitable for distribution. If left in current location the hazard that will return will be shock, equipment damage, and thermal damage. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 2015_high_water_mark.png | file://x:/photopub/docs/0000000496/2f814acb-d34e-4e75-8ca3-af1037885228.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7f62d37_cc0a_470a_8608_cb3954e36b1a
ELIN-678761-2016 | UW-447823-2016 | 10/5/2016 12:24:46 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | The main distribution has been located in a flood area. Neighbour has declared area floods annually in the fall . Supporting documents from survey company confirm that location is not suitable for distribution. If left in current location the hazard that will return will be shock, equipment damage, and thermal damage. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Telephone_service_in_flood_pain_area_.png | file://x:/photopub/docs/0000000496/0f209d11-2cde-4254-93aa-97f1203c2832.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7f62d37_cc0a_470a_8608_cb3954e36b1a
ELIN-678761-2016 | UW-447823-2016 | 10/5/2016 12:24:46 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | The main distribution has been located in a flood area. Neighbour has declared area floods annually in the fall . Supporting documents from survey company confirm that location is not suitable for distribution. If left in current location the hazard that will return will be shock, equipment damage, and thermal damage. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Panel_with_water_damage.png | file://x:/photopub/docs/0000000496/cb1e2723-d5c3-41a3-97ad-30a95951bba8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7f62d37_cc0a_470a_8608_cb3954e36b1a
ELIN-678761-2016 | UW-447823-2016 | 10/5/2016 12:24:46 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | The main distribution has been located in a flood area. Neighbour has declared area floods annually in the fall . Supporting documents from survey company confirm that location is not suitable for distribution. If left in current location the hazard that will return will be shock, equipment damage, and thermal damage. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | BCH_tag.png | file://x:/photopub/docs/0000000496/4efa2a55-7ce0-46ab-8479-d3d3426d005b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7f62d37_cc0a_470a_8608_cb3954e36b1a
ELIN-706690-2016 | EL-468582-2016 | 11/21/2016 12:36:50 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Panel is not weatherproof. Possibility of damage from weather. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | GFCI_receptacles_not_weatherproof.png | file://x:/photopub/docs/0000000519/afc9c57b-3046-43a7-98f4-76428b0df42f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e445bf9e_2dcc_4ba8_99b9_e32a3817d7b4
ELIN-706690-2016 | EL-468582-2016 | 11/21/2016 12:36:50 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Panel is not weatherproof. Possibility of damage from weather. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Neutral_not_grounded2.png | file://x:/photopub/docs/0000000519/17049690-11bf-4f0c-b669-9b820c83180a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e445bf9e_2dcc_4ba8_99b9_e32a3817d7b4
ELIN-694245-2016 | UW-459636-2016 | 10/31/2016 4:03:25 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | The receptacle and the junction box are not approved for wet locations. This could over time become a shock hazard due to ingress of water into the junction box. | 3 | General Equipment is not approved for the specific use | RV_receptacle.png | file://x:/photopub/docs/0000000509/c5231a97-ed9a-4567-a6ae-0cc6f5efdf18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__942a7ce4_cf8f_49c7_a38c_ae3f3aba17f0
ELIN-694245-2016 | UW-459636-2016 | 10/31/2016 4:03:25 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | The receptacle and the junction box are not approved for wet locations. This could over time become a shock hazard due to ingress of water into the junction box. | 3 | General Equipment is not approved for the specific use | rv_cover_shot.png | file://x:/photopub/docs/0000000509/698dd449-6cb4-477c-ba1b-b5de044851c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__942a7ce4_cf8f_49c7_a38c_ae3f3aba17f0
ELIN-667774-2016 | EL-427243-2016 | 9/21/2016 2:41:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | In a single phase three wire system, the identified neutral conductor is directly grounded at the first available service box in order to facilitate the safe clearing of faults occurring within the system. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Main_system_ground_terminated_on_mechanical_lug_secured_to_pole_mount_bracket.png | file://x:/photopub/docs/0000000488/a6dbfd71-f1fa-4480-8ea0-25042707e85e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90bd1c51_4bb7_4701_bf8f_d4ce1efa425c
BPVOP-607276-2016 | 4616977 | 9/21/2016 11:01:41 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | During the inspection of a DHW Unfired Heater with MAWP of 150 Psig was found that the T&P valve was overdue as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Overdue_T_P.png | file://x:/photopub/docs/0000000488/067791e2-8876-460d-bc7a-87b7d753cdc9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c94d1da7_5832_4817_ae40_b3754ad63504
BPVOP-665682-2016 | 4616978 | 9/21/2016 12:35:15 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | During the inspection of a DHW Unfired Heater with MAWP of 150 Psig was found that the T&P valve was overdue as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Overdue_T_P_.png | file://x:/photopub/docs/0000000488/55b767b6-da67-4942-97ed-3f41c92e07fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9f4efa0_f49d_4299_8977_24035e95e2da
BPVOP-665684-2016 | 4616979 | 9/21/2016 2:33:24 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | During the inspection of a DHW Tank with MAWP of 160 Psig I was found that the T&P valve was overdue as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 2_T_and_P_s.png | file://x:/photopub/docs/0000000488/2434cabe-de0e-4c3a-ae00-e96af2771ab6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7cdefa9_c899_40d8_adbd_bcf9e51349c0
BPVOP-665681-2016 | 4617129 | 9/21/2016 10:41:36 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | During the inspection of a DHW Unfired Heater with MAWP of 150 Psig I was found that the T&P valve was overdue as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | T_and_P_valve.png | file://x:/photopub/docs/0000000488/824e12e1-5c50-41ac-abe3-65d30142a2fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c85c2a03_cbae_4285_83cc_c4b78f18bc16
BPVOP-665666-2016 | 4616981 | 9/21/2016 11:56:06 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | During the inspection a a bank of 2 HW Boilers with MAWP of 45 psig was found that the Safety Relief Valves stamped 2007 and overdue as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Overdue_SRV.png | file://x:/photopub/docs/0000000488/02d19b2d-d31a-4e95-89bc-203491bc2ef8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d7a990d_4849_4cef_b13f_728bddb7c51c
ELIN-691917-2016 | UW-458171-2016 | 10/25/2016 9:23:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Before any regulated electrical work begins, an electrical permit is required and inspection requests are to be submitted at each phase of work. In this installation at a barn being used for a horticultural project, the safety officer discovered an unpermitted energized electrical installation. The safety officer observed several non-compliances including an electrical panel not being grounded and the incorrect use of cables. These non-compliances pose a shock hazard to persons and a fire hazard to the structure. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | NMSC_OS_barn_.png | file://x:/photopub/docs/0000000506/3796cb5b-055e-48c5-aba6-7a2cb36ce717.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__960e1301_bd64_4f08_8a87_0ccecbaeba89
ELIN-691917-2016 | UW-458171-2016 | 10/25/2016 9:23:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Before any regulated electrical work begins, an electrical permit is required and inspection requests are to be submitted at each phase of work. In this installation at a barn being used for a horticultural project, the safety officer discovered an unpermitted energized electrical installation. The safety officer observed several non-compliances including an electrical panel not being grounded and the incorrect use of cables. These non-compliances pose a shock hazard to persons and a fire hazard to the structure. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | OS_Barn_.png | file://x:/photopub/docs/0000000506/f833f8b6-3530-4ed6-909f-7b30d57cbda2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__960e1301_bd64_4f08_8a87_0ccecbaeba89
ELIN-706990-2016 | EL-468212-2016 | 11/21/2016 9:31:09 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 200 amp, 120/240V main distribution rated for indoor conditions only installed were main distribution is exposed to outdoor conditions. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_distribution_not_in_weather_proof_enclosure.png | file://x:/photopub/docs/0000000519/e7bce67a-adbd-4831-ad94-63d220a42c0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4af88d83_0d5d_4bc9_8040_12e3a8396383
ELIN-703619-2016 | EL-435193-2016 | 11/14/2016 6:40:29 PM | ASSESS: EL: Service Connection | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | 100 amp, 120/240 volt temporary service has service conductors installed with an ampacity rating less then the service ampacity rating. This is a thermal issue. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Temp_service.png | file://x:/photopub/docs/0000000515/d7e259b5-2cad-4b38-8ec1-688653cf930f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f67c49c8_f76d_454d_a051_73c461ff96fe
GAHE-704373-2016 | HE-468021-2016 | 11/15/2016 1:58:04 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Tank location does not meet code required clearances to combustibles. | 3 | Clearance to combustibles not maintained | Side_view.png | file://x:/photopub/docs/0000000516/5905a382-4f57-4fc8-bf31-3f57addf4943.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68a2b571_09c4_4cec_8cee_0e2f8f0f0add
GAHE-704373-2016 | HE-468021-2016 | 11/15/2016 1:58:04 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Tank location does not meet code required clearances to combustibles. | 3 | Clearance to combustibles not maintained | End_view_.png | file://x:/photopub/docs/0000000516/ef9658af-da0f-4a4c-8eaf-c203f805b5d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68a2b571_09c4_4cec_8cee_0e2f8f0f0add
PROP-598676-2016 | 2224238 | 11/15/2016 7:47:28 PM | ASSESS: PR OP: RAP | png | #asFound | PR031 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | 1 | 1 |  | 1 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | Missing_smoke_detector.png | file://x:/photopub/docs/0000000518/fc9479fa-74d7-4b27-be76-ac87ac7c1992.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__E458AE9B_B2CF_4996_8CED_A4BD3D105DE6
PROP-598680-2016 | PR-202849-2015 | 11/14/2016 7:48:56 PM | ASSESS: PR OP: RAP | png | #asFound | PR044 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | 3 | 2 | Tower safety switch/wire grounding fault. | 3 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | Return_station.png | file://x:/photopub/docs/0000000518/8579c6fa-d245-4c52-8e26-e03f5e734b31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__CBFEF6A7_DA64_4362_8A70_7AAF37728511
ELIN-643296-2016 | EL-381290-2016 | 9/23/2016 1:50:49 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Energized exposed circuits. Circuit not protected with correct over current devices. Potential for fire and shock. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Exposed_circuit_conductor.png | file://x:/photopub/docs/0000000490/f90259f1-e822-4069-9a84-aa1e5242be1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd901c6c_6051_42e8_ac5c_491a596424bc
ELIN-643296-2016 | EL-381290-2016 | 9/23/2016 1:50:49 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Energized exposed circuits. Circuit not protected with correct over current devices. Potential for fire and shock. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Incorrect_circuit_breakers.png | file://x:/photopub/docs/0000000490/b9fac1ff-5a4b-47f5-bf14-dfe38d5f00b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd901c6c_6051_42e8_ac5c_491a596424bc
ELIN-643345-2016 | EL-205316-2015 | 9/23/2016 2:29:55 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 4 | Bedroom circuits are not protected with an AFCI circuit breaker and are double terminated on a single regular circuit breaker. Possibility for circuit to be over-loaded without breaker reacting correctly causing fire or shock hazard. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_AFCI.png | file://x:/photopub/docs/0000000490/f81944b7-ae9f-4b64-b8a7-29adc0d75f80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06675d27_a27f_4fd2_99e0_e7b22e2d928e
ELIN-643296-2016 | EL-381290-2016 | 9/23/2016 1:50:49 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Energized exposed circuits. Circuit not protected with correct over current devices. Potential for fire and shock. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Panel_schedule_incorrect.png | file://x:/photopub/docs/0000000490/dd46a6c0-a785-4acd-83a3-e01faf876fba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd901c6c_6051_42e8_ac5c_491a596424bc
ELIN-643296-2016 | EL-381290-2016 | 9/23/2016 1:50:49 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Energized exposed circuits. Circuit not protected with correct over current devices. Potential for fire and shock. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Exposed_lighting_circuits.png | file://x:/photopub/docs/0000000490/83d17699-8d37-4d7d-ab15-bcb59eac0d9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd901c6c_6051_42e8_ac5c_491a596424bc
ELIN-643296-2016 | EL-381290-2016 | 9/23/2016 1:50:49 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Energized exposed circuits. Circuit not protected with correct over current devices. Potential for fire and shock. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | telcable_not_installed_in_box.png | file://x:/photopub/docs/0000000490/89841c69-9aef-44aa-a9fd-42e889c51a3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd901c6c_6051_42e8_ac5c_491a596424bc
ELIN-643345-2016 | EL-205316-2015 | 9/23/2016 2:29:55 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 4 | Bedroom circuits are not protected with an AFCI circuit breaker and are double terminated on a single regular circuit breaker. Possibility for circuit to be over-loaded without breaker reacting correctly causing fire or shock hazard. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Circuits_doubled_on_20Amp_breaker.png | file://x:/photopub/docs/0000000490/d1d19da9-3d9d-4ad6-a96b-7c2927b969dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06675d27_a27f_4fd2_99e0_e7b22e2d928e
ELIN-643345-2016 | EL-205316-2015 | 9/23/2016 2:29:55 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 4 | Bedroom circuits are not protected with an AFCI circuit breaker and are double terminated on a single regular circuit breaker. Possibility for circuit to be over-loaded without breaker reacting correctly causing fire or shock hazard. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Circuits_doubled_on_breakers.png | file://x:/photopub/docs/0000000490/0fb18b73-a3b0-4e53-85bd-4be04b3cc16d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06675d27_a27f_4fd2_99e0_e7b22e2d928e
ELIN-669966-2016 | EL-421357-2016 | 9/23/2016 9:48:20 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 15 amp, 120 volt receptacle within 1.5 meter of sink not ground fault protected. This is a thermal issue. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_within_1_5m_of_sink_not_GFCI_protected.png | file://x:/photopub/docs/0000000490/4ad9273b-200a-4919-a13d-baf415fe4245.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f6109ae_1871_4d10_a6be_6bc0a23910ae
ELIN-669969-2016 | EL-441915-2016 | 9/23/2016 11:04:45 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | 15 amp, 120 volt branch circuit wiring run through stud within 32 millimetres from stud edge. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD_within_32mm_of_stud_edge.png | file://x:/photopub/docs/0000000490/39bf7b96-7c93-473d-a084-09afeece716d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a5da6f7_6265_48c4_80b6_ab4d4d5f162c
ELHE-668153-2016 | HE-440668-2016 | 9/20/2016 6:20:57 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/240 volt 100 amp main combination consumer's service panelboard has exposed and energized conductors while all covers are removed and missing. When a service panelboard and its distribution has all covers missing and not installed, the power supply system is a possible electrical shock or fire hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | energized_main_service_panelboard_with_covers_missing_2.png | file://x:/photopub/docs/0000000488/deb52b36-1e35-4139-9f4f-b3d26c491e5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53698f41_806d_435d_bf5e_5e5a6fc40ff4
PROP-598625-2016 | 2224050 | 11/1/2016 1:29:16 PM | ASSESS: PR OP: RAP | png | #asFound | PR019 | Defect that impairs performance: Performance remains within limits Non-degenerative or very slow Reasonably detectable by the maintenance or operation program | 2 | 2 | A manual control lever which is utilized in the application of the emergency brake while the ropeway is being operated in an evacuation mode has broken of and therefore is inoperable. The manufacturer direction indicate that the aforementioned lever is to be utilized in event of an emergency. That being said there is an alternative method of applying the emergency brake in event of an emergency by use of a control valve at the manual pump hence why the lower hazard rating. | 2 | Defect that impairs performance: Performance remains within limits Non-degenerative or very slow Reasonably detectable by the maintenance or operation program | Broken_manual_emergency_brake_control_lever.png | file://x:/photopub/docs/0000000513/dd8d4a7f-18a5-42ef-89ec-9474722544a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7A2955F1_10A3_41D2_83D1_A9445AE26D53
PROP-598640-2016 | 2224148 | 11/2/2016 4:24:15 PM | ASSESS: PR OP: RAP | png | #asFound | PR031 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | 1 | 1 | An attendant stop button located in the attendant hut does not maintain its actuated state after being depressed. This is not deemed a significant hazard while the ropeway is operating of of the main electric drive as it operates off of a low voltage protection type circuit (i.e. even if the stop button resets itself it will not cause the drive to restart). It is however in the evacuation drive mode where it was noted that the attendant stop would not effectively kill the evacuation drive engine (due to the running engines inertia). Unless the button was held in for the period of time that would allow the engine to come to a complete stop the engine would restart and potentially the ropeway would continue to operate. | 1 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | Stop_button_does_not_maintain_state_after_being_actuated.png | file://x:/photopub/docs/0000000513/d19a1d75-ffc6-4445-ba7a-9d2f84bc7568.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C22B088F_943E_4FF8_BB21_8D4B799AF4E8
ELOP-667326-2016 | 5109382 | 9/20/2016 12:24:13 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Follow up assessment of combustible dust at pallet parts mill. Combustible Dust levels at or greater than 1/8 inch at height on vents, cables and sprinkler piping. Secondary explosion hazard (fireball) if disturbed and exposed to an ignition source. Open energized motor controller in mill due to a missing cover presents a shock hazard if inadvertently contacted by mill personnel working in the area. It can also be an ignition source igniting combustible dust. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Dust_at_height.png | file://x:/photopub/docs/0000000488/147af55b-8556-4caf-acc3-540f522f905a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e5cee16_d01c_4fc1_8a59_571ff89a7ec5
ELOP-667326-2016 | 5109382 | 9/20/2016 12:24:13 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Follow up assessment of combustible dust at pallet parts mill. Combustible Dust levels at or greater than 1/8 inch at height on vents, cables and sprinkler piping. Secondary explosion hazard (fireball) if disturbed and exposed to an ignition source. Open energized motor controller in mill due to a missing cover presents a shock hazard if inadvertently contacted by mill personnel working in the area. It can also be an ignition source igniting combustible dust. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_motor_controller.png | file://x:/photopub/docs/0000000488/e2e3c14c-d033-4d75-8683-9c016b436b18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e5cee16_d01c_4fc1_8a59_571ff89a7ec5
GAHE-708293-2016 | HE-470175-2016 | 11/21/2016 12:21:42 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA024 | No protection Low traffic | 3 | 3 | Tank is located beside driveway without vehicle protection. | 3 | No protection Low traffic | 1063_Bo_Hill.png | file://x:/photopub/docs/0000000519/d324da5e-a3e3-479e-afbf-e68613713950.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74c478af_cd05_49a9_8a27_e5a29c30ae81
ELOP-706767-2016 | EL-010627-2013 | 11/24/2016 11:05:18 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 4 | 3 separate dry core open ventilated transformers operating on a primary voltage of 600 volts with currents ranging from 70 - 125 amps. All 3 transformers have been mounted within 150 mm of combustible surfaces. Dry core open ventilated transformers use air for cooling and operate at temperatures that can affect nearby equipment or surfaces. Additionally, if a fault occurs in the transformer extreme heat and hot slag can eject from the transformer causing adjacent surfaces to ignite. This can lead to property damage or injury to persons. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 3_dry__core_transformers_without_adequate_clearance_to_combustible_surfaces.png | file://x:/photopub/docs/0000000520/1606d90c-b4a7-456a-a4f5-185ca60a032b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92e4a671_0954_4e96_a2e4_1777df1511a2
ELIN-709586-2016 | EL-433547-2016 | 11/23/2016 5:05:48 PM | ASSESS: EL: Final | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | Inadequate working clearances. Electrical equipment requires a minimum of 1m working clearance for safe operation and maintenance. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | B.png | file://x:/photopub/docs/0000000520/bba4794f-c70f-453d-a934-75e1a0d45cf4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65e1e8e4_ca52_4c60_81d6_200510c3abc7
ELIN-709248-2016 | EL-461690-2016 | 11/23/2016 4:33:50 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Knock out fillers missing. This is a shock hazard as an individual could touch live electrical parts. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | A.png | file://x:/photopub/docs/0000000520/b8c2d212-f2c8-445b-90be-3cde33bdd833.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e56ade8_0bc6_4f2a_9f5c_8092d1586fb9
GAHE-701199-2016 | HE-465879-2016 | 11/9/2016 2:26:31 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Propane tank too close to building. | 3 | Clearance to combustibles not maintained | 469_Clearwater_Valley.png | file://x:/photopub/docs/0000000514/f5e0bde0-f003-4bca-b432-a06a03e8f342.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__724acbe7_7135_4c8c_a444_26f97fdfd58f
BPOP-670449-2016 | BPV-405620-2015 | 11/9/2016 3:03:11 PM | ASSESS: Propane PV: Periodic | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | Build up of combustible materials around tank. Trees too close. | 0 | No Created Hazard Identified | 323_Grant.png | file://x:/photopub/docs/0000000514/7b37109e-12d8-4c6d-8190-1bd53b6154c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81c933bc_d004_49bb_9dd9_de6a4831594e
PROP-598639-2016 | 2224048 | 11/3/2016 9:05:08 PM | ASSESS: PR OP: RAP | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | Carriage limit switch set at a location where it is probable that in the event of the carriage moving beyond its allowable range that the carriage limit switch would not actuate. This could allow a condition in which the ropeway could continue to operate without proper carriage tension. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Carriage_limit_switch.png | file://x:/photopub/docs/0000000513/7bdb1458-05a9-4137-9c39-3ff4c8ff66e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6D821D1A_3E3F_4412_90D1_5075B2E5EDD6
GAIN-671450-2016 | GA-442716-2016 | 11/2/2016 2:39:53 PM | ASSESS: GA: Final | png | #asFound | GA100 | Hazards created by exhaust fans | 3 | 3 | Hazard created by mechanical exhaust. Operation of the natural draft commercial water heater is not as designed causing spillage of flue products into an unoccupied area due to operation of the mechanical exhaust. | 3 | Hazards created by exhaust fans | Hazard_created_by_mechanical_exhaust_.png | file://x:/photopub/docs/0000000510/fa419e36-9f3d-44ba-8784-e2358bb203ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1df10dff_1c2a_48ad_a621_e6d1425a50ef
GAUP-678850-2016 | UW-448211-2016 | 10/5/2016 3:35:11 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA112 | Leaking or Failing special venting system (Carbon Monoxide present in space) | 5 | 5 | The pool boiler was installed indoors. Any indoor installation requires a vent drain plug and cover to be installed. The drain plug and cover was not installed which allows flue gas to enter the indoor space. The mechanical room is attached to a pool change room and shower house. The flue gas may contain carbon monoxide which could enter the occupied space through two 4" vent openings. Carbon monoxide exposure can cause injury or death. | 5 | Leaking or Failing special venting system (Carbon Monoxide present in space) | Pool_boiler.png | file://x:/photopub/docs/0000000496/e99abfa0-187d-42c3-954a-e9a44e599b94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bccf014_5868_4863_9669_9930eeb9e8a4
GAUP-678850-2016 | UW-448211-2016 | 10/5/2016 3:35:11 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA112 | Leaking or Failing special venting system (Carbon Monoxide present in space) | 5 | 5 | The pool boiler was installed indoors. Any indoor installation requires a vent drain plug and cover to be installed. The drain plug and cover was not installed which allows flue gas to enter the indoor space. The mechanical room is attached to a pool change room and shower house. The flue gas may contain carbon monoxide which could enter the occupied space through two 4" vent openings. Carbon monoxide exposure can cause injury or death. | 5 | Leaking or Failing special venting system (Carbon Monoxide present in space) | Drain_plug_instructions.png | file://x:/photopub/docs/0000000496/aea49d41-b0aa-49d4-a2fd-2497a0bf8d86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bccf014_5868_4863_9669_9930eeb9e8a4
GAUP-678850-2016 | UW-448211-2016 | 10/5/2016 3:35:11 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA112 | Leaking or Failing special venting system (Carbon Monoxide present in space) | 5 | 5 | The pool boiler was installed indoors. Any indoor installation requires a vent drain plug and cover to be installed. The drain plug and cover was not installed which allows flue gas to enter the indoor space. The mechanical room is attached to a pool change room and shower house. The flue gas may contain carbon monoxide which could enter the occupied space through two 4" vent openings. Carbon monoxide exposure can cause injury or death. | 5 | Leaking or Failing special venting system (Carbon Monoxide present in space) | Vent_drain.png | file://x:/photopub/docs/0000000496/c396d1ab-d196-4820-afbe-e608ccd737ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bccf014_5868_4863_9669_9930eeb9e8a4
ELIN-701499-2016 | EL-452773-2016 | 11/24/2016 11:28:38 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Improper use of electrical equipment. Meterbase pole mounting hardware not installed. Dry type connectors used in wet locations. Box fill in excess of code requirements. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3931_GAMBA_POLE.png | file://x:/photopub/docs/0000000520/27a3d2cd-e9f1-44a4-947c-ae552359b8b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00f1ab64_01cb_4d53_ae8b_cd9410ed74f7
GAIN-706553-2016 | GA-453071-2016 | 11/24/2016 12:33:55 PM | ASSESS: GA: Final | png | #asFound | GA093 | Under sized system regulator for multiple appliances = < 10% | 3 | 3 | Existing 2 pound regulator is undersized to provide adequate gas flow to existing gas appliances and newly installed water heater. There is a possibility that during operation of the water heater could cause excessive pressure dropped in the gas system causing ignition problems with other existing appliances within the home causing an appliance explosion and appliance damage | 3 | Under sized system regulator for multiple appliances = < 10% | 15538_37.png | file://x:/photopub/docs/0000000520/6857f536-cccb-4b70-a529-65896bcacce5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55c73ca0_5a11_446e_9224_62de1235255e
ELIN-678696-2016 | EL-399166-2016 | 10/14/2016 11:38:04 AM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | During a Silver Label inspection of a used mobile home, breakers of an incorrect type were found to be installed in an electrical panel. Breaker types are tested and approved for safe reliable operation in specific panels. Although other types of breakers may physically fit into a panel, unless they have been approved for use within that panel, there is a potential for thermal equipment damage to occur which may spread to surrounding structure. | 3 | General Equipment is not approved for the specific use | BR_type_breaker_installed_in_panel_approved_for_DNPL_and_QNPL_types.png | file://x:/photopub/docs/0000000500/3919ade4-2cde-49ce-a26f-4a71d862ad2c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5c808f7_8061_4bc2_8306_6663dc064fc2
BPVIN-704423-2016 | BPV-445103-2016 | 11/16/2016 10:47:54 AM | ASSESS: BPV IN: Construction Boiler | png | #asFound | BP057 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | 2 | 2 |  | 2 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | leak_.png | file://x:/photopub/docs/0000000517/24054f22-51eb-404c-a08b-8298dce1bd9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df68aaaa_5f71_4d8d_abe8_4a5c115fdd94
ELIN-668339-2016 | EL-413327-2016 | 9/22/2016 11:31:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 600 volt 600 amp 3 phase 4 wire consumer's service has no grounding conductor terminated on service system identified conductor and service system is not grounded. When a service system is not grounded with an electrode and grounding conductor the system could fail in providing an equipotential plane for shock prevention and the system could become an electrical shock hazard to people. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 106.png | file://x:/photopub/docs/0000000489/ac92b87a-b173-4547-8bd0-2789a08e8347.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96aac832_ef74_4e91_801b_def3dc07431d
ELIN-668339-2016 | EL-413327-2016 | 9/22/2016 11:31:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 600 volt 600 amp 3 phase 4 wire consumer's service has no grounding conductor terminated on service system identified conductor and service system is not grounded. When a service system is not grounded with an electrode and grounding conductor the system could fail in providing an equipotential plane for shock prevention and the system could become an electrical shock hazard to people. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 103.png | file://x:/photopub/docs/0000000489/34bec7ce-ef22-4ba5-bbdc-ea8240ad5ff7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96aac832_ef74_4e91_801b_def3dc07431d
ELIN-668339-2016 | EL-413327-2016 | 9/22/2016 11:31:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 600 volt 600 amp 3 phase 4 wire consumer's service has no grounding conductor terminated on service system identified conductor and service system is not grounded. When a service system is not grounded with an electrode and grounding conductor the system could fail in providing an equipotential plane for shock prevention and the system could become an electrical shock hazard to people. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 100.png | file://x:/photopub/docs/0000000489/759a3bda-7aee-42a9-be58-b61da93a9bd8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96aac832_ef74_4e91_801b_def3dc07431d
ELIN-668339-2016 | EL-413327-2016 | 9/22/2016 11:31:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 600 volt 600 amp 3 phase 4 wire consumer's service has no grounding conductor terminated on service system identified conductor and service system is not grounded. When a service system is not grounded with an electrode and grounding conductor the system could fail in providing an equipotential plane for shock prevention and the system could become an electrical shock hazard to people. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 101.png | file://x:/photopub/docs/0000000489/e879c355-00fb-4087-b889-61b0eefb5750.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96aac832_ef74_4e91_801b_def3dc07431d
ELIN-668339-2016 | EL-413327-2016 | 9/22/2016 11:31:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 600 volt 600 amp 3 phase 4 wire consumer's service has no grounding conductor terminated on service system identified conductor and service system is not grounded. When a service system is not grounded with an electrode and grounding conductor the system could fail in providing an equipotential plane for shock prevention and the system could become an electrical shock hazard to people. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 104.png | file://x:/photopub/docs/0000000489/b05170f8-1d81-4f65-8603-891daed34b4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96aac832_ef74_4e91_801b_def3dc07431d
ELIN-668339-2016 | EL-413327-2016 | 9/22/2016 11:31:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 600 volt 600 amp 3 phase 4 wire consumer's service has no grounding conductor terminated on service system identified conductor and service system is not grounded. When a service system is not grounded with an electrode and grounding conductor the system could fail in providing an equipotential plane for shock prevention and the system could become an electrical shock hazard to people. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 105.png | file://x:/photopub/docs/0000000489/d9d2c492-9d75-4b5c-b755-cb667b2bbb33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96aac832_ef74_4e91_801b_def3dc07431d
ELIN-668339-2016 | EL-413327-2016 | 9/22/2016 11:31:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 600 volt 600 amp 3 phase 4 wire consumer's service has no grounding conductor terminated on service system identified conductor and service system is not grounded. When a service system is not grounded with an electrode and grounding conductor the system could fail in providing an equipotential plane for shock prevention and the system could become an electrical shock hazard to people. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 102.png | file://x:/photopub/docs/0000000489/28934dd1-5e28-4d3c-b37a-d26966d367ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96aac832_ef74_4e91_801b_def3dc07431d
ELIN-699351-2016 | EL-459014-2016 | 11/15/2016 11:05:26 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | Inadequate bonding of service equipment can result in fire or shock hazard under a fault condition on the utility side of the main service switch. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_grounding_bushing_installed_on_rigid_service_conduit.png | file://x:/photopub/docs/0000000517/0a2f00b1-12ca-45c2-88b7-ecc7076dd020.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__52cc85f5_4ea9_4dda_9d9b_ae0c3fc68feb
ELIN-671920-2016 | EL-428560-2016 | 9/28/2016 2:14:24 PM | ASSESS: EL: Final | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized 208 volt electrical panel, the locations as accessible to no trades persons. This is a school hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_energized_panel.png | file://x:/photopub/docs/0000000492/57daa1a9-819b-4454-af76-a0b9d0f3b394.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__52463d5e_17a5_4bcd_b755_a6c84dab2ba0
ELHE-694723-2016 | HE-459794-2016 | 10/31/2016 5:06:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Found privately owned overhead service wooden pole structure has pole rotting and pole is leaning to possibly fall over. When wooden poles are rotted and are not supported properly the electrical equipment is a possible electrical fire or shock hazard to people and property if pole falls over. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | pole_leaning_and_rotting_1.png | file://x:/photopub/docs/0000000508/f0de60e6-67a9-4925-b422-55af1efdb77e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0e5c762_5455_436a_8759_f0ffedc15f8a
ELHE-694723-2016 | HE-459794-2016 | 10/31/2016 5:06:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Found privately owned overhead service wooden pole structure has pole rotting and pole is leaning to possibly fall over. When wooden poles are rotted and are not supported properly the electrical equipment is a possible electrical fire or shock hazard to people and property if pole falls over. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | pole_leaning_and_rotting_2.png | file://x:/photopub/docs/0000000508/9838925f-47c8-4ac5-99fe-3e6286b70342.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0e5c762_5455_436a_8759_f0ffedc15f8a
ELHE-694723-2016 | HE-459794-2016 | 10/31/2016 5:06:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Found privately owned overhead service wooden pole structure has pole rotting and pole is leaning to possibly fall over. When wooden poles are rotted and are not supported properly the electrical equipment is a possible electrical fire or shock hazard to people and property if pole falls over. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | pole_leaning_and_rotting_3.png | file://x:/photopub/docs/0000000508/b4e7136e-e3de-495f-9cf0-540828a420fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0e5c762_5455_436a_8759_f0ffedc15f8a
ELIN-645896-2016 | EL-368167-2016 | 9/28/2016 11:07:48 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | There are two receptacles that do not have covers installed and they are energized. The exposed terminals are a possible shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Receptacle.png | file://x:/photopub/docs/0000000492/4f6e3255-cf54-4bfe-a3aa-c06f307efb82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddeb5e9b_9516_43b1_a98e_d455a25260e1
BPVOP-668692-2016 | 4485678 | 10/7/2016 10:23:11 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon the assessment of a Hot Water Bank of 2 Boilers with MAWP of 45 psig, was found that the Safety Relief Valves were overdue as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Overdue_SRV.png | file://x:/photopub/docs/0000000497/48745741-f2ed-448b-b463-131a20a9bf37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17d1e0b1_ca6f_4125_9280_caaefc0445b9
GAIN-670958-2016 | GA-433210-2016 | 10/14/2016 11:55:31 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | Possibility of snow being drawn into appliance intake. This may cause over fire condition due to reduced airflow . Possible fire risk and or damage to heat exchanger. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Chemainus2.png | file://x:/photopub/docs/0000000501/2bb563c3-63f2-46e8-b63c-a38ee9072036.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90da4264_8f75_4d67_8961_e9ace88c2875
ELIN-703715-2016 | EL-386408-2016 | 11/16/2016 2:37:17 PM | ASSESS: EL: Final | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 2 |  | 1 | General Working space or dedicated space is being used for storage | teck90.png | file://x:/photopub/docs/0000000517/dec43337-06bf-4338-90e5-d0218ad7755a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad18ec93_dfa0_4977_b390_14b886ccf465
ELIN-703715-2016 | EL-386408-2016 | 11/16/2016 2:37:17 PM | ASSESS: EL: Final | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 2 |  | 1 | General Working space or dedicated space is being used for storage | Bonding_required.png | file://x:/photopub/docs/0000000517/92a07ff6-9c3f-4f2f-b73c-557641ca156f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad18ec93_dfa0_4977_b390_14b886ccf465
ELIN-703715-2016 | EL-386408-2016 | 11/16/2016 2:37:17 PM | ASSESS: EL: Final | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 2 |  | 1 | General Working space or dedicated space is being used for storage | Equipment_clearances.png | file://x:/photopub/docs/0000000517/b2e97b39-984f-4ae4-833b-d0dbadb46e05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad18ec93_dfa0_4977_b390_14b886ccf465
ELIN-703715-2016 | EL-386408-2016 | 11/16/2016 2:37:17 PM | ASSESS: EL: Final | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 2 |  | 1 | General Working space or dedicated space is being used for storage | Equipment_clearances_2.png | file://x:/photopub/docs/0000000517/0efa5fd5-e8f6-4f52-8673-b244d988be13.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad18ec93_dfa0_4977_b390_14b886ccf465
ELIN-703715-2016 | EL-386408-2016 | 11/16/2016 2:37:17 PM | ASSESS: EL: Final | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 2 |  | 1 | General Working space or dedicated space is being used for storage | Exit_light.png | file://x:/photopub/docs/0000000517/1d496502-f270-4146-8fe8-279f20241bb5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad18ec93_dfa0_4977_b390_14b886ccf465
ELIN-679899-2016 | EL-395800-2016 | 10/7/2016 11:55:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 200 amp, 120/240 volt sub distribution panel de-energized but intended to be energized has panel cover not installed. Buss bars exposed to accidental contact by persons. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Panel_cover_to_sub_distribution_not_installed.png | file://x:/photopub/docs/0000000497/f87f19b8-c3f0-4eaf-aa98-625f26f64609.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27b72810_6b1a_4bcb_b2d3_4853a362a7c0
ELIN-689479-2016 | EL-422720-2016 | 11/1/2016 4:04:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | The 200 amp 120/240 volt main breaker at pole service does not include a grounding electrode, feeders from this pole service are overhead triplex cables with no bonding cabling, this can create a shock hazard at the pole | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Main_service_breaker_no_grounding.png | file://x:/photopub/docs/0000000510/e933a286-8951-40db-b6cc-906f57cc085b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6ca71f0_5f46_462a_8ea7_31f7b0ab1562
BPVOP-668506-2016 | BPV-244296-2015 | 9/21/2016 10:05:48 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Boiler_fire_tubes_water_side_.png | file://x:/photopub/docs/0000000494/44386edf-69d1-4961-bc7d-5a4c871ce49c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1c752e8_b5c1_47d3_90fd_714ffde733c5
ELIN-694346-2016 | EL-458682-2016 | 11/2/2016 4:21:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 2 | Grounding does exist for the temporary 60 amp 120/240 volt service tapped from the 400 amp 120/240 volt service however a hazard may exist should the contractor not install the grounding at the main service switch (meter/breaker combo) where required when the permanent service becomes energized, this could lead to an equipment damage and shock hazard in the future. No true hazard exists at this time | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Future__permanent__400_amp_service.png | file://x:/photopub/docs/0000000511/d015e475-8d8a-4104-b081-9abaa03334cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__52b97e5c_297e_40f9_b0fa_048c8afff5fb
ELIN-700177-2016 | EL-221551-2015 | 11/22/2016 10:13:48 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 3 | Main ground not installed. This is a shock and fire hazard as over current will not function correctly. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | A.png | file://x:/photopub/docs/0000000520/11be2e45-f2e1-4f38-95e2-5176cda53f06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59184da1_80c8_47c2_a1a5_7a218b454656
ELIN-710056-2016 | EL-420625-2016 | 11/24/2016 10:47:42 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | Service connection for new clubhouse. The metal service conduit nipple is not bonded to ground. This presents a potential shock hazard and also may affect service over-current device from functioning. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_bushing.png | file://x:/photopub/docs/0000000521/fa7a735b-b2fb-4fb3-a8bb-76c12c3862a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95ef21c7_9a4d_4435_8144_adf899472f2a
ELHE-670361-2016 | HE-442187-2016 | 9/26/2016 8:53:37 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | The service conduit is not supported by an approved method. The support can fail and this could damage the unprotected conductors and cause a fire. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Service_conduit.png | file://x:/photopub/docs/0000000490/40e8398d-b516-484b-a9bb-47b8bfdd1ae4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10f7eb5d_9a46_44be_8705_90043a19b460
ELIN-694346-2016 | EL-458682-2016 | 11/2/2016 4:21:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 2 | Grounding does exist for the temporary 60 amp 120/240 volt service tapped from the 400 amp 120/240 volt service however a hazard may exist should the contractor not install the grounding at the main service switch (meter/breaker combo) where required when the permanent service becomes energized, this could lead to an equipment damage and shock hazard in the future. No true hazard exists at this time | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Temporary_service_equipment.png | file://x:/photopub/docs/0000000511/e6cd4ff2-0540-4e79-876e-3711db7baf39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__52b97e5c_297e_40f9_b0fa_048c8afff5fb
ELIN-696160-2016 | EL-455906-2016 | 11/3/2016 2:29:31 PM | ASSESS: EL: Final | png | #asFound | EL157 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 4 | 4 | The 100amp 120/240 volt main breaker in the main panelboard is bolted into main panel and showing signs of burn marks and pitting at connections, this is a equipment damage issue | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | Loose_connections_2.png | file://x:/photopub/docs/0000000511/c92ae678-6e9b-48cb-89a7-1e0a16604be0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebd71191_b8bd_4f71_a564_7cd7b4570973
ELIN-696160-2016 | EL-455906-2016 | 11/3/2016 2:29:31 PM | ASSESS: EL: Final | png | #asFound | EL157 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 4 | 4 | The 100amp 120/240 volt main breaker in the main panelboard is bolted into main panel and showing signs of burn marks and pitting at connections, this is a equipment damage issue | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | Loose_connections.png | file://x:/photopub/docs/0000000511/46f0e24f-522b-437d-bf92-cec865a73c75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebd71191_b8bd_4f71_a564_7cd7b4570973
GAIN-677685-2016 | GA-447050-2016 | 10/11/2016 10:26:17 AM | ASSESS: GA: Rough-In | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Corrugated stainless steel gas line installed with out protection against puncture damage. | 2 | Physical protection of piping and tubing absent. | No_puncture_protection__.png | file://x:/photopub/docs/0000000498/ad7c0ad0-0f3b-4f74-987e-13b98015c150.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3dc3960_fa4b_495d_a899_b4f75a36455d
GAIN-677685-2016 | GA-447050-2016 | 10/11/2016 10:26:17 AM | ASSESS: GA: Rough-In | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Corrugated stainless steel gas line installed with out protection against puncture damage. | 2 | Physical protection of piping and tubing absent. | No_gas_puncture_protection_line_.png | file://x:/photopub/docs/0000000498/297c5e0a-23d8-4ae1-89aa-54e83095531f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3dc3960_fa4b_495d_a899_b4f75a36455d
GAIN-677685-2016 | GA-447050-2016 | 10/11/2016 10:26:17 AM | ASSESS: GA: Rough-In | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Corrugated stainless steel gas line installed with out protection against puncture damage. | 2 | Physical protection of piping and tubing absent. | No_puncture_protection_.png | file://x:/photopub/docs/0000000498/93552833-4cb3-482d-9843-d42f4123ab79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3dc3960_fa4b_495d_a899_b4f75a36455d
GAHE-704288-2016 | HE-467866-2016 | 11/15/2016 12:51:52 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | 500 gallon propane tank is directly beside combustible house wall with no clearance. | 3 | Clearance to combustibles not maintained | End_view_.png | file://x:/photopub/docs/0000000516/abb5a8f4-9006-4a20-969d-d0fa24ad47b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7add5c9c_5b74_46e5_aa97_762a09270e56
ELIN-709898-2016 | EL-385199-2016 | 11/25/2016 9:24:18 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 125 amp, 120/240 volt main distribution rated for indoor use only installed were subject to outdoor elements. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Enclosure_for_temp_to_perm_main_distribution.png | file://x:/photopub/docs/0000000521/802ae157-45fd-47b8-b00d-236031766988.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b3b7ea4_a385_43ed_ab9b_310f4ac100b1
GAIN-679840-2016 | GA-448311-2016 | 11/28/2016 9:52:44 AM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | Regulator must be installed as per manufacturers installation instructions. Vent limiter will not operate as designed if not installed in the correct orientation. | 2 | Not installed according to certified installation instructions | Vertical_mounted_regulator.png | file://x:/photopub/docs/0000000522/13d24504-4be8-4593-9434-aa3f0a0d42e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76e0aa1c_9fb7_47fd_9356_49b80b9ea163
ELIN-689307-2016 | EL-449781-2016 | 10/25/2016 9:26:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | Service non compliances | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Feeder_damage.png | file://x:/photopub/docs/0000000505/4ee48761-0add-4f32-ad11-25349a2d364d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bbc0e465_1215_40f7_9142_cc6d83dabd96
ELIN-689307-2016 | EL-449781-2016 | 10/25/2016 9:26:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | Service non compliances | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Panel_hole.png | file://x:/photopub/docs/0000000505/f4135e3e-de1a-4178-9829-cff240ce5927.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bbc0e465_1215_40f7_9142_cc6d83dabd96
ELIN-689307-2016 | EL-449781-2016 | 10/25/2016 9:26:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | Service non compliances | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Attachment_point.png | file://x:/photopub/docs/0000000505/dc67cd99-7edd-4514-a639-2e1c49a5b333.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bbc0e465_1215_40f7_9142_cc6d83dabd96
ELIN-689307-2016 | EL-449781-2016 | 10/25/2016 9:26:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | Service non compliances | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Garage.png | file://x:/photopub/docs/0000000505/24eff90e-6577-4dc0-9414-4fd79dd307f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bbc0e465_1215_40f7_9142_cc6d83dabd96
ELIN-678781-2016 | EL-291228-2015 | 10/13/2016 12:47:44 PM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | The exterior 15 amp 120 volt receptacles that are located in a wet and damp locations do not include weather protection covers on the deck areas, this can lead to moisture entering the receptacles and can become a thermal issue | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Exterior_receptacle.png | file://x:/photopub/docs/0000000500/e88586e6-d0f5-446d-bc5c-acc147fe1547.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46b81516_d6a7_4cef_882b_784caa5a678f
ELIN-691542-2016 | EL-457160-2016 | 10/27/2016 12:33:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Thermal and fire hazard due to shorting of conductors after possible mechanical damage from drywall screws etc. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable4.png | file://x:/photopub/docs/0000000506/e16b05ba-fb2d-4c2f-8000-2473f64d3671.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__947adc6e_961b_4bf0_942c_889e4cddd94b
ELIN-691542-2016 | EL-457160-2016 | 10/27/2016 12:33:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Thermal and fire hazard due to shorting of conductors after possible mechanical damage from drywall screws etc. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable1.png | file://x:/photopub/docs/0000000506/64086aa8-c964-4818-af68-f5efd3080597.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__947adc6e_961b_4bf0_942c_889e4cddd94b
ELIN-691542-2016 | EL-457160-2016 | 10/27/2016 12:33:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Thermal and fire hazard due to shorting of conductors after possible mechanical damage from drywall screws etc. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Heater1.png | file://x:/photopub/docs/0000000506/749c99df-30ff-4299-9e28-f46d8d65dbc9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__947adc6e_961b_4bf0_942c_889e4cddd94b
ELIN-691542-2016 | EL-457160-2016 | 10/27/2016 12:33:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Thermal and fire hazard due to shorting of conductors after possible mechanical damage from drywall screws etc. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable3.png | file://x:/photopub/docs/0000000506/0246a9eb-7caa-4617-bf65-a0dc06b85a14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__947adc6e_961b_4bf0_942c_889e4cddd94b
ELIN-691542-2016 | EL-457160-2016 | 10/27/2016 12:33:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Thermal and fire hazard due to shorting of conductors after possible mechanical damage from drywall screws etc. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable2.png | file://x:/photopub/docs/0000000506/bfa22be4-a3d5-49c8-8aa1-a81b20938d2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__947adc6e_961b_4bf0_942c_889e4cddd94b
ELIN-691542-2016 | EL-457160-2016 | 10/27/2016 12:33:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Thermal and fire hazard due to shorting of conductors after possible mechanical damage from drywall screws etc. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable5.png | file://x:/photopub/docs/0000000506/c593b22e-b399-4f79-8073-48b858b73a95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__947adc6e_961b_4bf0_942c_889e4cddd94b
ELIN-691704-2016 | EL-349430-2016 | 10/27/2016 2:39:17 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Shock hazard may present on gas line by becoming energized by a fault. | 3 | Equipment Gas line, cast or water pipe has not been bonded | No_bond.png | file://x:/photopub/docs/0000000506/3f4a6c98-93b2-4dd8-b81d-7d01916b2ca1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a670e075_3c40_4753_9833_5edcba441505
ELIN-691704-2016 | EL-349430-2016 | 10/27/2016 2:39:17 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Shock hazard may present on gas line by becoming energized by a fault. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Cable-2.png | file://x:/photopub/docs/0000000506/98d05cd8-f99d-4ae6-bbb7-03223c9ec510.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a670e075_3c40_4753_9833_5edcba441505
ELIN-691704-2016 | EL-349430-2016 | 10/27/2016 2:39:17 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Shock hazard may present on gas line by becoming energized by a fault. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Cable-1.png | file://x:/photopub/docs/0000000506/0e7d0053-e92f-4516-bf9e-8cae9aa2175e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a670e075_3c40_4753_9833_5edcba441505
BPVOP-665690-2016 | 2287907 | 10/21/2016 9:58:00 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP136 | 3.1.1 Safeties will not function - Pressure Relief Device Failed relief or pop test | 4 | 4 | During the inspection of a Domestic Hot Water Tank with MAWP of 125 psig, the pressure was rised to 90 psig for an attempt to hydro. The Safety Relief Valve had no tag, but in our records showed as a 75 psig set point. It did not pop at 90 psig. | 4 | 3.1.1 Safeties will not function - Pressure Relief Device Failed relief or pop test | Safety_Relief_Valve_with_no_tag.png | file://x:/photopub/docs/0000000504/5d657a53-e57d-4b48-bc05-d29008d62385.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73c3da6c_bfb8_4fda_8219_7a277a2c1578
GAHE-698372-2016 | HE-463773-2016 | 11/4/2016 7:53:59 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA024 | No protection Low traffic | 3 | 3 | No vehicle protection provided and tank does not have the required clearance to the combustible wall of the house. | 3 | No protection Low traffic | 2467_Vickers_Trail.png | file://x:/photopub/docs/0000000511/b22064ff-3977-487d-a06d-637bd527aca7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c68e0c2a_e0c3_454a_9db9_8cf84a14168e
ELIN-679288-2016 | EL-446918-2016 | 10/13/2016 1:13:07 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Multiple circuits rated between 15 and 30 amps 240 and 120 volts have been altered, added to, and changed in a commercial renovation. The conductors feeding these circuits were left connected to circuit breakers in a panelboard accessible to workers and public in general. If these circuits become energized they could present a risk for fire to the structure or touch step electric shock potential to persons | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Incomplete_circuits_connected_to_breakers_commercial_installation.png | file://x:/photopub/docs/0000000500/b55f53bb-af15-498a-9490-2a3635d737be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd1a8bae_4fb6_4f32_b092_a360ef8d73d3
GAOP-685031-2016 | 2170456 | 11/2/2016 10:07:37 AM | ASSESS: GA OP: Periodic | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | 1) The area around a propane tank shall be maintained free of combustible materials. 2) The area around the propane tank is non-maintained, trees and bushes have grown around and under the tank. Empty cylinders and waste materials are stored against the tank. 3) Combustible materials can create a hazard to the propane tank in the event of a fire. Clutter around the tank may limit access and be a hazard to fire fighting. | 3 | Clearance to combustibles not maintained | Undersized_fire_extinguisher_.png | file://x:/photopub/docs/0000000514/6913d532-8928-4e1a-b59e-16102c2f1547.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6FEDAFA6_7817_440E_A5E4_895CCB0A467C
GAOP-685031-2016 | 2170456 | 11/2/2016 10:07:37 AM | ASSESS: GA OP: Periodic | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | 1) The area around a propane tank shall be maintained free of combustible materials. 2) The area around the propane tank is non-maintained, trees and bushes have grown around and under the tank. Empty cylinders and waste materials are stored against the tank. 3) Combustible materials can create a hazard to the propane tank in the event of a fire. Clutter around the tank may limit access and be a hazard to fire fighting. | 3 | Clearance to combustibles not maintained | Materials_stored_against_dispenser_.png | file://x:/photopub/docs/0000000514/2fd48e1b-1eb1-484b-8a55-9277bc0f17b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6FEDAFA6_7817_440E_A5E4_895CCB0A467C
GAOP-660216-2016 | 2170499 | 11/8/2016 1:36:30 PM | ASSESS: GA OP: Periodic | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | 1) The area around the dispenser is required to be kept clear of combustible materials, weeds and grasses. 2) The area around the dispenser is cluttered with equipment, old cylinders weeds and grasses. 3) A build up of combustible materials can be a fire hazard to the tank and components. | 3 | Clearance to combustibles not maintained | Cache_Creek_dispenser_.png | file://x:/photopub/docs/0000000514/3332c5af-b4b8-491f-84e3-1652f60b1801.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01E554AF_07FC_4F2D_90F3_F38D71D86731
GAOP-660216-2016 | 2170499 | 11/8/2016 1:36:30 PM | ASSESS: GA OP: Periodic | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | 1) The area around the dispenser is required to be kept clear of combustible materials, weeds and grasses. 2) The area around the dispenser is cluttered with equipment, old cylinders weeds and grasses. 3) A build up of combustible materials can be a fire hazard to the tank and components. | 3 | Clearance to combustibles not maintained | Cache_creek_dispenser_2_.png | file://x:/photopub/docs/0000000514/91b549f7-770a-4662-88ad-0c50e73ff700.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01E554AF_07FC_4F2D_90F3_F38D71D86731
ELIN-700411-2016 | EL-457214-2016 | 11/10/2016 12:25:22 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Single lug/meter provided for dwelling unit with suite. | 0 | No Created Hazard Identified | Single_meter.png | file://x:/photopub/docs/0000000514/27984c8c-cc8d-49ea-8c43-5226d0d4d033.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f357b357_270e_4e53_bbdb_987cb8023a78
BPVOP-593349-2016 | 5361922 | 10/21/2016 10:36:53 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 1993 and was overdue as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_installed_in_1993.png | file://x:/photopub/docs/0000000504/b1ac7480-2689-496a-993d-a478b2356a97.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa9d8ff0_ecd2_4322_844c_42f654c55892
ELIN-683103-2016 | EL-446281-2016 | 10/25/2016 1:22:09 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Live electrical is not covered on outlets and switches,this presents a shock hazard to occupants of dwelling. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Example_of_cover_plate_missing_.png | file://x:/photopub/docs/0000000505/446ac210-f76f-4f2a-baa0-5e8df9e85c8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__581dce0b_66c3_4791_b6b8_a543f8b13b05
ELIN-683103-2016 | EL-446281-2016 | 10/25/2016 1:22:09 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Live electrical is not covered on outlets and switches,this presents a shock hazard to occupants of dwelling. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Light_with_no_ballast_cover_.png | file://x:/photopub/docs/0000000505/ffb9030c-c3e6-486b-8a3a-3458f796acad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__581dce0b_66c3_4791_b6b8_a543f8b13b05
ELIN-683103-2016 | EL-446281-2016 | 10/25/2016 1:22:09 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Live electrical is not covered on outlets and switches,this presents a shock hazard to occupants of dwelling. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Instructions_to_energize_defective_wiring_.png | file://x:/photopub/docs/0000000505/64f5f7f3-d75f-4a82-b636-2183561e7af3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__581dce0b_66c3_4791_b6b8_a543f8b13b05
ELIN-683103-2016 | EL-446281-2016 | 10/25/2016 1:22:09 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Live electrical is not covered on outlets and switches,this presents a shock hazard to occupants of dwelling. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Gas_line_and_skin_of_trailer_not_bonded.png | file://x:/photopub/docs/0000000505/4412a139-44f8-4a46-9453-9421ef02bc48.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__581dce0b_66c3_4791_b6b8_a543f8b13b05
GAIN-690030-2016 | GA-386536-2016 | 10/26/2016 4:44:16 PM | ASSESS: GA: Final | png | #asFound | GA118 | Clearance to a moisture exhaust duct | 2 | 2 |  | 2 | Clearance to a moisture exhaust duct | Moisture_exhaust.png | file://x:/photopub/docs/0000000505/28f95379-d0aa-4bdc-b66c-d1322eecc0ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78b5e869_297e_4b51_8a83_e9598e48e6ce
GAIN-690030-2016 | GA-386536-2016 | 10/26/2016 4:44:16 PM | ASSESS: GA: Final | png | #asFound | GA118 | Clearance to a moisture exhaust duct | 2 | 2 |  | 2 | Clearance to a moisture exhaust duct | Ball_check_position.png | file://x:/photopub/docs/0000000505/a06d690c-0a42-4ed0-bab2-f52fbbad8a17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78b5e869_297e_4b51_8a83_e9598e48e6ce
ELIN-684769-2016 | EL-449085-2016 | 10/25/2016 11:33:34 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Electrical heat trace has been fed with extension cord run through the floor of the home, across crawl space and cord connected to the equipment. Flexible cord can deteriorate or fail where it penetrates building construction and also provide for failure where additional cord connections fare required to feed the permanent electrical equipment. This can lead to damage to structures or injury to persons. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_run_through_floor_to_provide_power_to_permanent_heat_trace_equipment.png | file://x:/photopub/docs/0000000505/bc7497a1-f3b5-4431-9278-217b2c96968a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf00cf62_5b0e_4ae9_b0bb_5a326ff0cf3b
ELIN-701648-2016 | EL-464934-2016 | 11/14/2016 9:55:50 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | The service cable is over the allowed 1.5 meter distance within the building and is exposed to mechanical damage. Mechanical damage to this type of cable could create a significant fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable.png | file://x:/photopub/docs/0000000516/6a9d4b50-4f94-44ce-9e66-8514387522be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3328ba9_f079_4edb_8ac5_a12c47e03873
ELIN-702525-2016 | EL-384259-2016 | 11/14/2016 8:15:39 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Main distribution panel is energized with panel cover removed. The energized panel is open with energized metal bus bar parts creating a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Main_panel_open.png | file://x:/photopub/docs/0000000516/cd43d4e3-51bd-4c60-9d72-9a5e62f76a84.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20021a1d_c543_4726_918f_f3d7ee7aea80
ELOP-683453-2016 | 2200169 | 10/13/2016 1:22:07 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | This assessment found cables spliced without a box. Although well taped this joint is not protected within the required box thereby presenting a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Splice.png | file://x:/photopub/docs/0000000500/92c7fc19-6766-44e1-b9c5-57520b291aa9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7897140_bbcf_4ba2_8953_90b292ff3aa1
BPOP-670514-2016 | BPV-406323-2015 | 11/4/2016 7:16:58 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Service valve is closed but not plugged off. Valve could be left open or vandalized allowing high pressure gas to escape. This could cause a fire resulting in property damage or loss of life. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Unplugged_valve.png | file://x:/photopub/docs/0000000512/2e9952bb-6b65-49cc-8222-d6e724b5849d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc87ed65_d1ce_4298_845e_b9fc56259458
BPOP-670527-2016 | BPV-404944-2015 | 11/5/2016 4:06:42 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Service valve not plugged. Valve could be left open or vandalized allowing high Pressure Propane gas to escape. Ignition could take place resulting in fire ,property damage or loss of life. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 475_Black_Hill_Rd_.png | file://x:/photopub/docs/0000000512/0ad9a71c-e21c-4a00-853b-9e7e0db7c8ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb1a3591_15a0_4134_bff4_73321934497e
ELOP-708051-2016 | 5112236 | 11/23/2016 11:41:31 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dust_mitigation_for_multi_had__for_multi_head_saw.png | file://x:/photopub/docs/0000000520/4d8b03a1-f4cf-4660-9497-b8c48c538422.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed538189_53b5_4b5e_84d5_1a577363041c
ELOP-708051-2016 | 5112236 | 11/23/2016 11:41:31 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dust_clean_up__dust_clean_up_from_prior_assessment.png | file://x:/photopub/docs/0000000520/8845de44-2849-4ffd-b4ba-a59838494cbb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed538189_53b5_4b5e_84d5_1a577363041c
ELOP-708051-2016 | 5112236 | 11/23/2016 11:41:31 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Would_dust__would_dust_clean_up_from_prior_assessment.png | file://x:/photopub/docs/0000000520/9a30e634-4129-4052-a80e-0e8f2cc3d4a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed538189_53b5_4b5e_84d5_1a577363041c
ELOP-708051-2016 | 5112236 | 11/23/2016 11:41:31 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Area_under__Area_under_material_sorter__wood_dust_removed.png | file://x:/photopub/docs/0000000520/8df8d589-6701-4518-84fa-a288a81d25ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed538189_53b5_4b5e_84d5_1a577363041c
ELOP-708051-2016 | 5112236 | 11/23/2016 11:41:31 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Would_collectio.png | file://x:/photopub/docs/0000000520/3351e478-cf55-4abf-8768-225ff5710d6f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed538189_53b5_4b5e_84d5_1a577363041c
PROP-472237-2015 | PR-077872-2013 | 9/21/2016 2:50:43 PM | ASSESS: PR OP: Annual | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Dead trees near lift line could potentially fall on to the lift line. Particularly in high wind conditions. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Dead_trees_near_lift_line.png | file://x:/photopub/docs/0000000492/839e157d-ba2e-44bd-a665-ccafc1c49839.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cfc4f51_db7e_45f3_97c6_ab05e49d73b8
ELIN-678769-2016 | EL-391766-2016 | 10/6/2016 11:45:49 AM | ASSESS: EL: Final | png | #asFound | EL197 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no PPE in place. | 5 | 5 | Energized electrical equipment is required to be locked out or disconnected before any work is performed on the equipment. This is to protect the worker from exposure to an accidental shock or arc-flash. In this installation for a new 600A, 240V service, an electrical contractor disconnected energized overhead lines to the service to correct previous non-compliances. The contractor could have been exposed to a short circuit current greater than 24,000 amps if accidental contact was made with the conductors. The contractor was also exposed to an arc-flash hazard if one of the energized conductors made contact with one of the other ungrounded or grounded conductors. | 5 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no PPE in place. | Bare_live_OH_conductors.png | file://x:/photopub/docs/0000000497/5bce9ab8-57c7-41c6-be53-cabc56abe035.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90b7da10_bca6_4e10_a259_9c9668c5fcc3
ELIN-678769-2016 | EL-391766-2016 | 10/6/2016 11:45:49 AM | ASSESS: EL: Final | png | #asFound | EL197 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no PPE in place. | 5 | 5 | Energized electrical equipment is required to be locked out or disconnected before any work is performed on the equipment. This is to protect the worker from exposure to an accidental shock or arc-flash. In this installation for a new 600A, 240V service, an electrical contractor disconnected energized overhead lines to the service to correct previous non-compliances. The contractor could have been exposed to a short circuit current greater than 24,000 amps if accidental contact was made with the conductors. The contractor was also exposed to an arc-flash hazard if one of the energized conductors made contact with one of the other ungrounded or grounded conductors. | 5 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no PPE in place. | Previous_picture_of_EMT_mast.png | file://x:/photopub/docs/0000000497/9a144368-411b-4be5-b857-dabb0806e6ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90b7da10_bca6_4e10_a259_9c9668c5fcc3
ELIN-678769-2016 | EL-391766-2016 | 10/6/2016 11:45:49 AM | ASSESS: EL: Final | png | #asFound | EL197 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no PPE in place. | 5 | 5 | Energized electrical equipment is required to be locked out or disconnected before any work is performed on the equipment. This is to protect the worker from exposure to an accidental shock or arc-flash. In this installation for a new 600A, 240V service, an electrical contractor disconnected energized overhead lines to the service to correct previous non-compliances. The contractor could have been exposed to a short circuit current greater than 24,000 amps if accidental contact was made with the conductors. The contractor was also exposed to an arc-flash hazard if one of the energized conductors made contact with one of the other ungrounded or grounded conductors. | 5 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no PPE in place. | Hydro_xfmr_with_closed_cut_out.png | file://x:/photopub/docs/0000000497/953de21e-1fc4-4ff1-b6ac-0d50e3acbe86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90b7da10_bca6_4e10_a259_9c9668c5fcc3
ELIN-699389-2016 | EL-424873-2016 | 11/16/2016 2:12:26 PM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Approved electrical components are required to be used when jumpering meter sockets to provide temporary power to buildings that are under construction. This is required to prevent equipment from becoming damaged and to prevent persons or objects from contacting energized parts of electrical equipment. This electrical installation for a new commercial building under construction has two meter sockets (100A and 200A, 120/208V, 3 phase) that are jumpered out using short copper conductors that are under sized. The meter sockets are covered using thin plastic covers that were shipped with the equipment that are intended to prevent damage to the meter socket components. The meter sockets are energized. This is a potential shock hazard if the thin plastic covers are removed or fall off the meter sockets leaving exposed energized parts. It is a fire hazard if the jumpers are overloaded or if the contact points are insufficient or over loaded and thermally damage the meter socket components. | 3 | General Equipment is not approved for the specific use | Meter_stack_in_electrical_room.png | file://x:/photopub/docs/0000000517/816f5d78-e995-463a-8824-c67cc56675d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8aef342_c525_464e_8e53_4e5080f7fc18
ELIN-699389-2016 | EL-424873-2016 | 11/16/2016 2:12:26 PM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Approved electrical components are required to be used when jumpering meter sockets to provide temporary power to buildings that are under construction. This is required to prevent equipment from becoming damaged and to prevent persons or objects from contacting energized parts of electrical equipment. This electrical installation for a new commercial building under construction has two meter sockets (100A and 200A, 120/208V, 3 phase) that are jumpered out using short copper conductors that are under sized. The meter sockets are covered using thin plastic covers that were shipped with the equipment that are intended to prevent damage to the meter socket components. The meter sockets are energized. This is a potential shock hazard if the thin plastic covers are removed or fall off the meter sockets leaving exposed energized parts. It is a fire hazard if the jumpers are overloaded or if the contact points are insufficient or over loaded and thermally damage the meter socket components. | 3 | General Equipment is not approved for the specific use | Jumpered_meter.png | file://x:/photopub/docs/0000000517/2eec61b7-7ef9-476b-bdc1-67a4699736c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8aef342_c525_464e_8e53_4e5080f7fc18
ELIN-699389-2016 | EL-424873-2016 | 11/16/2016 2:12:26 PM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Approved electrical components are required to be used when jumpering meter sockets to provide temporary power to buildings that are under construction. This is required to prevent equipment from becoming damaged and to prevent persons or objects from contacting energized parts of electrical equipment. This electrical installation for a new commercial building under construction has two meter sockets (100A and 200A, 120/208V, 3 phase) that are jumpered out using short copper conductors that are under sized. The meter sockets are covered using thin plastic covers that were shipped with the equipment that are intended to prevent damage to the meter socket components. The meter sockets are energized. This is a potential shock hazard if the thin plastic covers are removed or fall off the meter sockets leaving exposed energized parts. It is a fire hazard if the jumpers are overloaded or if the contact points are insufficient or over loaded and thermally damage the meter socket components. | 3 | General Equipment is not approved for the specific use | New_comercial_building_under_construction_.png | file://x:/photopub/docs/0000000517/2fd91457-6624-445f-acf2-2cee9f844a3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8aef342_c525_464e_8e53_4e5080f7fc18
ELIN-699389-2016 | EL-424873-2016 | 11/16/2016 2:12:26 PM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Approved electrical components are required to be used when jumpering meter sockets to provide temporary power to buildings that are under construction. This is required to prevent equipment from becoming damaged and to prevent persons or objects from contacting energized parts of electrical equipment. This electrical installation for a new commercial building under construction has two meter sockets (100A and 200A, 120/208V, 3 phase) that are jumpered out using short copper conductors that are under sized. The meter sockets are covered using thin plastic covers that were shipped with the equipment that are intended to prevent damage to the meter socket components. The meter sockets are energized. This is a potential shock hazard if the thin plastic covers are removed or fall off the meter sockets leaving exposed energized parts. It is a fire hazard if the jumpers are overloaded or if the contact points are insufficient or over loaded and thermally damage the meter socket components. | 3 | General Equipment is not approved for the specific use | Meters_jumpered_with__10_awg_copper_conductors.png | file://x:/photopub/docs/0000000517/4d2ac4c2-3742-4de4-8c46-552ef4f76d39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8aef342_c525_464e_8e53_4e5080f7fc18
ELOP-683453-2016 | 2200169 | 10/13/2016 1:22:07 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | This assessment found cables spliced without a box. Although well taped this joint is not protected within the required box thereby presenting a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Connector_.png | file://x:/photopub/docs/0000000500/fd592802-532e-4f6d-8065-3447ef8dc903.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7897140_bbcf_4ba2_8953_90b292ff3aa1
ELOP-683453-2016 | 2200169 | 10/13/2016 1:22:07 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | This assessment found cables spliced without a box. Although well taped this joint is not protected within the required box thereby presenting a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Unapproved_saw_wiring.png | file://x:/photopub/docs/0000000500/49f86569-3896-494b-95f7-8795e819526a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7897140_bbcf_4ba2_8953_90b292ff3aa1
ELOP-683453-2016 | 2200169 | 10/13/2016 1:22:07 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | This assessment found cables spliced without a box. Although well taped this joint is not protected within the required box thereby presenting a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Unaproved_wiring.png | file://x:/photopub/docs/0000000500/a2927e14-befa-4159-bca8-c6726cfbdcd4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7897140_bbcf_4ba2_8953_90b292ff3aa1
BPOP-670516-2016 | BPV-404779-2015 | 10/7/2016 4:55:07 PM | ASSESS: Propane PV: Periodic | png | #asFound unplugged valve | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Service valve vapour port is not in use. Valve is closed but opening is not plugged. If vandalized (valve opened) it would release high pressure propane gas into the atmosphere.It could find a source of ignition resulting in fire and property damage. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 501_sibo_landfill_rd_.png | file://x:/photopub/docs/0000000504/e99e5896-3e16-4d1d-ab81-4c0f18d14abd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe25a957_fea4_40d0_89ac_4ef7a1698595
ELIN-681754-2016 | EL-396433-2016 | 10/31/2016 12:10:47 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | 15A 120V and 20A 120V receptacles installed for dwelling units are required to be tamper resistant type receptacles. This is required to protect persons from inserting conductive objects into the receptacle to prevent them from getting shocked or electrocuted. This installation has multiple 15A 120V receptacles installed in buildings, on the exterior of buildings and on posts in the yard that are not tamper resistant type receptacles. Left uncorrected this is a potential shock hazard if a person inserts a conductive object into a receptacle. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Non-tamper_resistant_receptacles_in_the_storage_buildings_and_the_shop.png | file://x:/photopub/docs/0000000507/0680fd20-2bfd-451c-bc22-ef022ed16ba5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925fe868_238a_4bd8_b3a1_17e168d91bf2
ELIN-681754-2016 | EL-396433-2016 | 10/31/2016 12:10:47 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | 15A 120V and 20A 120V receptacles installed for dwelling units are required to be tamper resistant type receptacles. This is required to protect persons from inserting conductive objects into the receptacle to prevent them from getting shocked or electrocuted. This installation has multiple 15A 120V receptacles installed in buildings, on the exterior of buildings and on posts in the yard that are not tamper resistant type receptacles. Left uncorrected this is a potential shock hazard if a person inserts a conductive object into a receptacle. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Storage_buildings.png | file://x:/photopub/docs/0000000507/e9b8f407-dcb1-4f1c-a42d-00be76c25a4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925fe868_238a_4bd8_b3a1_17e168d91bf2
ELIN-681754-2016 | EL-396433-2016 | 10/31/2016 12:10:47 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | 15A 120V and 20A 120V receptacles installed for dwelling units are required to be tamper resistant type receptacles. This is required to protect persons from inserting conductive objects into the receptacle to prevent them from getting shocked or electrocuted. This installation has multiple 15A 120V receptacles installed in buildings, on the exterior of buildings and on posts in the yard that are not tamper resistant type receptacles. Left uncorrected this is a potential shock hazard if a person inserts a conductive object into a receptacle. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Non-tamper_resistant_receptacle_on_exterior_of_building_.png | file://x:/photopub/docs/0000000507/2fd4dfaf-19eb-4aa4-a297-b39e6dabd70a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925fe868_238a_4bd8_b3a1_17e168d91bf2
ELIN-681754-2016 | EL-396433-2016 | 10/31/2016 12:10:47 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | 15A 120V and 20A 120V receptacles installed for dwelling units are required to be tamper resistant type receptacles. This is required to protect persons from inserting conductive objects into the receptacle to prevent them from getting shocked or electrocuted. This installation has multiple 15A 120V receptacles installed in buildings, on the exterior of buildings and on posts in the yard that are not tamper resistant type receptacles. Left uncorrected this is a potential shock hazard if a person inserts a conductive object into a receptacle. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | No-tamper_restant_recptacles_on_post_beside_the_garden_.png | file://x:/photopub/docs/0000000507/fe5c2f25-e956-411c-ba13-83988e0fd195.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925fe868_238a_4bd8_b3a1_17e168d91bf2
ELIN-681754-2016 | EL-396433-2016 | 10/31/2016 12:10:47 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | 15A 120V and 20A 120V receptacles installed for dwelling units are required to be tamper resistant type receptacles. This is required to protect persons from inserting conductive objects into the receptacle to prevent them from getting shocked or electrocuted. This installation has multiple 15A 120V receptacles installed in buildings, on the exterior of buildings and on posts in the yard that are not tamper resistant type receptacles. Left uncorrected this is a potential shock hazard if a person inserts a conductive object into a receptacle. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Non-tamper_resistant_receptacle_on_post.png | file://x:/photopub/docs/0000000507/74fe5637-ea26-4421-b606-fe6e6b6b03be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925fe868_238a_4bd8_b3a1_17e168d91bf2
ELIN-663557-2016 | EL-437691-2016 | 9/19/2016 6:20:37 PM | ASSESS: EL: Final | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Main outdoor disconnect has deteriorated neutral bar is showing signs of corrosion and main breaker has water damage. The hazard will be a thermal effect that will cause a fire if not corrected. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Panel_.png | file://x:/photopub/docs/0000000487/09991e18-01a7-4a38-b579-517dadd38c58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__16a39822_a83b_4a70_b36a_b19c8dbc6a82
ELIN-663557-2016 | EL-437691-2016 | 9/19/2016 6:20:37 PM | ASSESS: EL: Final | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Main outdoor disconnect has deteriorated neutral bar is showing signs of corrosion and main breaker has water damage. The hazard will be a thermal effect that will cause a fire if not corrected. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Inadequate_feeder_supports.png | file://x:/photopub/docs/0000000487/6d25eb6b-31e3-403c-acf1-98ea6eb7f9d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__16a39822_a83b_4a70_b36a_b19c8dbc6a82
ELIN-645592-2016 | EL-399895-2016 | 9/19/2016 10:59:49 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Conductors ( de-energized ) for switch are located by door way with no cover or wire nuts . If conductors were to become energized would be a significant shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Missing_switch.png | file://x:/photopub/docs/0000000487/e5c427ca-d199-4ba9-a726-d7bd128370a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d3d1ef0_8629_4c67_9237_1b4a3ef0d255
ELIN-645592-2016 | EL-399895-2016 | 9/19/2016 10:59:49 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Conductors ( de-energized ) for switch are located by door way with no cover or wire nuts . If conductors were to become energized would be a significant shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exterior_receptacle__.png | file://x:/photopub/docs/0000000487/271f5343-3e2e-41aa-8003-8d8e5771c6ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d3d1ef0_8629_4c67_9237_1b4a3ef0d255
ELIN-679115-2016 | EL-445408-2016 | 10/14/2016 12:00:56 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | Temporary construction service not constructed so as to protect electrical equipment for effects of weather. Water is found to be present on main overcurrent device and branch circuit breakers. This poses a serious risk of personal injury (shock) and property damage (thermal event) when equipment is energized. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Detail01_main_breaker.png | file://x:/photopub/docs/0000000500/3c7aa8cc-9e9f-43e5-b738-bfc3659e844f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7d9313e_f8a7_4f9d_bbbd_5391853be010
ELOP-684892-2016 | 3798341 | 10/16/2016 10:55:32 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | A 120/208V 100A Subpanel has been located in a bathroom which poses potential damage to the panel and components from the damp or wet environment in the bathroom. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_in_Bathroom.png | file://x:/photopub/docs/0000000501/67035bdb-540b-4eb9-8a72-73450a5c8fd2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5526f93_c584_4316_9878_535029137f4c
ELOP-624144-2016 | EL-408467-2016 | 9/21/2016 9:04:58 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | The conductors that feed RV receptacles on two services are not protected as they exit the ground. This exposes the conductors to possible damage by lawn maintenance equipment and this would create a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | RV_receptacle_feed.png | file://x:/photopub/docs/0000000488/db802ce8-256c-4f0c-86f8-d17b48ace33b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7C65A90D_73EE_4453_A65F_D190ECA41227
ELIN-667745-2016 | EL-436035-2016 | 9/21/2016 12:13:58 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 2 | At a rough wire assessment, branch circuit cabling installed in the ICF basement walls was found to be located at or near the surface of the styrofoam insulation. This wiring would be vulnerable to damage from nails once concealed just behind the drywall. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | NMD_in_ICF_walls_not_installed_deep_enough.png | file://x:/photopub/docs/0000000488/8030e8b2-4701-477f-b6b8-ef1c261971ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e50a6550_e7bd_4c6b_b787_199a7b2ad23b
GAIN-692711-2016 | GA-448107-2016 | 11/1/2016 9:23:30 AM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | Vent limiters installed in the vertical position. The limiters may not operate correctly installed in that position possibly allowing a larger volume of gas to escape into the occupied space. | 2 | Not installed according to certified installation instructions | Vent_limiter_position_.png | file://x:/photopub/docs/0000000509/be454e41-5eaa-4b38-b4b1-016fa9978d31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf627fea_31e8_4532_9b56_cfcf150fc3ed
EDIN-695802-2016 | ED-389603-2016 | 11/1/2016 3:25:42 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED057 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 2 | 2 | A safety zone violation at the bottom landing preventing access to the Stair Platform by the user from the call station. | 2 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 0002.png | file://x:/photopub/docs/0000000510/0f2c6381-9a40-4e4e-b7f0-4b41e6d0b5a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__364b6947_5680_46eb_80a3_bca7ceb5608c
EDIN-695802-2016 | ED-389603-2016 | 11/1/2016 3:25:42 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED057 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 2 | 2 | A safety zone violation at the bottom landing preventing access to the Stair Platform by the user from the call station. | 2 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 0001.png | file://x:/photopub/docs/0000000510/4d9a80ee-4d62-47ed-adb2-31b4bc4ff9c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__364b6947_5680_46eb_80a3_bca7ceb5608c
ELIN-686264-2016 | EL-392054-2016 | 10/26/2016 2:11:35 PM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | This assessment found an exterior outlet that did not have the type of weather proof cover, that protects even while a cord is inserted. There is a shock and fire hazard if the outlet becomes wet. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Exterior_outlet__wrong_cover.png | file://x:/photopub/docs/0000000506/713281d1-064a-4f3e-b74e-abd10d15d780.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__38fadbb0_e092_40fa_85af_eaf6c950f935
ELIN-690252-2016 | EL-437515-2016 | 11/1/2016 12:54:39 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service feeder is in fused and exposed on ground, if damaged would result in unprotected conductors that could cause shock or a thermal incident. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_feeder_not_protected.png | file://x:/photopub/docs/0000000510/71737dcb-09cf-4180-af01-af74933d70f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__811d48f3_2054_4ebf_adf6_324c06835ce6
ELOP-656106-2016 | EL-039303-2013 | 9/29/2016 7:59:54 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 4 | Combustibles around transformer are creating a fire hazard. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | Crane.png | file://x:/photopub/docs/0000000493/8400e86b-40b9-4fdc-9108-7056e9a1e9b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DEA2D5A1_74C1_4E71_A236_29F518FAF584
ELOP-656106-2016 | EL-039303-2013 | 9/29/2016 7:59:54 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 4 | Combustibles around transformer are creating a fire hazard. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | open_ko.png | file://x:/photopub/docs/0000000493/30282f14-e20b-408e-8d86-d28d7ffb867d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DEA2D5A1_74C1_4E71_A236_29F518FAF584
ELOP-656106-2016 | EL-039303-2013 | 9/29/2016 7:59:54 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 4 | Combustibles around transformer are creating a fire hazard. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | Deep_freezer.png | file://x:/photopub/docs/0000000493/3efbeeba-67ca-468b-97b9-efa5a72250c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DEA2D5A1_74C1_4E71_A236_29F518FAF584
GAIN-683598-2016 | GA-436018-2016 | 10/18/2016 10:24:52 AM | ASSESS: GA: Final | png | #asFound | GA085 | Regulator vent not terminated as per manufacturers instruction | 3 | 3 | Vent limiter not installed onto regulator. If malfunction occurs with regulator diaphragm, propane gas could leak out of vent for regulator possibly cause a fire due to the proximity of electrical equipment to regulator | 3 | Regulator vent not terminated as per manufacturers instruction | Missing_vent_limiter.png | file://x:/photopub/docs/0000000502/a5fadc11-7a0d-4ce8-b1e7-c16205078f2d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__77cad86a_e717_40b0_be99_63d3b92a4021
ELIN-695693-2016 | EL-445408-2016 | 11/3/2016 9:40:32 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Detail02_branch_circuit_breakers.png | file://x:/photopub/docs/0000000510/02e83510-4042-4c77-8d3b-6b0b1ddf999a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4dd24dc5_620e_4c31_8b68_9a5028c101da
ELIN-695693-2016 | EL-445408-2016 | 11/3/2016 9:40:32 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Detail01_service_compartment.png | file://x:/photopub/docs/0000000510/dce4cca1-9663-4dbe-bc97-9dadc1a43e84.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4dd24dc5_620e_4c31_8b68_9a5028c101da
BPVIN-687082-2016 | BPV-346879-2016 | 10/19/2016 11:17:05 AM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP140 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | 1 | 1 | Upon assessment it is determined that Tridicator temperature range is below code requirement but within operating range. There is no way to verify abnormal operation beyond normal operating condition. | 1 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | TRIDICATOR_WITH_TEMPERATURE_RANGE_BELOW_CODE_REQUIREMENT.png | file://x:/photopub/docs/0000000504/025896e5-62d5-4408-af7c-fc3211e84cea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5995d06_104b_46f4_afc5_88ae6d17312b
GAIN-675411-2016 | GA-445592-2016 | 10/21/2016 11:13:44 AM | ASSESS: GA: Final | png | #asFound | GA082 | Vent limiter style regulator not installed in a ventilated space | 3 | 3 | Ball check style vent limiting orifice is installed in the vertical position. In the event of diaphragm failure, the limiter would not limit the escape of natural gas to the required 2.5 cubic feet/hr. Also the regulator with vent limiting means is not installed in a ventilated space. This could cause an unsafe buildup of gas in the home, potentially leading to an explosion. | 3 | Vent limiter style regulator not installed in a ventilated space | Vent_limitir.png | file://x:/photopub/docs/0000000503/967658b9-83b9-4b5c-9b08-b8188aceb82a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7eea00aa_b9b9_4532_b8cf_f465b476d112
ELIN-674419-2016 | EL-425491-2016 | 10/10/2016 12:48:59 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | On a new 600volt 100amp service installation, the system ground conductor was found connected to the wrong connection point. This installation could lead to a thermal effect. Pic attached. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_connection.png | file://x:/photopub/docs/0000000499/15c65453-d2bd-4fc2-a0c8-a5bc6758ae3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bab5bb31_c02a_491d_b68d_b90a1f079285
GAIN-666741-2016 | GA-439760-2016 | 10/17/2016 12:25:38 PM | ASSESS: GA: Final | png | #asFound | GA068 | Improperly sized gas piping or tubing according to delivery pressure for a single appliance | 2 | 2 |  | 2 | Improperly sized gas piping or tubing according to delivery pressure for a single appliance | Gas_connector_too_small.png | file://x:/photopub/docs/0000000501/80e7dfae-3fe1-4a4a-a3c0-d984da862f27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28f17530_57e7_4bf0_98b6_78350cdb4aa2
ELIN-680261-2016 | EL-449057-2016 | 10/12/2016 12:26:19 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | At the time of a Service Connection assessment, the contractor had installed the service panel, rated for use indoors only, in the garage of a house under construction before the roof was on the house. This garage would be considered a wet location until a roof was installed as rainwater would be able to fall onto the electrical equipment. Damage to the equipment from water could result or a shock hazard should the service be connected. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Service_panel_installed_in_garage_with_no_roof_.png | file://x:/photopub/docs/0000000499/9f92d429-7a0d-4cd5-9d91-50878c3907ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da0db719_0a03_4388_afa7_332f9f0df4f9
ELIN-678428-2016 | EL-054773-2013 | 10/28/2016 7:35:35 AM | ASSESS: EL: Final | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 |  | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | PVC_box_connections.png | file://x:/photopub/docs/0000000510/3ca64b2a-04df-4cfe-9e7a-d2b7b241afdb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9db03ae_14ff_4f24_a45d_1ac9f19ba4c6
ELIN-678428-2016 | EL-054773-2013 | 10/28/2016 7:35:35 AM | ASSESS: EL: Final | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 |  | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | contoler_cable_support_and_disconnect_required.png | file://x:/photopub/docs/0000000510/a508f23c-908f-4848-b891-4aa5cb81ea4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9db03ae_14ff_4f24_a45d_1ac9f19ba4c6
GAIN-669684-2016 | GA-293782-2015 | 9/21/2016 2:27:39 PM | ASSESS: GA: Rough-In | png | #asFound | GA080 | Line pressure regulator without required overpressure protection in place | 3 | 3 | Pressure relief device must be installed to protect downstream equipment from overpressure should the regulator fail. | 3 | Line pressure regulator without required overpressure protection in place | Regulator.png | file://x:/photopub/docs/0000000489/cba84d25-7395-472b-9c9c-1d9fbfc3601e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__35fe4372_3b73_422f_81ec_801e83cc1f06
ELOP-683914-2016 | EL-325267-2015 | 10/25/2016 5:37:56 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | The Emergency Lighting is not functioning which could pose harm to persons who need to exit the buildings or other areas in an emergency or loss of power. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | EM_Pack.png | file://x:/photopub/docs/0000000507/ac8e2c51-5667-41f0-a6f4-60c5feb770db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b474633a_f26b_4317_9b11_2aa8b0a6d7fb
ELIN-691609-2016 | EL-353114-2016 | 10/27/2016 12:41:59 PM | ASSESS: EL: Service Connection | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Connector_on_branch_ccts.png | file://x:/photopub/docs/0000000506/3d9f9376-f203-43c1-ae66-0b13ee694b86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17b85e90_3739_4774_8031_266e9fcbddd1
ELIN-691609-2016 | EL-353114-2016 | 10/27/2016 12:41:59 PM | ASSESS: EL: Service Connection | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Inside_view_of_panel.png | file://x:/photopub/docs/0000000506/bd988957-c9b3-4e38-9bbd-1ad538ba8bd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17b85e90_3739_4774_8031_266e9fcbddd1
ELIN-691609-2016 | EL-353114-2016 | 10/27/2016 12:41:59 PM | ASSESS: EL: Service Connection | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Outlet_box.png | file://x:/photopub/docs/0000000506/414c1c8b-b64c-4050-aba0-d7b1990a3ed1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17b85e90_3739_4774_8031_266e9fcbddd1
ELIN-669034-2016 | EL-382356-2016 | 9/22/2016 9:00:25 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | 100 amp panel was energized without having the panel cover in place. This condition exposes the workers to a potential shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Cover_missing_.png | file://x:/photopub/docs/0000000490/40421bfe-a505-4d78-bc61-24ea26e9d2ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__163cd812_d4cc_4ba4_910b_3587a99ade86
ELIN-669256-2016 | EL-440234-2016 | 9/23/2016 11:41:32 AM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | The service equipment is mounted on a post that is not supported. Unsupported electric equipment can fall to the ground and be damaged and in turn this may create a shock hazard to people. | 0 | No Created Hazard Identified | TCS.png | file://x:/photopub/docs/0000000490/6ccca342-b64a-4ee5-8aed-ff15ef4f1c07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7be897d4_614c_44ca_8b53_34c27cc78cb3
ELIN-674614-2016 | EL-395800-2016 | 9/30/2016 11:08:42 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | 200 amp, 120/240 volt service conductor cable installed within 32 millimetres of stud edge. No mechanical protection provided. This could cause equipment damage. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | No_mechanical_protection_of_service_conductor.png | file://x:/photopub/docs/0000000493/f34032d6-7beb-472a-9491-a728d74708ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb8aea4d_24a8_4c53_a67a_d7cd2dde8c59
ELIN-674613-2016 | EL-395800-2016 | 9/30/2016 11:17:29 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | 15 amp, 120 volt outlet box greater then 100 millimetres supported on one side only. This could cause equipment damage. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Box_greater_then_100mm_supported_on_one_side_only.png | file://x:/photopub/docs/0000000493/fb381809-dfc5-4f40-838b-39fab27ce2f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8168bd3_0c6e_4232_b936_568a786a8cbc
ELIN-680624-2016 | EL-368474-2016 | 10/14/2016 3:17:35 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Receptacles in laundry areas are required to be on separate circuits or on the washing machine circuit. This is required so that occupants using clothes irons can plug into a receptacle that has a dedicated circuit to accommodate the load required by the iron. This installation has a laundry area that has a receptacle that is on a general purpose lighting/receptacle circuit. Left uncorrected this may cause the circuit to be overloaded. Circuits that are repeatedly overloaded can present a fire hazard if the circuit breaker is damaged or connections to the breaker or receptacle over heat and fail. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Receptacle_in_laundry_area_improper_circuit.png | file://x:/photopub/docs/0000000500/db3d28e9-7666-4136-8c08-b6d0780e0eb4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17a2e55b_8138_4ae2_a48d_5c0421b393dd
ELOP-684070-2016 | 5234898 | 10/13/2016 1:20:48 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Cables are required to be properly supported where they run to and between equipment. This is required to prevent the cables and cable terminations from getting damaged when accidentally snagged and from being left in locations where they are susceptible to damage. This installation has armoured cables that are not properly supported. Left uncorrected this is a potential shock and fire hazard if energized cables and their internal conductor's insulation is damaged and persons or objects contact them. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Unsupported_teck_cable_for_shingle_press_machine.png | file://x:/photopub/docs/0000000500/33d2eb2e-880e-4bd0-bfab-95832cec7631.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8327dcc8_8aed_40fe_9233_8a095529b86b
ELOP-684070-2016 | 5234898 | 10/13/2016 1:20:48 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Cables are required to be properly supported where they run to and between equipment. This is required to prevent the cables and cable terminations from getting damaged when accidentally snagged and from being left in locations where they are susceptible to damage. This installation has armoured cables that are not properly supported. Left uncorrected this is a potential shock and fire hazard if energized cables and their internal conductor's insulation is damaged and persons or objects contact them. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Unsupported_cable_for_shingle_press_machine_.png | file://x:/photopub/docs/0000000500/f9dc5869-a689-4b7a-a761-f3c4610314c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8327dcc8_8aed_40fe_9233_8a095529b86b
ELOP-684070-2016 | 5234898 | 10/13/2016 1:20:48 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Cables are required to be properly supported where they run to and between equipment. This is required to prevent the cables and cable terminations from getting damaged when accidentally snagged and from being left in locations where they are susceptible to damage. This installation has armoured cables that are not properly supported. Left uncorrected this is a potential shock and fire hazard if energized cables and their internal conductor's insulation is damaged and persons or objects contact them. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Unsupported_cable_at_saw_dust_hopper.png | file://x:/photopub/docs/0000000500/8aebf490-25fb-41b4-8c3c-7ca906086adf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8327dcc8_8aed_40fe_9233_8a095529b86b
ELOP-684070-2016 | 5234898 | 10/13/2016 1:20:48 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Cables are required to be properly supported where they run to and between equipment. This is required to prevent the cables and cable terminations from getting damaged when accidentally snagged and from being left in locations where they are susceptible to damage. This installation has armoured cables that are not properly supported. Left uncorrected this is a potential shock and fire hazard if energized cables and their internal conductor's insulation is damaged and persons or objects contact them. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Unsupported_cables_in_mill.png | file://x:/photopub/docs/0000000500/3e4cd2d0-1fbd-4598-bc8e-01ce0e152f47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8327dcc8_8aed_40fe_9233_8a095529b86b
PROP-683531-2016 | 2224030 | 10/13/2016 2:18:06 PM | ASSESS: PR OP: Annual | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | No fire alarm in machine room, in the event of a fire , attendant may not be made aware of a problem . | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Brockton_machine_room.png | file://x:/photopub/docs/0000000499/fc86c9fe-9c75-4927-9ed7-a3538928eee5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1fea4d9_dffd_47d3_8f28_9dd7a03acccf
ELIN-688648-2016 | EL-441561-2016 | 10/25/2016 11:20:22 AM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | Service raceways terminate in the top of the main service switch. This condition will allow condensation to form and drain into the switch which will result in corrosion forming inside the switch preventing it from operating correctly. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 3_inch_EMT_used_for_service_mast_.png | file://x:/photopub/docs/0000000505/8489ea59-6678-460d-b08d-f47b3df95866.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbc283ce_d1d6_43e6_a760_05e7de9300e5
ELIN-680624-2016 | EL-368474-2016 | 10/14/2016 3:17:35 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Receptacles in laundry areas are required to be on separate circuits or on the washing machine circuit. This is required so that occupants using clothes irons can plug into a receptacle that has a dedicated circuit to accommodate the load required by the iron. This installation has a laundry area that has a receptacle that is on a general purpose lighting/receptacle circuit. Left uncorrected this may cause the circuit to be overloaded. Circuits that are repeatedly overloaded can present a fire hazard if the circuit breaker is damaged or connections to the breaker or receptacle over heat and fail. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | New_house_under_construction.png | file://x:/photopub/docs/0000000500/d17852e9-60c4-4ec5-b2f2-0acce4c46758.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17a2e55b_8138_4ae2_a48d_5c0421b393dd
BPVOP-693947-2016 | 2267406 | 10/21/2016 5:49:12 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Hot Water Heating Boiler with Heating Surface (HS) of 25 square meter, MaximumAllowable Working Pressure (MAWP) of 100psig and Maximum Allowable Working Temperature (MAWT) of 250*Fahrenheit , it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_emergency_shutdown_switch_at_boiler_room_door.png | file://x:/photopub/docs/0000000507/2b0ba4a4-5912-4a0b-9c9e-029401e11ff6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a94b8f34_ce02_44ef_a32b_35253c248a41
BPVOP-679254-2016 | 4324549 | 10/17/2016 1:25:50 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Electric boiler (Power:24 Kilowatt, Maximum Allowable Working Pressure:100Psig) it is determined that safety valve has not been tested yearly. Failure to have safety valve tested yearly may lead to failure of safety to pop when boiler is subjected to pressure above Maximum Allowable Working Pressure . This could result in failure of pressure-boundary with rapid uncontrolled release of energy and may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_VALVE.png | file://x:/photopub/docs/0000000501/2da99b7d-e927-4db9-b83d-8c04f5c19f9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__B97C2D91_1502_4F12_95BF_EEF2E427B870
ELIN-668140-2016 | EL-430232-2016 | 9/26/2016 6:46:43 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | In a modular home, numerous 15amp 120volt outlets were found with covers not installed. This can lead to a shock hazard. Pic attached. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | No_covers.png | file://x:/photopub/docs/0000000491/b4c8c66c-eb37-400f-afb5-961902ec1c29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26374d25_409d_42d8_bab7_f8197d69f4a2
ELIN-688648-2016 | EL-441561-2016 | 10/25/2016 11:20:22 AM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | Service raceways terminate in the top of the main service switch. This condition will allow condensation to form and drain into the switch which will result in corrosion forming inside the switch preventing it from operating correctly. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Service_raceways_entered_in_top_of_main_switch_.png | file://x:/photopub/docs/0000000505/339d95b6-fadc-405c-9ad8-3e2ace726b5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbc283ce_d1d6_43e6_a760_05e7de9300e5
GAIN-672221-2016 | GA-309834-2015 | 10/3/2016 1:16:18 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | While assessing a boiler installation I found a boiler vent termination run in electrical conduit. This material is not intended for this use, and creates the high probability of the material failing. A failure would result in carbon monoxide entering the living space which would cause carbon monoxide poisoning. | 3 | Unapproved venting material | Vent_termination1.png | file://x:/photopub/docs/0000000494/40090ba9-f06d-48af-b1dd-19b8e339d683.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1beb9dbb_b3c1_476a_83df_0f443c518421
GAIN-672221-2016 | GA-309834-2015 | 10/3/2016 1:16:18 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | While assessing a boiler installation I found a boiler vent termination run in electrical conduit. This material is not intended for this use, and creates the high probability of the material failing. A failure would result in carbon monoxide entering the living space which would cause carbon monoxide poisoning. | 3 | Unapproved venting material | Vent_termination2.png | file://x:/photopub/docs/0000000494/245e4d2b-551b-47cb-bd9c-866c4d68e9fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1beb9dbb_b3c1_476a_83df_0f443c518421
ELIN-672242-2016 | EL-438128-2016 | 10/5/2016 8:53:12 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | A 15A 14/2 nonmetallic sheathed cable has been run exposed in a closet along the bottom baseboard trim where it is susceptible to mechanical damage. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Closet_Receptacle.png | file://x:/photopub/docs/0000000496/fe6e9409-221b-4ab6-9224-6873401ef07c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d93a4218_3ba5_4813_8df1_2430dd9f7d04
BPVIN-670520-2016 | UW-442327-2016 | 9/27/2016 10:57:39 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP120 | 3.0.1 Safeties will not function - Safety devices not functional, by-passed or missing with no back up corresponding safety/ operating control device | 5 | 5 | During the inspection of an Air Receiver part of a system was found a plug instead of the PRD. Also, in the system was found a PRD with a set point at 200 psig, while the vessel MAWP is 150 psig. | 5 | 3.0.1 Safeties will not function - Safety devices not functional, by-passed or missing with no back up corresponding safety/ operating control device | Safety_Relief_Valve.png | file://x:/photopub/docs/0000000491/7393f6dc-9b89-44ee-9f91-8dcf82f4e810.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__edf6c2d9_f04b_44a4_b2c5_a3086afee18e
BPVOP-670481-2016 | 3076738 | 9/27/2016 9:51:18 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP147 | 4.1.1 Incorrect readings/alarms - Reason to question the accuracy of the device | 2 | 2 | The pressure gauge it was marked NFG. | 2 | 4.1.1 Incorrect readings/alarms - Reason to question the accuracy of the device | Pressure_Gauge.png | file://x:/photopub/docs/0000000491/4fe84411-878c-4876-a7c0-3fcf033a0a3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7fe5adf2_92f8_4806_b0ec_835576d172d2
ELIN-672146-2016 | EL-439913-2016 | 9/27/2016 1:43:06 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Service supply bare neutral is in contact with service EMT. Possibility for service conduit to carry portion of unbalanced load as bonded electrical equipment. Potential for equipment damage or shock. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_supply_conductor_in_contact_with_service_EMT.png | file://x:/photopub/docs/0000000491/fdd27dcc-5903-4b68-80af-dde5de052088.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67043f12_9110_4b9f_ab54_e2b2179c0690
ELIN-670797-2016 | UW-442398-2016 | 9/26/2016 2:22:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL232 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | 4 | 4 | Electrical equipment operated in a Hazardous location. Wood dust producing facilities are a fire and explosion hazard is the dust is allowed to accumulate in sufficient quantities. | 4 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | D.png | file://x:/photopub/docs/0000000491/828e3c00-3b69-4b9a-8867-d6d79fd357af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__820cb0ef_b361_4d60_b937_ba445bbd6d3e
ELIN-673853-2016 | EL-240393-2015 | 9/30/2016 8:59:56 AM | ASSESS: EL: Final | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | Found 120 volt rated 15 amp circuit rated luminaires with bare bulbs installed in ceiling of clothes closet. When luminaires with bare bulbs are installed in clothes closets the electrical equipment could overheat combustible materials stored in clothes closets or the bare bulbs could become broken and could become a possible electrical fire or shock hazard to people or property. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | luminaire_.png | file://x:/photopub/docs/0000000493/33efc058-4ec3-4192-b828-378e6b909a73.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0fd5d20_0989_4d07_a747_c485e644c511
ELOP-656106-2016 | EL-039303-2013 | 9/29/2016 7:59:54 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 4 | Combustibles around transformer are creating a fire hazard. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | Open_ko2.png | file://x:/photopub/docs/0000000493/674058bb-71ac-4ce1-9844-e6ecc4e5a0c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DEA2D5A1_74C1_4E71_A236_29F518FAF584
ELOP-656106-2016 | EL-039303-2013 | 9/29/2016 7:59:54 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 4 | Combustibles around transformer are creating a fire hazard. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | No_strap.png | file://x:/photopub/docs/0000000493/fb9cf0f1-57c8-4e39-99cb-e14818340fda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DEA2D5A1_74C1_4E71_A236_29F518FAF584
ELOP-656106-2016 | EL-039303-2013 | 9/29/2016 7:59:54 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 4 | Combustibles around transformer are creating a fire hazard. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | Xmer.png | file://x:/photopub/docs/0000000493/98ce1e44-f4b3-42df-b1f8-a04c446bc286.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DEA2D5A1_74C1_4E71_A236_29F518FAF584
ELIN-674976-2016 | EL-444242-2016 | 10/6/2016 2:29:55 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | The grounding electrode has been terminated to a bonding lug in the 100A 120/240V Meterbase instead of at the neutral point in the main breaker section at the main panel. This could pose a shock hazard to persons as undesirable current may be present on the bonding system in the home, and the breakers may fail to operate under a fault condition as designed. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_Meterbase.png | file://x:/photopub/docs/0000000496/3fb9dbb7-96e2-4772-b8f4-844025335840.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ee46f5d_7d05_4aea_8f1a_97f636d4b7b8
ELIN-689338-2016 | EL-427589-2016 | 10/27/2016 12:34:09 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 15A 120V GFCI located next to the bathroom sink does not operate as designed, receptacle does not trip when tested and remains on, this poses a shock hazard to persons and potential equipment damage to items plugged into this receptacle. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Bathroom_Receptacle.png | file://x:/photopub/docs/0000000506/adbe1129-cc05-4350-b68e-02f668a078c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22619b4c_ab01_4ded_9ad7_0ff5e1ccad3a
ELIN-692313-2016 | EL-458122-2016 | 10/31/2016 1:18:32 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Pole has split and no guy this has an increased chance of failure and collapse. This would result in a shock hazard and possible fire. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Split_pole__no_guy.png | file://x:/photopub/docs/0000000508/281995ac-7498-409b-91f7-21de2308c340.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ab408c9_89b2_4cdc_b8e9_02f780b0c8f5
GAIN-510094-2016 | GA-319702-2015 | 10/24/2016 2:14:10 PM | ASSESS: GA: Final | png | #asFound | GA131 | Equipment service clearance non compliant | 1 | 1 |  | 1 | Equipment service clearance non compliant | Roof_access_.png | file://x:/photopub/docs/0000000505/7438241a-474a-4e12-a5b4-27e2aaf0aa4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44b5a0a4_8403_47db_be09_05704d2d2beb
GAIN-690471-2016 | GA-448641-2016 | 11/2/2016 4:16:26 PM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | If the regulator on the meter was to relive, the exists a possibility that fuel could be drawn into the appliance intake. Over fire condition resulting in damage to the appliance and the production of carbon monoxide . | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Ld.png | file://x:/photopub/docs/0000000510/da7b4381-98e5-4050-99c0-1aa44d75e12d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c326c283_a6f0_4254_b4d6_6e748c944ea3
BPVOP-689119-2016 | 2271434 | 10/20/2016 8:31:00 AM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP058 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | 3 | 3 | One feed water piping crack outside of the boiler was allowing high pressure and temperature water to escape and flash into steam, in the boiler furnace one tube overheated and cracked, allowing high pressure water to escape, this was contained within the boiler furnace, possible erosion of other water-wall tubes, if not corrected the possibility of combustion problems could occur. | 3 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | 13th_Water_wall_tube_from_rear_wall_leaking.png | file://x:/photopub/docs/0000000506/804945fe-0f56-4d13-83f5-221ad51b4b0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__982403c2_c9b1_4bef_b032_251c749e56e1
BPVOP-689119-2016 | 2271434 | 10/20/2016 8:31:00 AM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP058 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | 3 | 3 | One feed water piping crack outside of the boiler was allowing high pressure and temperature water to escape and flash into steam, in the boiler furnace one tube overheated and cracked, allowing high pressure water to escape, this was contained within the boiler furnace, possible erosion of other water-wall tubes, if not corrected the possibility of combustion problems could occur. | 3 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | FW_line_weld_neck_flange_butt_weld_leak.png | file://x:/photopub/docs/0000000506/51737e07-6b54-45c9-8c29-fd317ebd4dad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__982403c2_c9b1_4bef_b032_251c749e56e1
ELIN-692487-2016 | EL-437677-2016 | 10/28/2016 10:43:51 AM | ASSESS: EL: Service Connection | png | #asFound | EL199 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures • no PPE in place; and • qualified workers performing work. | 4 | 5 | Service conductor is NMD90 and does not have sufficient mechanical protection against a fault. Possibility for fire. | 4 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures • no PPE in place; and • qualified workers performing work. | NMD90.png | file://x:/photopub/docs/0000000507/b2f21cea-ff82-4293-8033-e82b93975cf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f3413a2d_4b1a_45d0_b43c_56542c0dd119
ELIN-691866-2016 | EL-453519-2016 | 11/2/2016 8:47:30 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unprotected service conductors are located in the interior cavity and extend beyond the allowed 1.5 m. The potential of damage to the conductors is increased by the additional length . This could result in a shock or fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Branch_CCTS_in_service_compartment_.png | file://x:/photopub/docs/0000000510/70ffc669-bee5-4dd4-a0a9-1fc087c421c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fdf7757_f6cf_4533_a3b5_dbf6bd3c1ce3
ELIN-694910-2016 | UW-461277-2016 | 11/1/2016 6:49:25 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 2 | Conduits could loose support due to expansion and contraction , this could cause equipment damage and possible shock hazard. | 3 | Conductors, No expansion joint or not installed correctly. | Control_wires_not_complete.png | file://x:/photopub/docs/0000000510/956dc3bf-c2b5-43e5-b497-a3bac77b8ae0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95af6ff4_ff49_4fd4_906c_be1c221f004b
ELIN-694910-2016 | UW-461277-2016 | 11/1/2016 6:49:25 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 2 | Conduits could loose support due to expansion and contraction , this could cause equipment damage and possible shock hazard. | 3 | Conductors, No expansion joint or not installed correctly. | P_clamps_on_exterior_PVC.png | file://x:/photopub/docs/0000000510/19d8d9e0-4004-4f17-8438-f738358c54cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95af6ff4_ff49_4fd4_906c_be1c221f004b
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dust_clean__dust_clean_up_record_page_2.png | file://x:/photopub/docs/0000000513/25e03c5e-7377-49bd-8a76-a7ed4d01a4a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dust_clean_up__dust_clean_up_records.png | file://x:/photopub/docs/0000000513/88285670-1b8d-42da-aaff-17675480e54f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Photo_one__Photo_one_accumulation_of_dust_under_equipment.png | file://x:/photopub/docs/0000000513/bf2db887-8d1a-47ac-b2e6-8eaa3c30a267.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dust_mitigatio__dust_mitigation_plan.png | file://x:/photopub/docs/0000000513/3ee63117-968b-4828-a65a-65b3f946b03a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | New_employee__New_employee_quiz_records_retained_in_personnel_file.png | file://x:/photopub/docs/0000000513/1e5bd3d3-6c0c-4f68-8408-63660eacb31a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Photo_three__Photo_three_dust_accumulation_under_electrical_equipment.png | file://x:/photopub/docs/0000000513/900975b5-9439-40c6-aed8-dc900bfb2ac3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Photo_for__Photo_for_dust_accumulation_under_electrical_equipment.png | file://x:/photopub/docs/0000000513/d984458b-2bd7-4c95-affd-f2a5f41986b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
GAIN-691308-2016 | GA-395244-2016 | 11/17/2016 8:47:53 AM | ASSESS: GA: Final | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | Uncertified piece of equipment connected to gas supply. Appliance has a CSA field certification which is not a recognized decal of certification. Uncertified equipment connected for use can be a high safety risk as they have not been appropriately tested for operation by a certification agency. | 3 | Uncertified appliance connected to gas supply but not in service | Uncertified_equipment_connected_to_gas_supply_.png | file://x:/photopub/docs/0000000517/88e0a43f-d037-4827-b039-053228785847.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b0b7ac1_0d83_4dcc_9166_6ac8eb66cf14
BPVIN-679105-2016 | BPV-442961-2016 | 10/11/2016 12:47:36 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP115 | 3.0.1 Safeties will not function - Safety Devices bypassed or failed but the back up corresponding safety devices operational | 4 | 4 | Upon assessment of hot water boilers with a maximum working pressure of 30 psig and maximum allowable working temperature of 200 Fahrenheit, there was no low-water fuel cut off installed. If the back up safety devices failed to operate under a low water level condition, the boiler could over pressure and seriously be damaged. | 4 | 3.0.1 Safeties will not function - Safety Devices bypassed or failed but the back up corresponding safety devices operational | Safety_relief_valve_installed_horizontally.png | file://x:/photopub/docs/0000000499/23eec4f7-199f-4230-82bd-7a05e28aff17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__622c9c5b_755c_450a_9685_db5ad2a6f37e
BPVIN-679105-2016 | BPV-442961-2016 | 10/11/2016 12:47:36 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP115 | 3.0.1 Safeties will not function - Safety Devices bypassed or failed but the back up corresponding safety devices operational | 4 | 4 | Upon assessment of hot water boilers with a maximum working pressure of 30 psig and maximum allowable working temperature of 200 Fahrenheit, there was no low-water fuel cut off installed. If the back up safety devices failed to operate under a low water level condition, the boiler could over pressure and seriously be damaged. | 4 | 3.0.1 Safeties will not function - Safety Devices bypassed or failed but the back up corresponding safety devices operational | Manual.png | file://x:/photopub/docs/0000000499/27071f11-8292-4dde-9ff2-8653776cb90c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__622c9c5b_755c_450a_9685_db5ad2a6f37e
ELIN-629047-2016 | EL-421958-2016 | 10/12/2016 1:47:31 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | In an existing modular home, a 120volt 15amp washroom receptacle was found without Ground fault protection in place. This can lead to a shock hazard. Pic attached. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Washroom_receptacle.png | file://x:/photopub/docs/0000000499/fccc1d37-0426-49a2-8734-feb1d258800e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95a36688_630c_4004_8470_a17f21efb072
ELIN-678870-2016 | EL-448052-2016 | 10/12/2016 1:27:22 PM | ASSESS: EL: Final | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | An unsecured junction box for splicing was installed in a drop ceiling. The loose box with no cable strapping near the box could create a fire or shock hazard if moved. The box could swing out and hit someone opening the ceiling tile as well. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Loose_junction_box.png | file://x:/photopub/docs/0000000499/1f8f4880-0d5e-4a38-9be0-e4735be12659.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b86d4e4_6eaf_46bd_a445_12aa2edb2f2b
EDIN-699629-2016 | ED-379332-2016 | 11/10/2016 8:34:52 AM | ASSESS: ED IN: Construction Use | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | A safe, guarded walking path across the roof to the elevator control room is required to protect personnel accessing the elevator control room. It was found during a section 5.10 elevator inspection that the guarded pathway was not completed. There is a roof fall hazard condition for personnel accessing the control room without a guarded pathway. This pathway is to access the control room for a newly installed 15 stop MRL traction elevator. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Pathway_across_roof.png | file://x:/photopub/docs/0000000514/a650604e-4f72-47cb-a5f5-f39aaf1627de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6b7b6c6_b836_4dfc_81aa_741754eef3c9
ELHE-703971-2016 | HE-467630-2016 | 11/10/2016 4:04:12 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL199 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures • no PPE in place; and • qualified workers performing work. | 4 | 4 | Persons performing electrical work on electrical equipment must de-energize the equipment unless the task can not be performed in the in the de-energized state. In this incident, an electrician for an educational institute entered a cable into an unmarked junction box in the ceiling that he believed was a 120 volt power circuit. The junction box was actually for a 347 volt lighting circuit. The electrician was attempting to splice the cable while the circuit was energized when he received a shock that entered through his right hand and exited through his left hand. The electrician was fortunate to only received a minor burn to his right hand and to not fall off his ladder when he received the shock. | 4 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures • no PPE in place; and • qualified workers performing work. | Junction_Box.png | file://x:/photopub/docs/0000000516/b2c2b2ca-e140-42b0-b664-6119e381a956.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1be508c9_7381_415d_9a66_325f2afcd45b
ELHE-703971-2016 | HE-467630-2016 | 11/10/2016 4:04:12 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL199 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures • no PPE in place; and • qualified workers performing work. | 4 | 4 | Persons performing electrical work on electrical equipment must de-energize the equipment unless the task can not be performed in the in the de-energized state. In this incident, an electrician for an educational institute entered a cable into an unmarked junction box in the ceiling that he believed was a 120 volt power circuit. The junction box was actually for a 347 volt lighting circuit. The electrician was attempting to splice the cable while the circuit was energized when he received a shock that entered through his right hand and exited through his left hand. The electrician was fortunate to only received a minor burn to his right hand and to not fall off his ladder when he received the shock. | 4 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures • no PPE in place; and • qualified workers performing work. | Burn_right_Index_finger.png | file://x:/photopub/docs/0000000516/6f13ba23-bef1-40e0-9d5a-7271ae29f12f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1be508c9_7381_415d_9a66_325f2afcd45b
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Photo_five__Photo_five_dust_accumulation_in_ceiling.png | file://x:/photopub/docs/0000000513/4d32944b-087c-4989-899e-ce70e7fa904b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Photo_six__Photo_six_dust_accumulation_under_electrical_equipment.png | file://x:/photopub/docs/0000000513/e1af8da3-883a-4fe1-9469-bf754042d1bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | New_employee__New_employee_quiz.png | file://x:/photopub/docs/0000000513/2b30077b-3609-4574-849e-3991843e52b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Office_of_the__Office_of_the_fire_commission_report.png | file://x:/photopub/docs/0000000513/37f145b6-6de6-42e7-90e6-e5d64a45b3a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Page_2__Page_to_dust_mitigation_plan.png | file://x:/photopub/docs/0000000513/69a04d79-3118-40f9-aeb3-f70b9d4d8c6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Photo_to__Photo_to_dust_accumulation_under_electrical_equipment.png | file://x:/photopub/docs/0000000513/193d0a5b-191a-44ef-8d6f-6d4117bb6936.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Monthly_crew__monthly_crew_safety_meeting_safety_meeting.png | file://x:/photopub/docs/0000000513/650f2e5e-3084-45af-8a6d-c6b57b2d014d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dust_mitigatio__dust_mitigation_clean_up_timeline.png | file://x:/photopub/docs/0000000513/e0670b48-b662-4311-9ea4-e6b9d2f57752.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Photo_seven.png | file://x:/photopub/docs/0000000513/66a1de1b-f2b3-4204-af9a-ffca90c2909b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Safe_work.png | file://x:/photopub/docs/0000000513/f865de65-e2b0-4826-80b9-69eb70a64ab8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
ELOP-695009-2016 | 371 | 11/7/2016 12:29:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Photo_eight__Photo_eight_dust_accumulation_under_electrical_equipment.png | file://x:/photopub/docs/0000000513/343f9202-ba3b-466f-b648-259ccb1f08b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e2ef47_0a5d_4121_968c_d31529b51864
GAIN-642202-2016 | GA-426039-2016 | 9/19/2016 1:16:01 PM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | Appliance connectors installed through wall | 2 | Certified appliance connector installed but not approved for application | Burgess.png | file://x:/photopub/docs/0000000487/a65f6055-9cd7-4bfe-9fc2-6611ce7d6cbb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6eec19fd_99b2_402f_98b8_8e1b48f6151f
GAIN-662556-2016 | GA-437083-2016 | 9/19/2016 9:49:21 AM | ASSESS: GA: Final | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | Water heater installed into 7" B-vent, This will cause spillage through the draft hood in colder weather, allowing products of combustion to enter residence. | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 103.png | file://x:/photopub/docs/0000000487/951bf756-156f-4f43-bec9-063c159acf32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bf70134_efec_4b22_bca1_668a01fcf539
ELIN-658563-2016 | EL-435480-2016 | 9/20/2016 11:05:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Incorrect roofing material | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Enclosure.png | file://x:/photopub/docs/0000000488/673528da-a508-4ee9-aff9-ba364f6762bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49ac7854_437e_4b84_894c_64a251e0ca3a
ELIN-665038-2016 | EL-388316-2016 | 9/26/2016 1:44:11 PM | ASSESS: EL: Final | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | An outdoor receptacle at grade operating at 120 volts has been tapped off of a circuit that feeds a bedroom. Outdoor receptacles must be robust to allow for use of high draw equipment outdoors. Circuits can sustain overloading and nuisance tripping if this requitpred ent is not met | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Exterior_at_grade_receptacle_not_on_dedicated_circuit.png | file://x:/photopub/docs/0000000491/a199f3da-e0da-493c-a3df-f126f212660c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2526da0e_84a0_4352_9b26_329418628c3f
ELIN-662120-2016 | EL-401620-2016 | 9/26/2016 12:36:36 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Arc fault protection was not provided for two circuits feeding 120 volt 15 amp receptacles in a residential dwelling designed to decrease the potential for fire for occupants and structure Equipment or building wiring can fault causing potential for property damage or injury to persons. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Afci_not_provided_exterior_and_convection_microwave.png | file://x:/photopub/docs/0000000491/9dfb116f-57a7-412e-a06b-9f33e69ee6cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aaae045b_aa89_427c_8028_fad33cb769e3
ELIN-668228-2016 | EL-416795-2016 | 9/21/2016 11:13:40 AM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | PVC_and_rigid_hub.png | file://x:/photopub/docs/0000000489/4ff276ee-fd76-478a-a065-51acc23d7b06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37d1c39e_d514_4b2a_81df_a742f4274ca6
ELIN-668228-2016 | EL-416795-2016 | 9/21/2016 11:13:40 AM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Duplex_Meter_base.png | file://x:/photopub/docs/0000000489/eda50202-d31c-4db5-b927-7d9e3fda2ba9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37d1c39e_d514_4b2a_81df_a742f4274ca6
BPOP-698463-2016 | BPV-404719-2015 | 11/5/2016 7:34:10 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Service valve on 500 GallonPropane Tank is unplugged. Valve could be left open or vandalized. If valve is opened high pressure Propane gas will escape could find source of ignition resulting in property damage or loss of life. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Unit_3___475_Black_Hills_Dr_.png | file://x:/photopub/docs/0000000512/b7ae5196-cec5-4c89-899f-b1065cd15065.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__339bf6fe_48e8_4d1f_a1e8_888cfbf9af78
BPOP-698466-2016 | BPV-404720-2015 | 11/6/2016 10:58:06 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Service valve closed but not plugged. Valve could be left open or vandalized allowing high pressure gas to escape. If source of ignition found could cause fire or explosion resulting in property damage or loss of life. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | unit_4_.png | file://x:/photopub/docs/0000000512/e9f654e6-d23a-4bc4-885f-fe444f003b38.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61feee05_484d_4c84_8fc5_ca96266bb711
BPOP-698469-2016 | BPV-404721-2015 | 11/6/2016 12:30:25 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Service valve not plugged. Valve could be left open or vandalized allowing high pressure gas to escape. If ignition takes place fire or explosion could cause property damage or loss of life. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | No_rain_cap_on_relief_valve.png | file://x:/photopub/docs/0000000512/92535d87-8251-4bf2-a968-c807e837d1e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10c6a33d_e223_46c2_9b79_64e7b1631a48
BPOP-698469-2016 | BPV-404721-2015 | 11/6/2016 12:30:25 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Service valve not plugged. Valve could be left open or vandalized allowing high pressure gas to escape. If ignition takes place fire or explosion could cause property damage or loss of life. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Unit_5__valve_not_plugged.png | file://x:/photopub/docs/0000000512/7ad73d60-d6be-4c8e-a44a-f883cf1349d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10c6a33d_e223_46c2_9b79_64e7b1631a48
BPOP-698468-2016 | BPV-404722-2015 | 11/6/2016 3:37:31 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | 1000 gallon Propane Tank service valve vapour port is not plugged. Valve could be left open or vandalized allowing high pressure gas to escape.Should a source of ignition be found fire or explosion could result causing property damage or loss of life. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Service_Valve_Not_Plugged.png | file://x:/photopub/docs/0000000512/0565c68a-caeb-4eae-99a2-19644e3cfc99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10966820_ab8f_4cb4_ba37_dc59a52742c7
BPOP-698470-2016 | BPV-404722-2015 | 11/6/2016 5:57:25 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Service valve not in use. Valve is closed but not plugged. Valve could be left open or vandalized allowing high pressure gas to escape. If ignition took place it would result in a fire or explosion causing property damage or loss of life. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Service_valve_wasp_nest_in_outlet.png | file://x:/photopub/docs/0000000512/80a963eb-c8c5-46c9-a734-18904ad15979.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__306151d1_3660_4cc8_92d1_f7411a19b855
BPOP-698470-2016 | BPV-404722-2015 | 11/6/2016 5:57:25 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Service valve not in use. Valve is closed but not plugged. Valve could be left open or vandalized allowing high pressure gas to escape. If ignition took place it would result in a fire or explosion causing property damage or loss of life. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Service_valve_not_plugged.png | file://x:/photopub/docs/0000000512/c924701b-4077-4c3c-aeb0-99ddc9556b72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__306151d1_3660_4cc8_92d1_f7411a19b855
GAIN-633668-2016 | GA-425510-2016 | 9/20/2016 3:52:55 PM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | Propane regulator relief vent under 4 feet from source of ignition. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Deka_fire_hall.png | file://x:/photopub/docs/0000000488/d721e554-5128-4a64-96b1-a05591a3589e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72aa957b_d178_48d0_894b_d27357c350fa
ELIN-673315-2016 | EL-444233-2016 | 9/29/2016 2:04:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Point_of_attachement_above_weatherhead__.png | file://x:/photopub/docs/0000000492/5ca86182-9eb4-4d82-bd96-e8894597a087.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96f30a15_0886_470e_8eab_0da253d9c910
ELOP-653115-2016 | EL-194685-2014 | 9/29/2016 8:53:30 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Armoured cable terminated in sub distribution panel. Sheathing of armoured cable is not in contact with metal connector. Cable sheaths in contact with metal connectors provide a mechanical connection of the bonding system. Bonding connections involving sheathing, enclosures and electrical equipment are required in order to have over- current devices operate properly. Failure of over-current devices may result in fire and shock. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Sheathing_of_armoured_cable_not_in_contact_with_connector.png | file://x:/photopub/docs/0000000492/ba03e43a-2544-460e-bb67-4354cbf1fac3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__B29A6BE3_2308_4FD4_925B_AD7091C5FCA2
GAIN-685696-2016 | GA-452509-2016 | 10/20/2016 11:07:57 AM | ASSESS: GA: Final | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | Black iron piping is passing through masonry without being wrapped or sleeved. Unprotected black iron piping in contact with masonry or concrete can be corrosive potentially leading to a gas leak. | 3 | Code prohibited practices or materials | Generator_piping.png | file://x:/photopub/docs/0000000503/1354ef40-5d7e-468a-a3e1-7886bb8e4e5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__230469f5_8fb3_42c7_a486_9b1a7ee33082
ELIN-696446-2016 | EL-457405-2016 | 11/3/2016 9:15:10 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | Grounding conductor not terminated at neutral bus at service box. Possibility of not properly clearing a fault. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Willow_grouse1.png | file://x:/photopub/docs/0000000510/2fdbff02-69b6-420d-b61b-d6cce45745c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8b37eea_53eb_4a6d_b211_6afbdc07dff1
ELIN-696446-2016 | EL-457405-2016 | 11/3/2016 9:15:10 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | Grounding conductor not terminated at neutral bus at service box. Possibility of not properly clearing a fault. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Willow_grouse_2.png | file://x:/photopub/docs/0000000510/90b6dace-7565-4ce5-a6f5-a7050d0b0f78.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8b37eea_53eb_4a6d_b211_6afbdc07dff1
BPVIN-699190-2016 | BPV-464401-2016 | 11/7/2016 12:43:05 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Clearances_.png | file://x:/photopub/docs/0000000512/f944e204-e9ea-44ea-8ebf-f0f6f9228de6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da6e8aaf_0f37_4106_a64d_400db94ee997
GAWP-668894-2016 | GA-386470-2016 | 9/21/2016 3:14:23 PM | ASSESS: GA Work In Progress | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | The moisture exhaust duct for the gas dryer became dislodged allowing the products of combustion to enter the occupied space. This may allow for carbon monoxide to enter the space possibly leading to illness or death of the occupants. | 5 | Venting system not connected or dislodged from energized appliance | Dryer_exhaust_duct.png | file://x:/photopub/docs/0000000488/0bb944ea-c717-40e6-a85e-277dcd793413.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47255ac3_4f3c_4c00_b02f_85a90f549c7e
ELIN-666705-2016 | EL-374309-2016 | 9/21/2016 12:38:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | This assessment found 2.13 M of service cable within the building. The cable was not concrete encased. Anything over 1.5 m is required to be encased in concrete. This extra protection is required as there is shock and fire hazard should this cable become damaged. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 7ft_of_service_cable.png | file://x:/photopub/docs/0000000488/be69cf34-adbe-4e74-a4e2-b921452bdf66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f812526_0fb5_4dd5_ba12_c7a599ab4f1d
ELIN-666082-2016 | EL-353259-2016 | 9/20/2016 11:46:55 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service cables are to be run on the outside of the building except when entering to connect to the service panel. The service cable is allowed a maximum of 1.5 meters inside the building unless the cable is encased in minimum 50mm of concrete. This requirement is to reduce the risk of fire because the service cable lacks effective over current protection. In this service cable installation for a single family dwelling, the cable was installed a total length of 2.2 m inside the building. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_cable_1250mm.png | file://x:/photopub/docs/0000000488/68528db6-a4ba-40f3-9903-e675841d6238.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30af1791_1642_4997_902a_fd0e1594701f
ELIN-666082-2016 | EL-353259-2016 | 9/20/2016 11:46:55 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service cables are to be run on the outside of the building except when entering to connect to the service panel. The service cable is allowed a maximum of 1.5 meters inside the building unless the cable is encased in minimum 50mm of concrete. This requirement is to reduce the risk of fire because the service cable lacks effective over current protection. In this service cable installation for a single family dwelling, the cable was installed a total length of 2.2 m inside the building. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_cable_950mm.png | file://x:/photopub/docs/0000000488/94245116-10e7-4abb-9427-a0a174713ef2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30af1791_1642_4997_902a_fd0e1594701f
ELIN-665264-2016 | EL-284430-2015 | 9/23/2016 1:21:28 PM | ASSESS: EL: Final | png | #asFound | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 4 | Lamp holders for ceiling lights not secured to outlet box so that energized 120v conductors are exposed in outlet box, increasing the possibility of accidental contact with energized conductors that may result in electrical shock. | 4 | Installation of electrical equipment Fixtures without suitable support. | Lamp_holders_hanging_from_ceiling_outlet_box.png | file://x:/photopub/docs/0000000490/816fcb2e-c6ee-4a58-9fca-d341021e38e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__462af6cd_e553_4dc0_a824_cbcafd9eadef
ELIN-700073-2016 | EL-455627-2016 | 11/8/2016 12:41:25 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Allowable length of service cable inside residence has been exceeded. Service cables are protected by utility overcurrent devices at the street. Exceeding this length within the residence without concrete encasing the cable may provide a risk of shock and fire to persons or property in the case of a cable fault. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Boarding_installed_where_service_cable_is_located_cable_is_in_excess_of_allowable_length_within_residence__.png | file://x:/photopub/docs/0000000513/6f5947f1-b37b-4dc8-9343-75a3deee71c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b7acd5ce_4dcd_40f2_b948_a6346d6a3c83
ELIN-699340-2016 | EL-464164-2016 | 11/9/2016 8:47:27 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #8 awg stranded conductor is terminated under wire binding screw, #8 is to large of a cable to terminate in this method, due to the fact that not all stranded conductors will be in contact with bonding screw and strap. Insufficient bonding may cause overcurrent devices to not react in the case of a fault, there is a possibility of shock and fire to persons and property. | 3 | Continuity Bonding; method for equipment is not adequate. | Bonding_is_not_adequate_due_to_size_of_cable_for_this_method_of_termination.png | file://x:/photopub/docs/0000000513/af1cac91-9683-4d07-83de-f7b23b70ba76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6bfe7ea3_3974_46d8_8a0f_b999077d8ec7
ELHE-705426-2016 | HE-468682-2016 | 12/7/2016 9:44:24 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | The power shed has exposed conductors from a service subfeed that could be energized. This is a shock hazard to anyone who might enter the power shed. | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | Service_conductors.png | file://x:/photopub/docs/0000000517/6bc36353-422d-4c91-99d8-cd839a3fac57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57dbb164_be1b_4448_a1f0_3b67e6065224
ELOP-623665-2016 | EL-379045-2016 | 11/17/2016 3:37:03 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | The open holes in the service metering cabinet are located within 3 feet of a charged sprinkler line. If broken or activated, the water would enter the main service splitter and would become a shock hazard to anyone entering the service room. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Metering_JB.png | file://x:/photopub/docs/0000000517/f629798c-c220-4645-8a70-bad4efc44328.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0FEC5A30_59C6_4A30_B298_CE3C4F972729
ELOP-699753-2016 | 5245 | 11/8/2016 3:21:29 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Computer_Desk.png | file://x:/photopub/docs/0000000513/4e67ff25-2888-43af-8c1f-f1cb1edafb82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3beb277_a737_49ec_a348_e76269f393aa
ELIN-697957-2016 | EL-339329-2016 | 11/5/2016 10:06:40 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | wall switches and thermostat located within 1m of shower stall not GFCI protected. Switch and thermostat could be reached from shower creating a shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Bathroom_switch.png | file://x:/photopub/docs/0000000513/3990d22c-d490-479a-9d35-4b07d70c7160.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__216a6ef7_8aec_422a_979a_f5482adce35b
ELIN-694438-2016 | EL-459763-2016 | 11/4/2016 10:44:35 AM | ASSESS: EL: Final | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | This assessment found two receptacles in a dwelling unit to be without the required bond wire connection. When properly connected this conductor provides a path back to the source, reducing the shock hazard by creating an equipotential plane. It also allows the over-current device to operate as intended, thereby reducing the fire hazard. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | open_bond.png | file://x:/photopub/docs/0000000511/379f5708-7d9d-403f-a9d1-1d750078b40a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6146cc9_a6db_4304_93f4_73855aa70d32
GAIN-680288-2016 | GA-449308-2016 | 11/8/2016 11:35:30 AM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | A gas leak was found inside burner cabinet of furnace. When furnace is turned on the flames are in close proximity of gas leak. This could cause a possible explosion in furnace cabinet or mechanical room American Standard seen in photo, the piping with the leaked is just under the burners of furnace | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Piping_where_leak_is_detected.png | file://x:/photopub/docs/0000000513/50b64d40-31ac-4753-ad9c-bbcf7e43f499.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c63b4bc6_7fae_40be_93ee_f8e6a8bd5f1d
GAHE-707076-2016 | HE-469688-2016 | 11/18/2016 4:36:11 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Exposed_poly_piping.png | file://x:/photopub/docs/0000000519/def29d13-3c3b-4e32-9739-dbaf6f655dc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__362c4f14_00cc_412c_a6ce_77b902162542
GAUP-669721-2016 | UW-441734-2016 | 9/22/2016 2:51:12 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound Very hard to take full size picture of non compliance however, American Standard seen wire is on top of fireplace | GA137 | Clearance to combustible not met | 3 | 3 | Electrical wiring for a Gas Fireplace was installed on top of fireplace. Clearances to combustible material is not met. Heat from the fireplace could melt the wiring possibly causing an electrical fire on top of fireplace. | 3 | Clearance to combustible not met | Wire_onto_of_fireplace.png | file://x:/photopub/docs/0000000489/17abcb85-6fab-46b2-90a5-d3047be951e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fb2d715_dacb_45bf_95ee_b178445ab1a6
GAIN-671590-2016 | GA-388241-2016 | 10/6/2016 1:45:14 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | Found pool boiler in operation without combustion air supply to enclosure. This will cause the production of excessive carbon monoxide. It could lead to carbon monoxide poisoning if someone was left inside the unventilated pool boiler enclosure. | 4 | Combustion air supply missing | Hayward.png | file://x:/photopub/docs/0000000496/80a5f5cb-4a37-460e-8016-9820dc80d326.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__803a68f5_dc27_4b6c_bf44_80667d8f1185
GAIN-671590-2016 | GA-388241-2016 | 10/6/2016 1:45:14 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | Found pool boiler in operation without combustion air supply to enclosure. This will cause the production of excessive carbon monoxide. It could lead to carbon monoxide poisoning if someone was left inside the unventilated pool boiler enclosure. | 4 | Combustion air supply missing | Vent.png | file://x:/photopub/docs/0000000496/0e7a83d1-cc9e-4235-9165-903af708c2c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__803a68f5_dc27_4b6c_bf44_80667d8f1185
EDRI-669697-2016 | ED-402432-2016 | 9/21/2016 1:44:58 PM | ASSESS: ED RI: Initial | png | #asFound | ED028 | Defect that results in loss of control but means of detection and/or stopping means are functional | 4 | 4 | During car top testing, with three people on the hoist roof, the hoist started an uncontrolled descent when the brakes were released and motors had not engaged first. When brakes were applied to stop the descent only one of two brakes engaged which was not able to slow or stop our descent. Another safety was in place that would have prevented the hoist from going over 2 meters per second. This additional safety did not engage as the one functioning brake prevented the descent from accelerating. Hoist ran into the buffer springs at the bottom of the hoist way, stopping the hoist. No injuries occurred. | 4 | Defect that results in loss of control but means of detection and/or stopping means are functional | Hoist_on_buffers.png | file://x:/photopub/docs/0000000489/79f94f03-8855-4db1-9d13-ea5d2df7eb6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a318099_911e_4dec_8cab_04ab5c4eb9e3
EDRI-669697-2016 | ED-402432-2016 | 9/21/2016 1:44:58 PM | ASSESS: ED RI: Initial | png | #asFound | ED028 | Defect that results in loss of control but means of detection and/or stopping means are functional | 4 | 4 | During car top testing, with three people on the hoist roof, the hoist started an uncontrolled descent when the brakes were released and motors had not engaged first. When brakes were applied to stop the descent only one of two brakes engaged which was not able to slow or stop our descent. Another safety was in place that would have prevented the hoist from going over 2 meters per second. This additional safety did not engage as the one functioning brake prevented the descent from accelerating. Hoist ran into the buffer springs at the bottom of the hoist way, stopping the hoist. No injuries occurred. | 4 | Defect that results in loss of control but means of detection and/or stopping means are functional | Failed_brake1.png | file://x:/photopub/docs/0000000489/f6253222-1f7a-49b1-97e9-3081004113d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a318099_911e_4dec_8cab_04ab5c4eb9e3
ELIN-617973-2016 | EL-217743-2015 | 10/6/2016 10:06:01 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | 200A 1PH Sub Feed from residential 400A 1PH service has been routed into commercial grocery store to supplement overloading of 400A 3PH commercial service. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 400A_3PH_Comm.png | file://x:/photopub/docs/0000000496/35a2604a-59c8-4ea0-a0b8-4079cb8e19fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34756386_a09f_4d77_9454_6153929dab49
ELIN-617973-2016 | EL-217743-2015 | 10/6/2016 10:06:01 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | 200A 1PH Sub Feed from residential 400A 1PH service has been routed into commercial grocery store to supplement overloading of 400A 3PH commercial service. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 400A_1PH_Res.png | file://x:/photopub/docs/0000000496/265865db-a881-4b31-8f6b-85adabf09562.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34756386_a09f_4d77_9454_6153929dab49
ELIN-617973-2016 | EL-217743-2015 | 10/6/2016 10:06:01 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | 200A 1PH Sub Feed from residential 400A 1PH service has been routed into commercial grocery store to supplement overloading of 400A 3PH commercial service. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Unprotected_Cable.png | file://x:/photopub/docs/0000000496/51230c75-5cdc-40e5-9ead-600f4807cbaf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34756386_a09f_4d77_9454_6153929dab49
ELHE-668367-2016 | HE-440756-2016 | 9/21/2016 9:49:46 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | Complaint of unsafe wiring in unit of apartment building. Occupants of a suite have altered the smoke detector circuit in their suite. This smoke detector circuit also provides local protection for other units. Should the circuit breaker trip or the circuit fail then occupants of other units would not have warning of danger from smoke in their unit. This is a life safety concern. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Smoke_detector_circuit_altered.png | file://x:/photopub/docs/0000000488/15638584-27a6-4fc5-bd9f-45065565526b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d85e3fc3_0a12_4069_aadd_27e1d3e2e099
ELIN-674232-2016 | EL-439494-2016 | 9/30/2016 12:42:04 PM | ASSESS: EL: Final | png | #asFound | EL083 | Continuity Separately derived system, communication or similar system has not been properly grounded | 4 | 4 | The transformer ground wire is spliced incorrectly. This could lead to a shock hazard. | 4 | Continuity Separately derived system, communication or similar system has not been properly grounded | Xformer_ground_splice.png | file://x:/photopub/docs/0000000493/05ad58f1-abae-4b04-b4ca-a7bc38459a81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fdc06b2e_7322_445b_a2a5_b7c7f7dc5998
ELIN-671881-2016 | EL-368045-2016 | 10/28/2016 5:05:51 PM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 3 | Service cables entering buildings and electrical equipment must be installed a in a way that will prevent water from entering the building and the electrical equipment. This is to prevent the equipment from rust and corrosion that can cause it to fail over time. This installation has two over head service cables entering a building and terminating into the back of a service switch. The cables are not sealed where they enter the building and the cable connectors and 600A, 120/240V service switch are not approved for a wet location or intended to prevent water from entering the equipment. This is a shock and fire hazard if over time the equipment becomes rusted or corroded and equipment or conductor terminations fail causing the equipment to become energized or over heated to the point that equipment or adjacent surfaces ignite. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Service_shed.png | file://x:/photopub/docs/0000000507/71b81bc2-85e2-4dc9-9d05-8e97991ee73a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__04604890_d031_4eb3_bc3f_f1f8c63e5042
ELIN-693365-2016 | EL-336578-2016 | 10/28/2016 4:56:27 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Feeder cables supplying power to sub-service equipment equipment must be properly sized to carry the load that they are supplying. This is required to prevent thermal damage to the cable, cable insulation, and the points where they terminate at equipment. This installation has 3 x #4/0 AWG feeder cables feeding 3 x 225A panel boards. The load on the panels are continuous lighting and air-conditioning loads that may overload the cables. Left uncorrected this is a potential fire hazard if cables or terminations over heat and fail. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Electrical_service_shed_in_fore_ground_and_detached_building_in_the_back_ground.png | file://x:/photopub/docs/0000000507/43524689-4859-4ecc-ae27-e066d0c25fd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__790f48ef_57c3_4c63_9da7_41da64900ed9
ELIN-671881-2016 | EL-368045-2016 | 10/28/2016 5:05:51 PM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 3 | Service cables entering buildings and electrical equipment must be installed a in a way that will prevent water from entering the building and the electrical equipment. This is to prevent the equipment from rust and corrosion that can cause it to fail over time. This installation has two over head service cables entering a building and terminating into the back of a service switch. The cables are not sealed where they enter the building and the cable connectors and 600A, 120/240V service switch are not approved for a wet location or intended to prevent water from entering the equipment. This is a shock and fire hazard if over time the equipment becomes rusted or corroded and equipment or conductor terminations fail causing the equipment to become energized or over heated to the point that equipment or adjacent surfaces ignite. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Cables_enter_the_back_of_the_switch_near_the_top.png | file://x:/photopub/docs/0000000507/1dc0d1b0-9084-426d-bf77-5222ffd3bd9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__04604890_d031_4eb3_bc3f_f1f8c63e5042
ELIN-693365-2016 | EL-336578-2016 | 10/28/2016 4:56:27 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Feeder cables supplying power to sub-service equipment equipment must be properly sized to carry the load that they are supplying. This is required to prevent thermal damage to the cable, cable insulation, and the points where they terminate at equipment. This installation has 3 x #4/0 AWG feeder cables feeding 3 x 225A panel boards. The load on the panels are continuous lighting and air-conditioning loads that may overload the cables. Left uncorrected this is a potential fire hazard if cables or terminations over heat and fail. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Sub_feed_cables_run_from_splitter_in_electrical_shed_to_detached_building_are_not_properly_sized_and_protected_from_over_current_.png | file://x:/photopub/docs/0000000507/f19269ee-7675-4d3c-88e7-eab4f2247b1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__790f48ef_57c3_4c63_9da7_41da64900ed9
ELIN-671881-2016 | EL-368045-2016 | 10/28/2016 5:05:51 PM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 3 | Service cables entering buildings and electrical equipment must be installed a in a way that will prevent water from entering the building and the electrical equipment. This is to prevent the equipment from rust and corrosion that can cause it to fail over time. This installation has two over head service cables entering a building and terminating into the back of a service switch. The cables are not sealed where they enter the building and the cable connectors and 600A, 120/240V service switch are not approved for a wet location or intended to prevent water from entering the equipment. This is a shock and fire hazard if over time the equipment becomes rusted or corroded and equipment or conductor terminations fail causing the equipment to become energized or over heated to the point that equipment or adjacent surfaces ignite. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Cables_entering_back_of_shed.png | file://x:/photopub/docs/0000000507/b6d94bb1-6032-468c-870e-c8ad2b88f003.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__04604890_d031_4eb3_bc3f_f1f8c63e5042
BPOP-700885-2016 | BPV-459801-2016 | 11/10/2016 10:36:52 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA023 | Inadequate protection Low traffic | 2 | 2 | Protection from traffic is not sufficient, possible damage from vehicles can severely damage tank or cause leakage | 2 | Inadequate protection Low traffic | National.png | file://x:/photopub/docs/0000000515/fcc978db-e0f0-4a17-b797-224270dc47c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa803077_2cd8_4e1e_8c2f_643a1167e70b
ELIN-672961-2016 | EL-443395-2016 | 9/28/2016 12:17:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Less than approved electrode depth may compromise service ground effectiveness. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Plate.png | file://x:/photopub/docs/0000000492/d3a7a12d-4fcb-4c55-97c7-403e5ac9080f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31a04d14_89df_441b_8b85_a55a608962fe
BPVOP-679455-2016 | 4093834 | 10/6/2016 1:53:45 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | During the inspection of a Domestic Hot Water Storage Tank with MAWP of 150 psig was found that the Safety Relief Valve was overdue so per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Overdue_SRV.png | file://x:/photopub/docs/0000000496/5981130d-13b5-4023-82ec-e380fbc89778.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebceec38_0f0e_4ec8_b392_2728fbc7efc2
ELIN-683755-2016 | EL-451554-2016 | 10/17/2016 1:26:46 PM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | Service connection for new single family dwelling. Receptacles installed do not have weatherproof cover plates and are open to the weather. This is a shock hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Receptacles_open__receptacles_open_to_the_weather_.png | file://x:/photopub/docs/0000000501/e48ea5ed-b62d-42fe-884d-86d61182afb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97925a11_48e2_46bf_8f64_b071ace52f29
GAHE-703325-2016 | HE-467134-2016 | 11/14/2016 12:29:10 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | 250 gallon propane tank has no clearance to combustible building wall. | 3 | Clearance to combustibles not maintained | 538_Fouquet_.png | file://x:/photopub/docs/0000000515/f3746ba9-d81e-4657-938a-f1e518f993d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af534dfb_b27e_4d26_8359_31dac41a9e8f
ELIN-706885-2016 | EL-469174-2016 | 11/23/2016 1:38:41 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Panel_cover__panel_cover_enclosure.png | file://x:/photopub/docs/0000000520/2d26f651-648c-47e4-9aae-acf6f37b8eec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c064e415_b9c8_478f_8b12_294a2e5777a0
ELIN-706885-2016 | EL-469174-2016 | 11/23/2016 1:38:41 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Condition_of__condition_of_branch_circuit_wiring_with_panel_open_no_power.png | file://x:/photopub/docs/0000000520/824e6017-dfda-46a3-9d0a-898d853dc303.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c064e415_b9c8_478f_8b12_294a2e5777a0
ELIN-709598-2016 | EL-467716-2016 | 11/24/2016 10:28:54 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL070 | Effective bonding and grounding The identified conductor is not provided or is not longer functional. | 4 | 4 | In a sub-distribution connection for a residential electrical service the neutral on the feeder conductor is required to be connected to the neutral lug at the panel and not bonded to the panel. This is to prevent neutral currents from circulating through the bonding system and to carry any unbalanced fault currents back to the source. In this installation, a home owner connected the neutral conductor to a bonding lug in the panel. This could lead to circulating currents in the bonding of the panel and create a shock hazard to persons. | 4 | Effective bonding and grounding The identified conductor is not provided or is not longer functional. | Service_panel.png | file://x:/photopub/docs/0000000520/67d5786e-b16d-4bf4-9522-3cc33057b310.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3bbf5e6_f9fd_464b_80dc_9b65669e616d
ELIN-683031-2016 | EL-435041-2016 | 10/14/2016 2:26:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Panel_covered_with_poly.png | file://x:/photopub/docs/0000000500/33f8d5be-8c24-42fe-b387-2874aad43c97.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ad3a238_4ba3_4c11_b5cf_dab451db2c61
ELIN-683031-2016 | EL-435041-2016 | 10/14/2016 2:26:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | No_roof.png | file://x:/photopub/docs/0000000500/e6cb16c8-126f-4fa7-9155-75ef71fdd5f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ad3a238_4ba3_4c11_b5cf_dab451db2c61
GAHE-689641-2016 | HE-456122-2016 | 10/24/2016 10:05:17 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | The As Found condition of the system showed 6 uncapped branch lines on the gas piping. The As Found hazard is uncapped gas lines can lead to gas entering into the building envelope leading to potential fire, explosion, or asphyxiation by occupants. | 5 | Open gas line connected to fuel supply (no cap/plug) | Uncapped_1.png | file://x:/photopub/docs/0000000504/b2204906-054a-44f5-816b-bcd5db694368.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea8d964c_cca7_4eb5_8410_a073e0425b18
GAHE-689641-2016 | HE-456122-2016 | 10/24/2016 10:05:17 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | The As Found condition of the system showed 6 uncapped branch lines on the gas piping. The As Found hazard is uncapped gas lines can lead to gas entering into the building envelope leading to potential fire, explosion, or asphyxiation by occupants. | 5 | Open gas line connected to fuel supply (no cap/plug) | Uncapped_4.png | file://x:/photopub/docs/0000000504/0247bb5e-c5ce-48b8-b1fd-bf7a271d9158.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea8d964c_cca7_4eb5_8410_a073e0425b18
GAHE-689641-2016 | HE-456122-2016 | 10/24/2016 10:05:17 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | The As Found condition of the system showed 6 uncapped branch lines on the gas piping. The As Found hazard is uncapped gas lines can lead to gas entering into the building envelope leading to potential fire, explosion, or asphyxiation by occupants. | 5 | Open gas line connected to fuel supply (no cap/plug) | Uncapped_3.png | file://x:/photopub/docs/0000000504/04c704c7-ae58-4170-9f60-907902342f49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea8d964c_cca7_4eb5_8410_a073e0425b18
GAHE-689641-2016 | HE-456122-2016 | 10/24/2016 10:05:17 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | The As Found condition of the system showed 6 uncapped branch lines on the gas piping. The As Found hazard is uncapped gas lines can lead to gas entering into the building envelope leading to potential fire, explosion, or asphyxiation by occupants. | 5 | Open gas line connected to fuel supply (no cap/plug) | Uncapped_5.png | file://x:/photopub/docs/0000000504/10cc904e-5b22-470e-9df0-83cdb8b947d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea8d964c_cca7_4eb5_8410_a073e0425b18
ELIN-693088-2016 | EL-448651-2016 | 11/3/2016 5:55:34 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL134 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | 3 | 3 | Outlet box not adequately supported. This poses a risk of personal injury (shock) or property damage (thermal event) due to mechanical damage to conductors or cabling. | 3 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | View01_dryer_outlet_box.png | file://x:/photopub/docs/0000000511/c2e74201-ec4b-40d5-bfb7-0d009496c1b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__786694c7_0a1c_4055_ba71_6dbc358a24e7
ELIN-670797-2016 | UW-442398-2016 | 9/26/2016 2:22:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL232 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | 4 | 4 | Electrical equipment operated in a Hazardous location. Wood dust producing facilities are a fire and explosion hazard is the dust is allowed to accumulate in sufficient quantities. | 4 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | F.png | file://x:/photopub/docs/0000000491/ff4a415e-5bbf-4d6a-a214-c0e697e3a45c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__820cb0ef_b361_4d60_b937_ba445bbd6d3e
ELIN-670797-2016 | UW-442398-2016 | 9/26/2016 2:22:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL232 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | 4 | 4 | Electrical equipment operated in a Hazardous location. Wood dust producing facilities are a fire and explosion hazard is the dust is allowed to accumulate in sufficient quantities. | 4 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | C.png | file://x:/photopub/docs/0000000491/e8f4f37c-f842-486d-a30e-de234b8ee64f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__820cb0ef_b361_4d60_b937_ba445bbd6d3e
GAIN-641994-2016 | GA-430921-2016 | 9/27/2016 2:14:48 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | The regulator vent may leak gas near a source of ignition in the event of regulator failure. | 2 | Not installed according to certified installation instructions | Flex_connector_not_protected_from_damage_.png | file://x:/photopub/docs/0000000491/2be309ba-bdea-47b8-8e39-f0fdf8da7494.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a33702d7_87c3_47c9_a86e_10cd86ba5d06
GAIN-641994-2016 | GA-430921-2016 | 9/27/2016 2:14:48 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | The regulator vent may leak gas near a source of ignition in the event of regulator failure. | 2 | Not installed according to certified installation instructions | Regulator_installed_improperly.png | file://x:/photopub/docs/0000000491/42b747c2-7203-4a26-965b-5dd332b835ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a33702d7_87c3_47c9_a86e_10cd86ba5d06
ELIN-688678-2016 | EL-419703-2016 | 10/28/2016 10:52:18 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | The receptacle beside a sink has no GFCI protection. This could be a shock hazard for a person using the sink that could have an electric appliance plugged into the receptacle. | 0 | No Created Hazard Identified | Suite_receptacle.png | file://x:/photopub/docs/0000000505/fdf20ed2-63c5-417e-8067-438c5e0eec15.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ee16cc2_12d7_44a2_8f4f_dcf879876042
GAIN-675712-2016 | GA-445869-2016 | 10/4/2016 12:25:34 PM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Tubing must be approved for underground use. Un-approved tubing is subject to damage and possible leak. | 3 | Non-compliant material/fittings installed | Un-approved_tubing.png | file://x:/photopub/docs/0000000495/830ca15e-1998-4563-a7a0-522d00347d9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3af576ec_018d_4a6a_9089_74be8888f13b
GAIN-645046-2016 | GA-345882-2016 | 10/4/2016 4:56:37 PM | ASSESS: GA: Final | png | #asFound | GA069 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | 3 | 3 | Undersized tubing can cause appliances to be underfired, resulting in improper combustion and possible flashback | 3 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | Undersized_tubing.png | file://x:/photopub/docs/0000000495/59f86e97-e900-4bae-8091-4e8277c95d36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00ac0d93_a7aa_4bd1_9aed_80d5624aa4ff
GAIN-670466-2016 | GA-425604-2016 | 10/4/2016 2:48:07 PM | ASSESS: GA: Final | png | #asFound | GA045 | Gas connector passes through wall, floor, ceiling, partition or into appliance | 2 | 2 |  | 2 | Gas connector passes through wall, floor, ceiling, partition or into appliance | Connector.png | file://x:/photopub/docs/0000000495/571617a9-413d-4a1e-8656-a00a512bae86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fef8fc05_e316_4649_9e99_e835dbc054ee
GAHE-703453-2016 | HE-467241-2016 | 11/14/2016 2:30:52 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Combustible materials are stored too close to tank and building is covering the tank. Retaining wall on back side of tank is made with creosote railway ties. | 3 | Clearance to combustibles not maintained | 316_Dutch_Lake.png | file://x:/photopub/docs/0000000515/11d37880-4b69-4aaf-9676-00f89c855515.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__344efb70_cc1f_4bf0_862e_9fa47c65a277
BPOP-670483-2016 | BPV-404862-2015 | 10/31/2016 11:44:53 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | Pressure gauge not readable due to corrosion, unable to ascertain volume in tank | 0 | No Created Hazard Identified | Rusty_gauge.png | file://x:/photopub/docs/0000000508/3d2a33b5-ca81-41b7-9edf-6cdcf2cd1d75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e281978a_44d4_4e67_afb6_9eed346993fd
BPOP-670483-2016 | BPV-404862-2015 | 10/31/2016 11:44:53 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | Pressure gauge not readable due to corrosion, unable to ascertain volume in tank | 0 | No Created Hazard Identified | Data_plate.png | file://x:/photopub/docs/0000000508/6131ffac-f25c-4edc-9362-cb48ffbcfce9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e281978a_44d4_4e67_afb6_9eed346993fd
BPOP-670483-2016 | BPV-404862-2015 | 10/31/2016 11:44:53 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | Pressure gauge not readable due to corrosion, unable to ascertain volume in tank | 0 | No Created Hazard Identified | No_propane.png | file://x:/photopub/docs/0000000508/8f8ad272-92fc-4f65-a25d-d066aafdcd14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e281978a_44d4_4e67_afb6_9eed346993fd
ELIN-698784-2016 | EL-458833-2016 | 11/8/2016 8:11:27 AM | ASSESS: EL: Final | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | 8' high output electronic fluorescents luminaries are located below 2.1 meters without mechanical protection. This could be a hazard to persons or property if someone was to break the fluorescent bulbs. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Located_below_2___1_meters.png | file://x:/photopub/docs/0000000513/d3d4cbc1-8b29-45ca-956d-636d2329ab72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8dc13a26_2756_4f6d_a7e3_42f7f6539f9d
ELIN-700217-2016 | EL-457808-2016 | 11/9/2016 2:29:23 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | 200 amp, 120/240 volt temporary to permanent main distribution panel and meter base installed on temporary wall that is not braced properly. Down bracing only supported to temporary wall and not to ground. This could cause equipment damage. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Bracing_to_wall_only_and_not_to_ground_.png | file://x:/photopub/docs/0000000514/2c1a28ce-d92c-4e8e-b4b4-4365c33414a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96c487ff_d8ce_4b1d_9bce_c16e6ee20b36
ELOP-693493-2016 | 369 | 11/14/2016 12:30:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Accumulations_of__accumulations_of_dust_and_cable_tray-typically_observed_throughout_mill.png | file://x:/photopub/docs/0000000515/f6a07d30-4217-45ca-8ad8-1cf9150f9d4c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e196c3a9_270c_49f4_8ea6_8feed5c14cf4
ELOP-693493-2016 | 369 | 11/14/2016 12:30:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Does_the__dust_accumulation_from_vibrator.png | file://x:/photopub/docs/0000000515/dde8aa74-b754-4c83-964a-08c2a3776149.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e196c3a9_270c_49f4_8ea6_8feed5c14cf4
ELOP-693493-2016 | 369 | 11/14/2016 12:30:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Repairs_is__repair_is_required_at_waist_conveyor_M8.png | file://x:/photopub/docs/0000000515/65e5bb92-a37f-44f3-bd50-bdd3b34ba345.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e196c3a9_270c_49f4_8ea6_8feed5c14cf4
ELOP-693493-2016 | 369 | 11/14/2016 12:30:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Fire_safety__fire_safety_plan.png | file://x:/photopub/docs/0000000515/fb5b54bb-1761-4bbe-b4df-a3cebeed6041.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e196c3a9_270c_49f4_8ea6_8feed5c14cf4
ELOP-693493-2016 | 369 | 11/14/2016 12:30:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dust_clean.png | file://x:/photopub/docs/0000000515/6032c9fa-8e68-4bdc-9ad4-36501c3f343e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e196c3a9_270c_49f4_8ea6_8feed5c14cf4
ELOP-693493-2016 | 369 | 11/14/2016 12:30:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Accumulation_of__accumulation_of_dust_from_the_mill_under_floor_chain.png | file://x:/photopub/docs/0000000515/c50118a1-6025-4a1d-b6b6-749159114a77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e196c3a9_270c_49f4_8ea6_8feed5c14cf4
ELOP-693493-2016 | 369 | 11/14/2016 12:30:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dust_accumulati__dust_accumulation_on_floor_under_mill.png | file://x:/photopub/docs/0000000515/2d34f246-c4ca-4c4a-a368-8acf2837bfc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e196c3a9_270c_49f4_8ea6_8feed5c14cf4
ELOP-693493-2016 | 369 | 11/14/2016 12:30:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Delta_Cedar__Delta_cedar_product_dust_mitigation_plan.png | file://x:/photopub/docs/0000000515/34df59be-19db-4d0b-8a9e-afd7fae90160.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e196c3a9_270c_49f4_8ea6_8feed5c14cf4
ELOP-693493-2016 | 369 | 11/14/2016 12:30:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | As_found_a__as_found_accumulation_of_dust_and_motor_control_room.png | file://x:/photopub/docs/0000000515/e4b23dd5-539e-4461-9463-e0e25de5a578.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e196c3a9_270c_49f4_8ea6_8feed5c14cf4
ELOP-693493-2016 | 369 | 11/14/2016 12:30:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Work_safe_BC.png | file://x:/photopub/docs/0000000515/8a1d6a67-32f0-4600-844d-fc1316916edd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e196c3a9_270c_49f4_8ea6_8feed5c14cf4
ELOP-693493-2016 | 369 | 11/14/2016 12:30:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Work_safe_BC__work_safe_BC_dust_mitigation_cleaning_brochure.png | file://x:/photopub/docs/0000000515/ddcac9d5-0430-40ee-a66b-5c548d549830.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e196c3a9_270c_49f4_8ea6_8feed5c14cf4
ELOP-693493-2016 | 369 | 11/14/2016 12:30:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | New_employee.png | file://x:/photopub/docs/0000000515/f333e609-dda3-41ed-914f-c4a7d387fa29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e196c3a9_270c_49f4_8ea6_8feed5c14cf4
ELHE-682971-2016 | HE-450665-2016 | 10/12/2016 6:40:57 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cord is not approved for use, and is subject to mechanical damage and environmental damage being used as fixed wiring. The hazards are both thermal and shock from not being protected from the environment . | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_strapped_to__pedestal_.png | file://x:/photopub/docs/0000000500/078e0671-b91d-48d3-99d4-9989695cb325.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__765a783f_2f36_4a33_a12d_7fbb59a61682
ELHE-682971-2016 | HE-450665-2016 | 10/12/2016 6:40:57 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cord is not approved for use, and is subject to mechanical damage and environmental damage being used as fixed wiring. The hazards are both thermal and shock from not being protected from the environment . | 4 | Conductors, Misuse of flexible cords. | Cab_tire_in_panel.png | file://x:/photopub/docs/0000000500/e99279a9-7191-4c07-83ba-b07ed333d6a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__765a783f_2f36_4a33_a12d_7fbb59a61682
GAIN-700843-2016 | GA-388228-2016 | 11/18/2016 3:53:04 PM | ASSESS: GA: Rough-In | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | The as found condition is a direct vent boiler installation in a mechanical room without ventilation air being provided as required by the manufacturer. The as found hazard is that the lack of ventilation air can lead to excessive heat affecting the electronic safety components on the boilers. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | System_Manual_statement.png | file://x:/photopub/docs/0000000518/6783c069-6760-46b4-bda0-c2cebcb2e4e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__769a2e57_02e2_4a7d_94fc_6d7d5784d107
ELIN-706685-2016 | EL-461309-2016 | 11/21/2016 2:42:28 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | This assessment found that a multi gang switch box was not supported as required. There is a hazard the equipment could come loose and break presenting a shock/fire hazard. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Four_gang_box.png | file://x:/photopub/docs/0000000519/90a31a42-0a8e-4f15-8b5a-1ab561ab1729.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a5be035a_0285_4e04_a97d_c4800436db92
ELIN-706430-2016 | EL-469278-2016 | 11/21/2016 1:52:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 |  | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Unisulated_bond.png | file://x:/photopub/docs/0000000519/a84600d4-a33a-48ee-963e-fc34348c2765.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31d3a7c3_f904_4c22_9642_d559f33ae3e3
PROP-598679-2016 | 3125256 | 10/28/2016 1:55:42 PM | ASSESS: PR OP: RAP | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | It was observed that it was possible to open the electrical drive control enclosure (480 V, contains VFD) with the door open and the disconnect mechanism in the on position. It is possible to open enclosure door without the use of the disconnect door release defeating mechanism. This results in an arch flash hazard to an unqualified person as it is possible to energize the VFD and it associated contacts and protection circuits energized with the enclosure door open. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Electrical_enclosure_with_door_open.png | file://x:/photopub/docs/0000000509/978a1cae-921e-4ca8-ad52-7b956731da81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__AF021853_AEFE_4F66_9110_A3C4099DF5C6
PROP-598654-2016 | 3213339 | 10/26/2016 6:01:30 PM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | It was noted that at multiple location that belts guide sections had become loose and it was possible to lift or move them by hand. Ropeway code indicates that a clearance between the top of the belt to the bottom of the belt guide must be less than 5mm. Loose belt guides could result in the clearance being in excess of 5mm resulting in a pinch hazard to people equipment and limbs (fingers/toes). | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Fasteners_used_to_retain_belt_guide_pulled_out_of_decking.png | file://x:/photopub/docs/0000000509/3a10529c-4b27-418b-9731-7ff9c9ed4e93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__297EBB3B_7443_4FEC_BE73_C23B310E10FB
PROP-598650-2016 | 3213338 | 10/28/2016 4:46:22 PM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | It was observed that a section of belt guide has come loose at the incoming end. This results in a pinch hazard to rider which are at risk of either theirs skis or limbs becoming entrapped under the loose guide. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Guide_not_secured_to_deck.png | file://x:/photopub/docs/0000000509/50e0c812-5669-41c9-a147-3454f093dcf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55886AB3_5F0B_48E3_8C98_2C7EB7BF98DF
ELIN-666115-2016 | EL-439353-2016 | 9/26/2016 6:56:17 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | In the 200 amp 120/240 volt panel the mechanical connection between the bonding and grounding has been removed. This poses a shock hazard and possibly may prevent the breakers from operating as designed, as undesirable current may be present on the bonding conductors and would not be cleared without the path to ground. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Bonding_strap.png | file://x:/photopub/docs/0000000491/f0780af3-8cd2-4e50-9f58-65d2546b4164.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8cc9310_4ccd_4afe_a0bc_7d0d17280dad
GAHE-682748-2016 | HE-450926-2016 | 10/21/2016 1:58:46 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dryer_blaze.png | file://x:/photopub/docs/0000000505/1b1b3863-03ab-4252-9e79-49569964158e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__232332a8_5a8a_4089_90e9_91fa36452a90
ELIN-688589-2016 | EL-282758-2015 | 10/28/2016 12:00:24 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | Branch circuits operating on 15 amp breakers and a 40 amp breaker at 240 volts are Non metallic sheathed cable enclosed in walls and in bottom of trusses in a building housing chickens and rabbits. Rodent activity is common in buildings with livestock due to storage of feed, bedding and other attractants. Non metallic sheathed cable is subject to damage that could cause property damage and injury to livestock or persons. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Nmd_90_and_standard_dry_location_covers_and_equipment_in_building_housing_livestock.png | file://x:/photopub/docs/0000000506/4123feab-195d-45a2-b9df-837a1d1e78e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a32dba5_6c0e_41c7_a7ca_a42e39ef394e
ELIN-684614-2016 | EL-407932-2016 | 10/26/2016 11:05:54 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | A 200 amp 240 volt single phase armoured cable is not bonded on one end of the service feeder. The armour of cables must be electrically continuous to ensure proper operation of overcurrent protection should cable armour become energized. Injury to persons or damage to structures can occur as a result o this noncompliance. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Service_cable_armor_not_bonded_on_service_end_sleeved_pvc_conduit.png | file://x:/photopub/docs/0000000505/af3778a4-fc7d-42b4-9fd7-6db4232b8313.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5888a705_7220_459f_ada0_9d8c1393977b
ELIN-677711-2016 | EL-443096-2016 | 10/26/2016 11:13:27 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Energized non-compliant entry addition wiring evidence confirms wiring installed by non-qualified individual Energized non-compliant entry addition wiring installed by non-qualified individual may present a shock hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Service_.png | file://x:/photopub/docs/0000000505/e69f7e51-67fc-4fff-851a-5c60b2bf2bf2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61a4b1fe_e849_4045_b327_3120f7132719
ELIN-677711-2016 | EL-443096-2016 | 10/26/2016 11:13:27 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Energized non-compliant entry addition wiring evidence confirms wiring installed by non-qualified individual Energized non-compliant entry addition wiring installed by non-qualified individual may present a shock hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Non_compliant_addition_wiring.png | file://x:/photopub/docs/0000000505/8e8657c8-eb52-4d15-89ac-d69462be0f99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61a4b1fe_e849_4045_b327_3120f7132719
ELIN-691496-2016 | UW-457804-2016 | 10/26/2016 12:58:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Overhead service conductors are located below 2.5 meters above flat roof. This could be shock hazard if someone was to grab these conductors while doing maintenance on the roof. These conductors are protected from the supply authority fusing, which is over fused due to feeding multiple units from one transformer. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Overhead_service_conductors.png | file://x:/photopub/docs/0000000505/b4253a62-5a9b-4f75-bb59-c737a2266f58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcc9d937_68d3_4b30_9402_87f6cfb4cfb9
ELIN-701371-2016 | EL-466028-2016 | 11/14/2016 3:07:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical equipment intended and approved for installation in dry locations is not permitted to get wet. Water on or inside electrical equipment intended for installation in dry locations can damage equipment by causing it to rust, corrode, short out and fail. This installation has a new 200A 120/240V service panel, main breaker, 15A branch circuit breakers, and 15A, 120V ground fault circuit interrupter (GFCI) receptacles that are installed in a new house under construction. The roofing material has not been installed on the house yet and rain water has entered the house and the electrical equipment. This is a potential shock and fire hazard if the wetted electrical equipment is energized. Circuit breakers and GFCI receptacles that have been wet may be damaged and fail to operate correctly at the time they are energized or in the future due to corrosion, rust, and internal component damage. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Meter_base__.png | file://x:/photopub/docs/0000000515/4d9a2d85-46b3-4135-9933-beaa222415e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1dc3170_0164_4cb5_85d3_16ea4d1f8d13
BPOP-670637-2016 | BPV-405348-2015 | 10/18/2016 11:36:25 AM | ASSESS: Propane PV: Periodic | png | #asFound | BP107 | 3.0.1 Safeties will not function - Pressure Relief Device No drain hole provided in the device body or discharge piping to allow drainage of liquids | 2 | 2 | Rain cap missing and weep hole plugged. Relief valve full of water | 2 | 3.0.1 Safeties will not function - Pressure Relief Device No drain hole provided in the device body or discharge piping to allow drainage of liquids | Prv.png | file://x:/photopub/docs/0000000502/df37f918-0b71-4b25-8549-fff27c9a7026.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11850947_8e2c_459b_95a5_9989c6a272b5
BPOP-670622-2016 | BPV-405252-2015 | 10/18/2016 9:11:19 AM | ASSESS: Propane PV: Periodic | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Relief valve service interval exceeds 25 years | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Relief_valve_rain_cap.png | file://x:/photopub/docs/0000000502/06b4eda1-7002-404f-8ac2-91e2d2949ef5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ce51fe6_e5bf_4500_bd34_8dd4e50cbd29
ELIN-709086-2016 | 4239156 | 11/24/2016 9:12:41 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed 32mm from the face of structural members when they pass through them. This is required to prevent damage to the cables from nails and screws both during and after construction. This installation for wiring of a recreation and guest room had NMSC installed less than 32mm from the face of structural members where they pass through them. This was a shock and fire hazard if wiring is damaged by nails, screws, or other fasteners secured to the walls either during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Interior_of_rec-guest_room.png | file://x:/photopub/docs/0000000520/ca37239a-8d30-490d-a14a-25fc54d690ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a85408c_4037_4c1c_aa69_c81e429de0b9
ELOP-704418-2016 | 3900093 | 11/16/2016 9:10:22 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Non metallic electrical wiring is without a box to contain the wiring splices at the end of the run. This creates a potential shock hazard. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Loose_cab_tire.png | file://x:/photopub/docs/0000000517/b8318f12-3d9c-4da5-9125-2e690de3e3de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d09e24f_a8b1_49c4_aee0_65e645fe2081
PROP-693311-2016 | PR-434158-2016 | 10/28/2016 1:23:00 PM | ASSESS: PR OP: Annual | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Loose belt and misalignment of supports. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Jack_stands.png | file://x:/photopub/docs/0000000508/0e986ba8-b451-438e-8a3b-302334c85e3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__983a1f41_d6be_4faf_a13b_80c5d4e888e1
PROP-693311-2016 | PR-434158-2016 | 10/28/2016 1:23:00 PM | ASSESS: PR OP: Annual | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Loose belt and misalignment of supports. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Loose_carpeting.png | file://x:/photopub/docs/0000000508/f03e97ca-652d-49ab-afa2-d05279a7be0a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__983a1f41_d6be_4faf_a13b_80c5d4e888e1
PROP-693311-2016 | PR-434158-2016 | 10/28/2016 1:23:00 PM | ASSESS: PR OP: Annual | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Loose belt and misalignment of supports. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Skirting_off.png | file://x:/photopub/docs/0000000508/094d4ebb-c2e5-4229-a392-63de8cbf3199.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__983a1f41_d6be_4faf_a13b_80c5d4e888e1
PROP-693305-2016 | PR-434160-2016 | 10/28/2016 2:54:59 PM | ASSESS: PR OP: Annual | png | #asFound | PR009 | Misalignments that are: Reasonably detectable by maintenance program Likely to propagate slowly toward a deropement condition. | 2 | 2 | Sheave assembly mis-alignment. | 2 | Misalignments that are: Reasonably detectable by maintenance program Likely to propagate slowly toward a deropement condition. | Load_test.png | file://x:/photopub/docs/0000000508/46227425-c34e-49e8-b341-6f83555c55d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c103e12a_0872_4e42_bc90_469128e2e3b7
PROP-693305-2016 | PR-434160-2016 | 10/28/2016 2:54:59 PM | ASSESS: PR OP: Annual | png | #asFound | PR009 | Misalignments that are: Reasonably detectable by maintenance program Likely to propagate slowly toward a deropement condition. | 2 | 2 | Sheave assembly mis-alignment. | 2 | Misalignments that are: Reasonably detectable by maintenance program Likely to propagate slowly toward a deropement condition. | Rollback_brake.png | file://x:/photopub/docs/0000000508/b33125b5-5b38-4e75-accf-6f445ada6899.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c103e12a_0872_4e42_bc90_469128e2e3b7
PROP-693305-2016 | PR-434160-2016 | 10/28/2016 2:54:59 PM | ASSESS: PR OP: Annual | png | #asFound | PR009 | Misalignments that are: Reasonably detectable by maintenance program Likely to propagate slowly toward a deropement condition. | 2 | 2 | Sheave assembly mis-alignment. | 2 | Misalignments that are: Reasonably detectable by maintenance program Likely to propagate slowly toward a deropement condition. | No_stop_sign.png | file://x:/photopub/docs/0000000508/54bf01d1-973f-43c9-ad5e-01421bc833c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c103e12a_0872_4e42_bc90_469128e2e3b7
PROP-693305-2016 | PR-434160-2016 | 10/28/2016 2:54:59 PM | ASSESS: PR OP: Annual | png | #asFound | PR009 | Misalignments that are: Reasonably detectable by maintenance program Likely to propagate slowly toward a deropement condition. | 2 | 2 | Sheave assembly mis-alignment. | 2 | Misalignments that are: Reasonably detectable by maintenance program Likely to propagate slowly toward a deropement condition. | Misalignment.png | file://x:/photopub/docs/0000000508/7883369c-3086-4df6-9583-1f9837574822.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c103e12a_0872_4e42_bc90_469128e2e3b7
ELIN-679216-2016 | EL-448466-2016 | 10/6/2016 5:39:33 AM | ASSESS: EL: Final | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Cab tire and other conductors which are not approved for use and damaged are exposed, if left in current state there will be a shock hazard, and thermal hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Damaged_cords.png | file://x:/photopub/docs/0000000497/adc244b5-5f39-4bae-b656-f7a6ba0806dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0751c8a7_d2fb_46b7_9acc_ed627c5ac50d
ELIN-679216-2016 | EL-448466-2016 | 10/6/2016 5:39:33 AM | ASSESS: EL: Final | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Cab tire and other conductors which are not approved for use and damaged are exposed, if left in current state there will be a shock hazard, and thermal hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Unapproved_receptacles_.png | file://x:/photopub/docs/0000000497/8c8a11dd-3087-4d60-abca-cc37d907463b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0751c8a7_d2fb_46b7_9acc_ed627c5ac50d
ELIN-679216-2016 | EL-448466-2016 | 10/6/2016 5:39:33 AM | ASSESS: EL: Final | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Cab tire and other conductors which are not approved for use and damaged are exposed, if left in current state there will be a shock hazard, and thermal hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Damaged_wire.png | file://x:/photopub/docs/0000000497/79030ca8-dde7-45f4-8ff5-cb2d2ebc5009.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0751c8a7_d2fb_46b7_9acc_ed627c5ac50d
GAHE-704373-2016 | HE-468021-2016 | 11/15/2016 1:58:04 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Tank location does not meet code required clearances to combustibles. | 3 | Clearance to combustibles not maintained | 30_935_Old_North_1.png | file://x:/photopub/docs/0000000516/f1e01230-d8ca-455b-b7c3-f8a1948fa4f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68a2b571_09c4_4cec_8cee_0e2f8f0f0add
GAHE-704373-2016 | HE-468021-2016 | 11/15/2016 1:58:04 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Tank location does not meet code required clearances to combustibles. | 3 | Clearance to combustibles not maintained | 30_935_Old_north_2.png | file://x:/photopub/docs/0000000516/057d8aaa-b196-4f0a-b993-1c175df3e8b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68a2b571_09c4_4cec_8cee_0e2f8f0f0add
ELIN-672591-2016 | EL-421137-2016 | 9/30/2016 9:15:56 AM | ASSESS: EL: Service Connection | png | #asFound | EL011 | Conductors are exposed to accidental contact by persons Overhead communication conductors, are not attached or supported adequately. | 2 | 2 | Consumer service attachment point is located at the same elevation as the weatherhead, resulting in the ingress of moisture to the consumer service raceway. This causes corrosion of the consumer service equipment leading to an increased risk of property damage (thermal event). | 2 | Conductors are exposed to accidental contact by persons Overhead communication conductors, are not attached or supported adequately. | View01_point_of_attachment_.png | file://x:/photopub/docs/0000000493/ca4f7271-8c9b-4024-89ef-4ddc02238cf2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__308cfa90_376f_4d29_9a44_25b0666c8dd4
ELIN-673048-2016 | EL-439361-2016 | 9/29/2016 8:54:03 AM | ASSESS: EL: Service Connection | png | #asFound | EL039 | Equipment is not marked / identified Multiple service boxes not marked. | 2 | 2 | Secondary suite distribution supplied from main distribution panel in contravention of requirements of CEC 26-402. | 2 | Equipment is not marked / identified Multiple service boxes not marked. | View01_distribution_.png | file://x:/photopub/docs/0000000493/65e20a0c-87cb-4dc5-82b9-6a23be5e556a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6b31727_135c_40d1_9d6f_76244298d220
GAIN-702127-2016 | GA-466528-2016 | 11/14/2016 1:58:48 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Appliance installed on combustible flooring. Risk of fire or toxic fumes from the synthetic flooring material being exposed to above ambient temperature. | 3 | Clearance to combustible not met | American_range.png | file://x:/photopub/docs/0000000515/ab51c635-ed70-41a7-84e8-c11836c6fcf2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__078dcc68_5bd5_450a_98bf_abf720274759
BPVOP-481531-2015 | 2295927 | 10/22/2016 12:10:27 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 | Not required. | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | scale.png | file://x:/photopub/docs/0000000504/6e8dfb5e-e4e8-42bc-b3a2-3e7dc8217254.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d0c7fa6_6bca_4506_9c2d_5498a686001b
PROP-599973-2016 | 2224097 | 9/28/2016 8:59:00 AM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Good practice to ensure that the main bullwheel bolts are maintaining correct torque value. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Return_Bullwheel.png | file://x:/photopub/docs/0000000494/f70324a4-560b-4c6f-a98e-beba075b96ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30514AFA_78D9_4974_BEA6_9D2E1F971399
PROP-599973-2016 | 2224097 | 9/28/2016 8:59:00 AM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Good practice to ensure that the main bullwheel bolts are maintaining correct torque value. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 100A_breaker_non_GFCI.png | file://x:/photopub/docs/0000000494/f6e2448a-5a4c-4578-97c7-08e78414f7f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30514AFA_78D9_4974_BEA6_9D2E1F971399
PROP-599974-2016 | 2224098 | 10/1/2016 2:40:03 PM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Main axle carrying load of sheave assembly show signs of high wear. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Assembly_axle_wear.png | file://x:/photopub/docs/0000000494/1d6bd1f4-654c-4c9a-bb93-458d6efcf4ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8742777C_4A73_4E62_8160_72B5B626AA22
GAIN-671590-2016 | GA-388241-2016 | 10/6/2016 1:45:14 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | Found pool boiler in operation without combustion air supply to enclosure. This will cause the production of excessive carbon monoxide. It could lead to carbon monoxide poisoning if someone was left inside the unventilated pool boiler enclosure. | 4 | Combustion air supply missing | Wayward_hayward.png | file://x:/photopub/docs/0000000496/9530dfdb-5151-4546-9ab7-fb5abb4f36b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__803a68f5_dc27_4b6c_bf44_80667d8f1185
ELIN-662117-2016 | EL-426264-2016 | 9/28/2016 2:13:51 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | A 15 amp 120 volt gfi receptacle is located close enough to a hot tub for occupants to easily reach while seated in the tub. Receptacles must be installed a minimum of 1.5 meters distant from pools or hot tubs to prevent contact by persons while in pool water. This is added protection above ground fault protection in place to protect persons from potential injury. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_56_cm_from_hot_tub_inner_wall.png | file://x:/photopub/docs/0000000496/9632fcff-4a88-4471-8db2-e1201725817a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b28bd0c3_5514_4bbd_a954_07a1b257dfe0
ELIN-709340-2016 | EL-454102-2016 | 11/23/2016 11:42:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | A new 200A 120/240V Service has been provided to a property that has only a Power Shack in place, no dwelling has yet been built, and multiple dwellings are proposed on site. The 4/0 conductor size used is only allowed for a calculated load on a single family dwelling. The cable is not rated to handle 200 amps or the other loads that could be placed on it, this could result in Equipment damage. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Meterbase.png | file://x:/photopub/docs/0000000520/10ad7129-2081-4ca4-b5ea-c5b321a5a2ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ee52745_3c1f_44ea_b259_3967466ed623
GAHE-706925-2016 | HE-469568-2016 | 11/18/2016 1:17:31 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Propane tank surrounded by trees. The required clearance to readily ignitable materials is 10 feet. | 3 | Clearance to combustibles not maintained | 3836_Zinck_1.png | file://x:/photopub/docs/0000000518/95953521-69d2-4b19-bce3-c69db52dd4bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfa8d631_a934_4a7c_9dee_b5795a0f2df3
GAHE-706925-2016 | HE-469568-2016 | 11/18/2016 1:17:31 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Propane tank surrounded by trees. The required clearance to readily ignitable materials is 10 feet. | 3 | Clearance to combustibles not maintained | 3836_Zinck_2.png | file://x:/photopub/docs/0000000518/1914b457-8986-46da-9055-a0ba121019a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfa8d631_a934_4a7c_9dee_b5795a0f2df3
ELIN-705509-2016 | EL-340049-2016 | 11/22/2016 12:53:27 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed conductors become energized when light switch turned on. No fixture or cover installed. No wire nuts on conductors. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4634_Sheridan_2.png | file://x:/photopub/docs/0000000520/6ac6f339-9a4f-4d85-b21c-86ecef21778d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__465ccfcd_8cc4_4076_8c4e_d4896f23634e
ELIN-705509-2016 | EL-340049-2016 | 11/22/2016 12:53:27 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed conductors become energized when light switch turned on. No fixture or cover installed. No wire nuts on conductors. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4634_Sheridan.png | file://x:/photopub/docs/0000000520/2186ab6b-190c-455a-9fc1-41d799ee57c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__465ccfcd_8cc4_4076_8c4e_d4896f23634e
ELIN-678380-2016 | UW-447772-2016 | 10/4/2016 8:06:08 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Arc-fault protection is required on new branch circuits 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation, a new 15 amp circuit for a dedicated receptacle was installed with out arc-fault protection in a single family dwelling. If a series or parallel arc was to occur in this branch circuit or in an appliance connected to this circuit, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Main_Panel_no_arc_fault_devices.png | file://x:/photopub/docs/0000000496/254ba9bc-e79c-487f-922e-9d6493d52c1e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed95601f_b9c2_4dc6_9cbd_d0a92635619b
ELHE-678506-2016 | HE-447836-2016 | 10/5/2016 10:10:36 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 5 | A water system for a single dwelling is fed by overhead electrical wiring and equipment in a state of disrepair and utilizing the forest to support the cables. These cables can be reached by persons and are accessible to the public and this could lead to injury to persons. The conductors are damaged and supported by trees. This can lead to a forest interface fire and damage surrounding properties. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Old_single_conductor_copper_with_visible_damage_to_weatherproof_coating_hanging_low_and_supported_by_trees_and_vegetation.png | file://x:/photopub/docs/0000000496/f48aaf9d-e7e0-473f-9982-e8af57a199dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__adfcf20b_e858_4a8f_bcfe_0a9cc9f01886
ELIN-709086-2016 | 4239156 | 11/24/2016 9:12:41 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed 32mm from the face of structural members when they pass through them. This is required to prevent damage to the cables from nails and screws both during and after construction. This installation for wiring of a recreation and guest room had NMSC installed less than 32mm from the face of structural members where they pass through them. This was a shock and fire hazard if wiring is damaged by nails, screws, or other fasteners secured to the walls either during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wall_where_wiring_is_not_installed_to_code.png | file://x:/photopub/docs/0000000520/fe998130-131e-4515-ac30-421a4dbc10db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a85408c_4037_4c1c_aa69_c81e429de0b9
ELIN-709086-2016 | 4239156 | 11/24/2016 9:12:41 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed 32mm from the face of structural members when they pass through them. This is required to prevent damage to the cables from nails and screws both during and after construction. This installation for wiring of a recreation and guest room had NMSC installed less than 32mm from the face of structural members where they pass through them. This was a shock and fire hazard if wiring is damaged by nails, screws, or other fasteners secured to the walls either during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_not_installed_32mm_from_face_of_studs.png | file://x:/photopub/docs/0000000520/853d4c40-e8c6-4e71-8367-8980ebea440f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a85408c_4037_4c1c_aa69_c81e429de0b9
ELIN-709086-2016 | 4239156 | 11/24/2016 9:12:41 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed 32mm from the face of structural members when they pass through them. This is required to prevent damage to the cables from nails and screws both during and after construction. This installation for wiring of a recreation and guest room had NMSC installed less than 32mm from the face of structural members where they pass through them. This was a shock and fire hazard if wiring is damaged by nails, screws, or other fasteners secured to the walls either during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Rec_guest_room.png | file://x:/photopub/docs/0000000520/7927a914-28ee-49c0-8f0b-4d85355e7159.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a85408c_4037_4c1c_aa69_c81e429de0b9
ELIN-709086-2016 | 4239156 | 11/24/2016 9:12:41 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed 32mm from the face of structural members when they pass through them. This is required to prevent damage to the cables from nails and screws both during and after construction. This installation for wiring of a recreation and guest room had NMSC installed less than 32mm from the face of structural members where they pass through them. This was a shock and fire hazard if wiring is damaged by nails, screws, or other fasteners secured to the walls either during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wall_where_wiring_is_not_installed_32mm_from_face_of_structural_members.png | file://x:/photopub/docs/0000000520/37390c5a-4226-4256-aa11-3e7a4683592a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a85408c_4037_4c1c_aa69_c81e429de0b9
PRIN-599864-2016 | PR-375097-2016 | 11/3/2016 7:47:00 AM | ASSESS: PR IN: Acceptance | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | Wind monitoring not functioning on drive terminal. High winds may not stop or slow Gondola. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | plc_wind_meter.png | file://x:/photopub/docs/0000000510/967ffff4-c050-4907-8332-3ebf94438022.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d954a61_97a9_4475_bec9_70bd86f1cdf2
ELIN-677239-2016 | EL-443773-2016 | 10/6/2016 2:45:29 PM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | A 60 amp 240 volt recreational vehicle service has been provided on a consumer pole. The Cutler Hammer panelboard provided has been fitted with Seimens circuit breakers for both the man service disconnect and some branch circuit positions. Seimens breakers have not been designed or tested in Cutler Hammer panelboards. Unforeseen failures can occur in these breakers or their locations in the panel, leading to a potential for property damage or injury to persons | 3 | General Equipment is not approved for the specific use | Seimens_breakers_in_Cutler_Hammer_panelboard.png | file://x:/photopub/docs/0000000498/b5baddce-ed9c-4051-b6c3-a20290a674cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d25a86cb_dc08_4250_8f7e_b26975f9c029
ELIN-678380-2016 | UW-447772-2016 | 10/4/2016 8:06:08 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Arc-fault protection is required on new branch circuits 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation, a new 15 amp circuit for a dedicated receptacle was installed with out arc-fault protection in a single family dwelling. If a series or parallel arc was to occur in this branch circuit or in an appliance connected to this circuit, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | New_branch_circuit.png | file://x:/photopub/docs/0000000496/fd1edb3f-2671-4181-9ead-13d23691aaaa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed95601f_b9c2_4dc6_9cbd_d0a92635619b
ELIN-678380-2016 | UW-447772-2016 | 10/4/2016 8:06:08 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Arc-fault protection is required on new branch circuits 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation, a new 15 amp circuit for a dedicated receptacle was installed with out arc-fault protection in a single family dwelling. If a series or parallel arc was to occur in this branch circuit or in an appliance connected to this circuit, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | New_receptacle_installed.png | file://x:/photopub/docs/0000000496/f02ee78f-0d03-4775-88d5-e03ddd81d5eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed95601f_b9c2_4dc6_9cbd_d0a92635619b
ELIN-680849-2016 | EL-445402-2016 | 10/13/2016 11:24:22 AM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Temporary service not weatherproof presents shock hazard to workers | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Tcs_burdick.png | file://x:/photopub/docs/0000000499/333e2c70-7432-419e-a0a4-5b9abb41a450.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df9280d0_dbed_49ec_b963_143e1e39cb0b
PROP-681254-2016 | PR-433592-2016 | 10/12/2016 5:11:22 PM | ASSESS: PR OP: Annual | png | #asFound | PR000 | No Created Hazard Identified | 0 | 0 | Small landing at unload will stop lift to unload chair. Expired fire extinguisher. | 0 | No Created Hazard Identified | Unload_footpassengers.png | file://x:/photopub/docs/0000000499/7ad841b7-ab23-4f38-b0bf-54d40a5a9cdb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d106909c_f3cf_4119_8e06_4bb1c64196fb
ELIN-678118-2016 | EL-447617-2016 | 10/5/2016 3:37:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Length of unprotected service cable in wall is greater than allowed by directive, increasing the possibility of the risk of fire | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_cable_in_wall_2.png | file://x:/photopub/docs/0000000496/a40ee90f-11ef-4107-8e42-482a332e4ae9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71db491d_81d2_4574_836c_9973bc921a17
BPVOP-704931-2016 | 2280936 | 11/17/2016 2:44:04 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP163 | 5.0.1 Operator non-compliance - Safety orders not followed or adhered to | 3 | 3 | Due to the nature of construction and operation of machine mounted air receivers, they require complete non destructive examination for units over the age of 20 years old to identify any defects in the pressure vessel. This could not be demonstrated for this equipment. | 3 | 5.0.1 Operator non-compliance - Safety orders not followed or adhered to | Nameplate.png | file://x:/photopub/docs/0000000517/aa408824-b722-4dfd-b3ed-d846f97eb462.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be2c0e9c_205f_4850_8a5a_34d3a4c84c8d
BPVIN-705052-2016 | BPV-448149-2016 | 11/16/2016 10:06:49 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Safetydischarge.png | file://x:/photopub/docs/0000000517/dd0513bb-2523-40c2-b640-7fa59825da32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__86f4b05a_2237_424d_901d_242be8de17c9
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 124.png | file://x:/photopub/docs/0000000490/c58f13fa-d7a8-446a-b921-11d27fa510d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 101.png | file://x:/photopub/docs/0000000490/e3aeff7a-001c-4286-996b-e3c7d8908c96.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 114.png | file://x:/photopub/docs/0000000490/b66378aa-5457-4fcc-bd89-cee29d618f7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 112.png | file://x:/photopub/docs/0000000490/60bf8059-edf5-4957-a287-685dffa24043.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 104.png | file://x:/photopub/docs/0000000490/d00d4616-1f77-489e-817d-a9693e980e04.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 119.png | file://x:/photopub/docs/0000000490/f057d2a8-00db-4ad2-a8f9-9bf83cc0892d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 120.png | file://x:/photopub/docs/0000000490/0f200872-e117-434e-9a33-34698c30020b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 126.png | file://x:/photopub/docs/0000000490/0d94d9be-b46b-48bf-83c2-dd004592f268.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 107.png | file://x:/photopub/docs/0000000490/29457570-65a1-4093-96db-aed97e049215.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 129.png | file://x:/photopub/docs/0000000490/35175815-499c-4cfb-b518-a394163dc2af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 109.png | file://x:/photopub/docs/0000000490/92a7241a-557f-4660-a977-f9436280acc7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 116.png | file://x:/photopub/docs/0000000490/4e745169-7fe6-4fd2-bd3b-ce467bee7f40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 110.png | file://x:/photopub/docs/0000000490/568cee16-d48c-4e15-96af-50768a6db9e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 127.png | file://x:/photopub/docs/0000000490/5c5a9e9e-7599-4290-8cc9-da91a6939119.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 118.png | file://x:/photopub/docs/0000000490/2f5750fc-bc2d-476a-abab-986679b84e1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 122.png | file://x:/photopub/docs/0000000490/8ce18a9e-d8b7-4b7c-9d33-0820834a5724.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 105.png | file://x:/photopub/docs/0000000490/32d8ca20-a4f6-4c87-81fd-59d46a6569d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 113.png | file://x:/photopub/docs/0000000490/c009b4ea-a01b-4184-934a-ea53a89da62d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 123.png | file://x:/photopub/docs/0000000490/8151c833-7de9-4969-a900-b70e5f196554.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 102.png | file://x:/photopub/docs/0000000490/cfdfc56a-9923-4f04-bd45-b71e3aa0032d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 128.png | file://x:/photopub/docs/0000000490/0cb47e2c-4396-419a-a1f2-b1a1ced588cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 117.png | file://x:/photopub/docs/0000000490/9c3a46eb-7038-49b4-8818-1c7078084d21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
GAIN-706960-2016 | GA-469599-2016 | 11/21/2016 11:57:09 AM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | Certified connector not approved for application. Connector can be damaged due to vibration exposure when installed in application it is not certified for. | 2 | Certified appliance connector installed but not approved for application | Connector_not_approved_for_application.png | file://x:/photopub/docs/0000000519/2ef9aa34-b680-4516-8519-4191c49727db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2362f1c7_acb3_4095_becc_d5d4e929360f
GAIN-703252-2016 | GA-368459-2016 | 11/21/2016 4:04:01 PM | ASSESS: GA: Final | png | #asFound | GA047 | Damage to natural gas or propane distribution systems due to unsafe work practices no release of gas | 2 | 2 | Damaged to gas distribution system, no escape of gas. Damaged copper tubing could be further damaged causing a release of gas and potential for fire. | 2 | Damage to natural gas or propane distribution systems due to unsafe work practices no release of gas | Damaged_copper_tubing.png | file://x:/photopub/docs/0000000519/2d8b2561-750b-488d-8c74-cd3bcdd6840d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__80c9c2cb_1276_43a4_b8c7_318d3c9393b3
ELIN-678118-2016 | EL-447617-2016 | 10/5/2016 3:37:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Length of unprotected service cable in wall is greater than allowed by directive, increasing the possibility of the risk of fire | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_cable_in_wall.png | file://x:/photopub/docs/0000000496/e6f171bc-aaaf-4c11-a252-3fa6a08b4912.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71db491d_81d2_4574_836c_9973bc921a17
GAUP-678965-2016 | UW-448294-2016 | 10/5/2016 3:01:22 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Gas line installed behind kitchen equipment with a valve in off position, piping not capped. Valve could get knocked and gas could escape from piping causing a fire or an explosion | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Open_gas_line_with_valve.png | file://x:/photopub/docs/0000000496/48fe5998-9ac3-4044-b0be-f2419a9c4f1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d150732_388f_481e_8f47_56116975a0d5
EDIN-673168-2016 | ED-425739-2016 | 9/28/2016 2:14:04 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | The second stage of one side of the out of ground piston is scraping the hoistway wall for approximately 15-20 feet when it is extended. During an acceptance inspection it was found that there was not enough clearance between the piston and the hoistway wall. With continued use there may be substantial damage to the piston causing the possibility of a major failure to the supporting means of the elevator. This will in turn cause an incident that may include injury to the occupants of the elevator. It was found the General Contractor failed to construct the hoistway to give enough clearance to the elevator moving components. This 2 stop 5000lbs hydraulic elevator is located in a newly constructed supermarket. | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Piston_scraping_hoistway_Sept_29_2016.png | file://x:/photopub/docs/0000000492/c7c22023-a178-42de-8223-21e267575c17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30615239_db44_4152_a2a4_db712d893b61
ELIN-672634-2016 | EL-407922-2016 | 10/3/2016 1:16:06 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | The 15 amp 120 volt receptacle and switch do not protect the live terminals from accidental contact, this is a shock hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_receptacle_and_switch.png | file://x:/photopub/docs/0000000494/a8f95313-3c68-4b45-9d0d-598178a7407e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0ea5cae_038d_4042_a7f9_91cf2f6f442f
ELIN-639754-2016 | EL-425699-2016 | 10/3/2016 3:04:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | The 100 amp 120/240 volt service has the grounding conductor terminated to the panel enclosure and not to the identified, this can lead to an equipment damage issue | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Ground_conductor_to_can.png | file://x:/photopub/docs/0000000494/97c0e44b-3d8d-471c-9477-6972535e0e7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0667bbad_71c0_4f46_8474_d0ea787a433d
ELIN-675911-2016 | EL-437983-2016 | 10/3/2016 11:10:50 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 200 amp 120/240 volt RPVC conduit entrance into the meterbase uses a Male TA fitting into a female threaded hub, this can lead to an equipment damage issue | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | RPVC_TA_fitting.png | file://x:/photopub/docs/0000000494/7bbe8097-742f-454e-a6d6-6409477074de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7397cf0_cab6_429e_a650_0fa609b142ba
BPOP-670519-2016 | BPV-405769-2015 | 9/27/2016 6:21:16 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Vapour valve on service valve was not plugged off. Valve was closed but left unplugged. If tampered with could cause high pressure gas leak,and potential for fire ,property damage ,or loss of life. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 801_Sibco.png | file://x:/photopub/docs/0000000504/68f1ed00-078e-406e-b42e-9e087d277225.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29eada52_7c47_4c98_be97_64f5a02da2f8
BPOP-670674-2016 | BPV-405894-2015 | 10/17/2016 8:41:47 AM | ASSESS: Propane PV: Periodic | png | #asFound | BP107 | 3.0.1 Safeties will not function - Pressure Relief Device No drain hole provided in the device body or discharge piping to allow drainage of liquids | 2 | 2 | PRV rain cap off and weep hole plugged. Relief valve full of water. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device No drain hole provided in the device body or discharge piping to allow drainage of liquids | PRV_1.png | file://x:/photopub/docs/0000000501/f5df30d3-7ee8-46d4-ac71-3dff5af6c812.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49077565_708c_405a_9d56_bc4b35e52d9e
ELIN-665316-2016 | UW-438800-2016 | 9/16/2016 5:18:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized wiring in boxes with switches, receptacles, light fixtures and junction boxes are required to have cover plates installed on them. This is required to prevent accidental contact with energized terminals on switches and receptacles and energized conductors at fixtures and junction boxes. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation has energized terminals exposed to contact at switches, receptacles, and wiring/connections exposed to contact, and damage, because required cover plates are not installed. This is a potential shock and fire hazard if persons or objects contact energized terminals/wiring or if wiring or equipment fails and boxes do not contain thermal energy as intended. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_switch_in_mercantile_building_without_a_cover_plate_in_place.png | file://x:/photopub/docs/0000000488/c18da8b6-5780-4918-8233-6b32f9dcc01c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c8e24ff_fdb0_4ac2_99ea_c1914981aaae
ELIN-665316-2016 | UW-438800-2016 | 9/16/2016 5:18:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized wiring in boxes with switches, receptacles, light fixtures and junction boxes are required to have cover plates installed on them. This is required to prevent accidental contact with energized terminals on switches and receptacles and energized conductors at fixtures and junction boxes. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation has energized terminals exposed to contact at switches, receptacles, and wiring/connections exposed to contact, and damage, because required cover plates are not installed. This is a potential shock and fire hazard if persons or objects contact energized terminals/wiring or if wiring or equipment fails and boxes do not contain thermal energy as intended. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Addition_to_house.png | file://x:/photopub/docs/0000000488/2dc3d988-83a8-431f-a935-6a16599cf91e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c8e24ff_fdb0_4ac2_99ea_c1914981aaae
ELIN-665316-2016 | UW-438800-2016 | 9/16/2016 5:18:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized wiring in boxes with switches, receptacles, light fixtures and junction boxes are required to have cover plates installed on them. This is required to prevent accidental contact with energized terminals on switches and receptacles and energized conductors at fixtures and junction boxes. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation has energized terminals exposed to contact at switches, receptacles, and wiring/connections exposed to contact, and damage, because required cover plates are not installed. This is a potential shock and fire hazard if persons or objects contact energized terminals/wiring or if wiring or equipment fails and boxes do not contain thermal energy as intended. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Cabin_building.png | file://x:/photopub/docs/0000000488/78e59f58-b242-4ed9-ae78-bc2be9251daa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c8e24ff_fdb0_4ac2_99ea_c1914981aaae
ELIN-665316-2016 | UW-438800-2016 | 9/16/2016 5:18:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized wiring in boxes with switches, receptacles, light fixtures and junction boxes are required to have cover plates installed on them. This is required to prevent accidental contact with energized terminals on switches and receptacles and energized conductors at fixtures and junction boxes. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation has energized terminals exposed to contact at switches, receptacles, and wiring/connections exposed to contact, and damage, because required cover plates are not installed. This is a potential shock and fire hazard if persons or objects contact energized terminals/wiring or if wiring or equipment fails and boxes do not contain thermal energy as intended. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_junction_boxes_in_crawl_space_without_covers_.png | file://x:/photopub/docs/0000000488/aca061e6-f8e7-469e-95bf-1c3ed699c01d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c8e24ff_fdb0_4ac2_99ea_c1914981aaae
ELIN-665316-2016 | UW-438800-2016 | 9/16/2016 5:18:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized wiring in boxes with switches, receptacles, light fixtures and junction boxes are required to have cover plates installed on them. This is required to prevent accidental contact with energized terminals on switches and receptacles and energized conductors at fixtures and junction boxes. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation has energized terminals exposed to contact at switches, receptacles, and wiring/connections exposed to contact, and damage, because required cover plates are not installed. This is a potential shock and fire hazard if persons or objects contact energized terminals/wiring or if wiring or equipment fails and boxes do not contain thermal energy as intended. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Mercantile_building.png | file://x:/photopub/docs/0000000488/c1055171-afbc-465a-81c0-d546f98f8664.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c8e24ff_fdb0_4ac2_99ea_c1914981aaae
ELIN-665316-2016 | UW-438800-2016 | 9/16/2016 5:18:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized wiring in boxes with switches, receptacles, light fixtures and junction boxes are required to have cover plates installed on them. This is required to prevent accidental contact with energized terminals on switches and receptacles and energized conductors at fixtures and junction boxes. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation has energized terminals exposed to contact at switches, receptacles, and wiring/connections exposed to contact, and damage, because required cover plates are not installed. This is a potential shock and fire hazard if persons or objects contact energized terminals/wiring or if wiring or equipment fails and boxes do not contain thermal energy as intended. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_switch_in_laundry_room_without_a_cover_plate.png | file://x:/photopub/docs/0000000488/886c93b1-95b1-4d05-88bd-07019a64e900.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c8e24ff_fdb0_4ac2_99ea_c1914981aaae
ELIN-665316-2016 | UW-438800-2016 | 9/16/2016 5:18:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized wiring in boxes with switches, receptacles, light fixtures and junction boxes are required to have cover plates installed on them. This is required to prevent accidental contact with energized terminals on switches and receptacles and energized conductors at fixtures and junction boxes. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation has energized terminals exposed to contact at switches, receptacles, and wiring/connections exposed to contact, and damage, because required cover plates are not installed. This is a potential shock and fire hazard if persons or objects contact energized terminals/wiring or if wiring or equipment fails and boxes do not contain thermal energy as intended. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_fixture_in_cabin_without_canopy_in_place.png | file://x:/photopub/docs/0000000488/429490a8-cf23-4029-a8f3-9cc22e3a840a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c8e24ff_fdb0_4ac2_99ea_c1914981aaae
ELIN-665316-2016 | UW-438800-2016 | 9/16/2016 5:18:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized wiring in boxes with switches, receptacles, light fixtures and junction boxes are required to have cover plates installed on them. This is required to prevent accidental contact with energized terminals on switches and receptacles and energized conductors at fixtures and junction boxes. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation has energized terminals exposed to contact at switches, receptacles, and wiring/connections exposed to contact, and damage, because required cover plates are not installed. This is a potential shock and fire hazard if persons or objects contact energized terminals/wiring or if wiring or equipment fails and boxes do not contain thermal energy as intended. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_receptacles_in_mercantile_without_cover_plates_in_place.png | file://x:/photopub/docs/0000000488/98d0aa07-6005-411e-a52d-481d5a5ad8bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c8e24ff_fdb0_4ac2_99ea_c1914981aaae
ELIN-669203-2016 | EL-437471-2016 | 9/23/2016 1:54:56 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | The 200 amp 120/240 volt consumer service cable is installed within insulated walls greater than 1.5 meters, this is both an Equipment damage and thermal hazard | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Consumer_service_cable.png | file://x:/photopub/docs/0000000490/6935c976-5e72-4ef8-baa7-4d1a2fc4a259.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a093bc48_3d33_460f_83ca_0bca0e7e46cc
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 106.png | file://x:/photopub/docs/0000000490/5941ef74-0270-492e-86d0-48988d4222cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 121.png | file://x:/photopub/docs/0000000490/7b4c736e-4031-454c-ab7c-5b514c0fe70b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 125.png | file://x:/photopub/docs/0000000490/72381575-a398-4bc9-b4ca-eec608e87a59.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 111.png | file://x:/photopub/docs/0000000490/a7be9651-bd9f-40fb-8ebe-31dec4d98267.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 108.png | file://x:/photopub/docs/0000000490/43eae405-cb15-40b9-8dc0-bc2814489601.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 103.png | file://x:/photopub/docs/0000000490/b8b823fe-551f-405d-90b2-4e97ea9354a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 115.png | file://x:/photopub/docs/0000000490/fa45cfc4-760d-4f83-b07c-8ac2e7201767.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
ELHE-663689-2016 | HE-437797-2016 | 9/23/2016 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 100.png | file://x:/photopub/docs/0000000490/8b13c3e9-0958-40c7-b667-d543cdb7bd0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f887eed6_aef0_4226_883a_8f75d7c14710
GAHE-664434-2016 | HE-438185-2016 | 9/15/2016 10:21:56 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | Eight propane tanks installed at multiple buildings, installed against building and building openings. | 2 | Installation clearances or set backs to propane containers not met | Multiple_tanks_to_close_to_buildings.png | file://x:/photopub/docs/0000000487/d6ce7998-f3ee-4d51-bc29-0333080fe4f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43e6f295_5f7a_4af7_9b1e_6d8f4da8e442
GAHE-664425-2016 | HE-438168-2016 | 9/15/2016 10:49:08 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA006 | Container not set upon compliant base | 2 | 2 | Tank legs not on cement pads, tank could tip over | 2 | Container not set upon compliant base | Rubber_hose_used_to_connect_regulator_.png | file://x:/photopub/docs/0000000487/2c10ccd2-83c0-4578-851e-54a913798360.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef8cc35e_dbe4_41b9_b37d_a3cd0dd2247f
GAHE-664465-2016 | HE-438205-2016 | 9/15/2016 10:06:33 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA006 | Container not set upon compliant base | 2 | 2 | Tank installed on wood blocks, and sunk in mud, bottom of tank in mud | 2 | Container not set upon compliant base | Tank_on_wooden_blocks.png | file://x:/photopub/docs/0000000487/6d20be58-0563-43ab-a651-f433ecbcfb55.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf632cc8_10c0_4945_82bb_00654643c7dc
GAHE-664425-2016 | HE-438168-2016 | 9/15/2016 10:49:08 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA006 | Container not set upon compliant base | 2 | 2 | Tank legs not on cement pads, tank could tip over | 2 | Container not set upon compliant base | Tank_to_close_to_building_.png | file://x:/photopub/docs/0000000487/27e40860-9005-4704-8a41-768b088294ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef8cc35e_dbe4_41b9_b37d_a3cd0dd2247f
GAHE-664434-2016 | HE-438185-2016 | 9/15/2016 10:21:56 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | Eight propane tanks installed at multiple buildings, installed against building and building openings. | 2 | Installation clearances or set backs to propane containers not met | Tank_installed_between_buildings.png | file://x:/photopub/docs/0000000487/64a6506e-8d1a-471c-ac9a-464ee7d93f5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43e6f295_5f7a_4af7_9b1e_6d8f4da8e442
GAHE-664425-2016 | HE-438168-2016 | 9/15/2016 10:49:08 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA006 | Container not set upon compliant base | 2 | 2 | Tank legs not on cement pads, tank could tip over | 2 | Container not set upon compliant base | Tank_not_on_proper_blocks.png | file://x:/photopub/docs/0000000487/a1bd2fbb-b38e-4847-bf9a-ffcda1ff6caf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef8cc35e_dbe4_41b9_b37d_a3cd0dd2247f
ELIN-676690-2016 | EL-445969-2016 | 10/4/2016 10:14:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | The 100 amp 120/240 volt panel feeder cable has the bond conductor connected to the identified neutral conductor buss. This can lead to a shock hazard | 3 | Continuity Bonding; method for equipment is not adequate. | Wrong_bond_connection.png | file://x:/photopub/docs/0000000495/71582182-0ff4-4dd6-a6b5-64d06459d35c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4c6b5cd_95e6_46d9_8b58_f5607653e0ff
GAHE-702099-2016 | HE-466508-2016 | 11/10/2016 3:28:23 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Propane tank is too close to house. | 3 | Clearance to combustibles not maintained | 10065_Findlay.png | file://x:/photopub/docs/0000000514/783ec052-f550-4578-ab68-ae40b3759826.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbe5880d_5c02_46fa_b316_a458543fd1d0
ELHE-682683-2016 | HE-450875-2016 | 10/12/2016 2:56:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | There are numerous 120 volt open splices in the store within reach of the customers. There is also unapproved electrical equipment being offered for sale. These are potential shock and equipment failure hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 120_volt_energized_lvt.png | file://x:/photopub/docs/0000000499/acefe461-e6c4-455e-9380-c56d17f55b1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bf142ca_1ffa_4e95_a63e_f652fd83e7a8
ELHE-682683-2016 | HE-450875-2016 | 10/12/2016 2:56:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | There are numerous 120 volt open splices in the store within reach of the customers. There is also unapproved electrical equipment being offered for sale. These are potential shock and equipment failure hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Store_front.png | file://x:/photopub/docs/0000000499/d1e8faf8-c88f-4a14-9d2f-0e60353abb80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bf142ca_1ffa_4e95_a63e_f652fd83e7a8
ELHE-682683-2016 | HE-450875-2016 | 10/12/2016 2:56:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | There are numerous 120 volt open splices in the store within reach of the customers. There is also unapproved electrical equipment being offered for sale. These are potential shock and equipment failure hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Unapproved_light__.png | file://x:/photopub/docs/0000000499/84f4c5ce-7911-42d3-a6c1-35fc5c906e88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bf142ca_1ffa_4e95_a63e_f652fd83e7a8
ELHE-682683-2016 | HE-450875-2016 | 10/12/2016 2:56:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | There are numerous 120 volt open splices in the store within reach of the customers. There is also unapproved electrical equipment being offered for sale. These are potential shock and equipment failure hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Unapproved_lighting_fixture.png | file://x:/photopub/docs/0000000499/7f0538f4-3e4a-4e3a-9386-afde146111b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bf142ca_1ffa_4e95_a63e_f652fd83e7a8
ELHE-682683-2016 | HE-450875-2016 | 10/12/2016 2:56:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | There are numerous 120 volt open splices in the store within reach of the customers. There is also unapproved electrical equipment being offered for sale. These are potential shock and equipment failure hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_splices.png | file://x:/photopub/docs/0000000499/91f0e775-9259-446d-b580-0ef2c54d5466.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bf142ca_1ffa_4e95_a63e_f652fd83e7a8
ELHE-682683-2016 | HE-450875-2016 | 10/12/2016 2:56:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | There are numerous 120 volt open splices in the store within reach of the customers. There is also unapproved electrical equipment being offered for sale. These are potential shock and equipment failure hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_splice.png | file://x:/photopub/docs/0000000499/01db2569-0270-4702-8270-cdf31fd9e521.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bf142ca_1ffa_4e95_a63e_f652fd83e7a8
ELHE-682683-2016 | HE-450875-2016 | 10/12/2016 2:56:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | There are numerous 120 volt open splices in the store within reach of the customers. There is also unapproved electrical equipment being offered for sale. These are potential shock and equipment failure hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_splice_.png | file://x:/photopub/docs/0000000499/e61f3699-92ab-46cd-b246-5d46f1d285b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bf142ca_1ffa_4e95_a63e_f652fd83e7a8
ELHE-682683-2016 | HE-450875-2016 | 10/12/2016 2:56:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | There are numerous 120 volt open splices in the store within reach of the customers. There is also unapproved electrical equipment being offered for sale. These are potential shock and equipment failure hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_splices_.png | file://x:/photopub/docs/0000000499/d06422a8-a503-4e2a-ae74-c4eba5fe56cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bf142ca_1ffa_4e95_a63e_f652fd83e7a8
ELHE-682683-2016 | HE-450875-2016 | 10/12/2016 2:56:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | There are numerous 120 volt open splices in the store within reach of the customers. There is also unapproved electrical equipment being offered for sale. These are potential shock and equipment failure hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Ccts_red_tagged_1.png | file://x:/photopub/docs/0000000499/f099180a-3a73-43b0-b773-c75bfd80dfe0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bf142ca_1ffa_4e95_a63e_f652fd83e7a8
ELHE-682683-2016 | HE-450875-2016 | 10/12/2016 2:56:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | There are numerous 120 volt open splices in the store within reach of the customers. There is also unapproved electrical equipment being offered for sale. These are potential shock and equipment failure hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Ccts_red_tagged_2.png | file://x:/photopub/docs/0000000499/7bed20ba-3bbf-477b-a827-b1a3e61c76ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bf142ca_1ffa_4e95_a63e_f652fd83e7a8
ELHE-682683-2016 | HE-450875-2016 | 10/12/2016 2:56:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | There are numerous 120 volt open splices in the store within reach of the customers. There is also unapproved electrical equipment being offered for sale. These are potential shock and equipment failure hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | unapproved_lighting_fixture.png | file://x:/photopub/docs/0000000499/b28e83ea-f0f0-4b7a-b048-601f7d524749.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bf142ca_1ffa_4e95_a63e_f652fd83e7a8
ELHE-682683-2016 | HE-450875-2016 | 10/12/2016 2:56:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | There are numerous 120 volt open splices in the store within reach of the customers. There is also unapproved electrical equipment being offered for sale. These are potential shock and equipment failure hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_splices__.png | file://x:/photopub/docs/0000000499/216503bc-f974-4f41-bb85-184e7d5a235d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bf142ca_1ffa_4e95_a63e_f652fd83e7a8
ELIN-692591-2016 | EL-458483-2016 | 10/28/2016 8:39:35 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 |  | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Ditch.png | file://x:/photopub/docs/0000000507/b2b5dce7-3dec-4082-a0cd-c889dfcbf392.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9bbd3a9_ec2d_419c_a336_9971bfc57b2c
GAIN-686920-2016 | GA-453589-2016 | 10/24/2016 11:39:27 AM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 |  | 2 | Certified appliance connector installed but not approved for application | 930_trunk.png | file://x:/photopub/docs/0000000505/16b36202-ce6c-4460-8391-66bd1e21b587.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a5de7b0_6940_476f_b2c2_27432a8bfbc9
GAIN-663727-2016 | GA-436849-2016 | 10/24/2016 1:22:29 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | Valleyview_2.png | file://x:/photopub/docs/0000000505/6b997011-cd64-49d4-9a1f-57f472aff384.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e74b3d17_25c6_4177_96a7_88b42f3ec013
EDOP-688797-2016 | 3830737 | 10/24/2016 4:06:46 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | Deck Barricades prevent access to area beside moving walks that is not safe for public. A deck barricade was removed from the bottom landing beside the moving walk giving access to an unsafe area. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Deck_Barricade_1.png | file://x:/photopub/docs/0000000503/08309eee-5240-4d3d-a39d-b0c60816cb27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3a3d998_1be9_4e09_b08b_cf8d716db454
EDOP-688797-2016 | 3830737 | 10/24/2016 4:06:46 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | Deck Barricades prevent access to area beside moving walks that is not safe for public. A deck barricade was removed from the bottom landing beside the moving walk giving access to an unsafe area. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Deck_Barricade_2.png | file://x:/photopub/docs/0000000503/f9e4ff8b-68be-482a-bb04-7bbd1be69c4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3a3d998_1be9_4e09_b08b_cf8d716db454
ELIN-676447-2016 | EL-440661-2016 | 10/3/2016 3:02:49 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | This assessment found that the gas pipe was not bonded. There is a shock and fire hazard if the pipe becomes energized either through the buildings voltage or a lightning strike. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Saber.png | file://x:/photopub/docs/0000000494/4725ad71-dc57-411a-839a-f53707682dd1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af63371e_4627_4ec7_9701_c1403a79fea7
ELHE-677145-2016 | HE-446737-2016 | 10/3/2016 4:06:41 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Ungrounded conductors are required to be protected by correctly sized devices (usually fuses or circuit breakers) that de-energize the circuit if an overload or short-circuit occurs. Correctly sized devices prevent the overloading of conductors which can cause overheating and the breakdown of the conductor insulation. During an assessment for an incident notification at a single family dwelling, a #14 copper conductor for a 15A, 120V fridge receptacle was connected to a 30A, single pole breaker in the electrical panel. If other devices are connected to this same same circuit, the 30A breaker would not protect the #14 conductor from becoming overloaded. The overloading of the conductor could break down the insulation which leads to equipment damage. The breakdown of the insulation can also lead to a short circuit on the conductor which could create a shock or fire hazard within the dwelling. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Inside_of_panel.png | file://x:/photopub/docs/0000000495/ec3e352f-f4e0-4bd1-82e4-bbd499cf162a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa42b862_d87d_4c75_8641_a0e0c77ed115
ELHE-677145-2016 | HE-446737-2016 | 10/3/2016 4:06:41 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Ungrounded conductors are required to be protected by correctly sized devices (usually fuses or circuit breakers) that de-energize the circuit if an overload or short-circuit occurs. Correctly sized devices prevent the overloading of conductors which can cause overheating and the breakdown of the conductor insulation. During an assessment for an incident notification at a single family dwelling, a #14 copper conductor for a 15A, 120V fridge receptacle was connected to a 30A, single pole breaker in the electrical panel. If other devices are connected to this same same circuit, the 30A breaker would not protect the #14 conductor from becoming overloaded. The overloading of the conductor could break down the insulation which leads to equipment damage. The breakdown of the insulation can also lead to a short circuit on the conductor which could create a shock or fire hazard within the dwelling. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | CCT8_fridge_on_30A_breaker.png | file://x:/photopub/docs/0000000495/5da27461-cf89-4179-9cfb-bd49029bdd79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa42b862_d87d_4c75_8641_a0e0c77ed115
ELIN-697882-2016 | EL-461389-2016 | 11/9/2016 11:48:28 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 1 | Cables not properly secured are subject to both mechanical and electrical damage. | 0 | No Created Hazard Identified | BX_12-618.png | file://x:/photopub/docs/0000000514/d24a3ad4-239d-47a8-98d0-9b81debb7a7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be75e857_b42d_44aa_aba7_e52e853fe939
ELIN-644035-2016 | EL-356477-2016 | 9/19/2016 12:53:24 PM | ASSESS: EL: Final | png | #asFound | EL171 | Conductor sizing Loads exceed branch circuit conductor ampacity. | 3 | 2 | A built in AC unit operating at 120 volts and 12 amps is connected to a general purpose circuit feeding other receptacles in an office building. AC units of this size use considerable power and if not placed on dedicated circuits can cause circuit overloading. This can cause property or equipment damage. | 3 | Conductor sizing Loads exceed branch circuit conductor ampacity. | AC_into_standard_receptacle_general_purpose_circuit.png | file://x:/photopub/docs/0000000487/251fbd4c-3a7b-48c3-bc62-eb686c9a98b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ccb5ec9e_a8e4_4955_9c52_18d77c107630
ELIN-649690-2016 | EL-123360-2014 | 9/20/2016 6:54:29 AM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | A service cable feeding a new residential dwelling service rated 125 amps and 240 volts has settled during construction pulling the cable down out of the connector leaving the armour of the cable exposed and the armor not connected to the grounding system for the building. Water can enter the cable and the equipment when the cable is not weathertight at the equipment leading to equipment damage or potential injury to persons | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Cable_pulled_from_connector_meter_subject_to_mechanical_damage.png | file://x:/photopub/docs/0000000487/f1d42efd-25e6-4075-8c14-6878c475adb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2497740f_ac6a_4bfa_84ce_a51e1068d1db
ELIN-677043-2016 | EL-051326-2013 | 9/14/2016 2:52:42 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | 120 volt dishwasher circuit and island counter plug shared circuit which may lead to equipment failure. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3.png | file://x:/photopub/docs/0000000495/2d03e9b5-f25e-4d66-8284-9591cf12a331.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__847a40f8_d069_4f75_b758_6cfa098129bc
ELIN-677043-2016 | EL-051326-2013 | 9/14/2016 2:52:42 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | 120 volt dishwasher circuit and island counter plug shared circuit which may lead to equipment failure. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 1.png | file://x:/photopub/docs/0000000495/e0a6d9e7-0b93-4b19-8255-c4799465f7de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__847a40f8_d069_4f75_b758_6cfa098129bc
ELIN-677043-2016 | EL-051326-2013 | 9/14/2016 2:52:42 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | 120 volt dishwasher circuit and island counter plug shared circuit which may lead to equipment failure. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 7.png | file://x:/photopub/docs/0000000495/b44cf2f1-addc-4c98-bfd8-5e8629ab2c4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__847a40f8_d069_4f75_b758_6cfa098129bc
ELIN-677043-2016 | EL-051326-2013 | 9/14/2016 2:52:42 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | 120 volt dishwasher circuit and island counter plug shared circuit which may lead to equipment failure. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 4.png | file://x:/photopub/docs/0000000495/3912cac1-5eef-457c-8c56-187914b3d5fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__847a40f8_d069_4f75_b758_6cfa098129bc
ELIN-677043-2016 | EL-051326-2013 | 9/14/2016 2:52:42 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | 120 volt dishwasher circuit and island counter plug shared circuit which may lead to equipment failure. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 2.png | file://x:/photopub/docs/0000000495/b8bc83a9-4beb-4dbf-96fc-f066b2c15339.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__847a40f8_d069_4f75_b758_6cfa098129bc
ELIN-677043-2016 | EL-051326-2013 | 9/14/2016 2:52:42 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | 120 volt dishwasher circuit and island counter plug shared circuit which may lead to equipment failure. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 6.png | file://x:/photopub/docs/0000000495/59da4073-4376-4c52-96a0-091cc299fe36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__847a40f8_d069_4f75_b758_6cfa098129bc
ELIN-677043-2016 | EL-051326-2013 | 9/14/2016 2:52:42 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | 120 volt dishwasher circuit and island counter plug shared circuit which may lead to equipment failure. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 5.png | file://x:/photopub/docs/0000000495/17466e55-b9b0-4b33-afda-adfa89b87f3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__847a40f8_d069_4f75_b758_6cfa098129bc
PROP-599972-2016 | 2224096 | 9/27/2016 3:35:54 AM | ASSESS: PR OP: RAP | png | #asFound | PR029 | Malfunction that is: may not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | Fuel leaking from fuel tank inside machine room results in fire hazard. | 3 | Malfunction that is: may not be reasonably detectable by maintenance program Likely to propagate | Evacuation_drive_fuel_tank_leak.png | file://x:/photopub/docs/0000000496/a6405743-6c82-4ab1-a4ca-a3426ab25f5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__BF8C7355_98FB_4AB3_8106_1FBF2105E551
AMIN-674730-2016 | AM-442508-2016 | 9/30/2016 | ASSESS: AM IN: Acceptance | png | #asFound | AM028 | Procedures/Signs not posted Improper training or procedure | 1 | 1 | At the time of inspection a delineation perimeter is not installed around the unit. If this unit were operating this would present a hazard to spectators that would come too close to the device. | 1 | Procedures/Signs not posted Improper training or procedure | No_delineation_perimeter_installed_around_unit.png | file://x:/photopub/docs/0000000496/9f6cd004-da62-431a-b649-c89eb0d1177a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__303ee481_540d_430c_96ed_6d1fde50407e
AMIN-674706-2016 | AM-442489-2016 | 9/30/2016 | ASSESS: AM IN: Acceptance | png | #asFound | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 3 | A small number of the manufacturer specified attachment point were not anchored. Device was not operating for public at the time of inspection. In the event of windy condition there is a risk that the device could roll over resulting in a injury hazard to people near the device. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Attachment_point_not_anchored.png | file://x:/photopub/docs/0000000496/87d4644a-eff4-45d0-b020-0cba6facff9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b297107_6c2c_43f1_b80b_ff04d4a168df
AMIN-674601-2016 | AM-442460-2016 | 9/30/2016 | ASSESS: AM IN: Acceptance | png | #asFound | AM042 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 1 | 1 | Tear was noted in the material used as the sliding surface which lays over the inflatable structure. There is a risk that a person sliding down the slide could become entangled and injured. The operator intended not to utilize the 1 damaged lane of 4 lanes and therefore risk level is very minimal. | 1 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Tear_in_slide_material.png | file://x:/photopub/docs/0000000496/a4856647-27eb-4b62-be92-c44dca714de5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd73205b_1a4e_4f67_9d1f_9045a30749dd
ELIN-673857-2016 | UW-444447-2016 | 9/29/2016 6:14:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | The buried Cab tire will always be at risk for mechanical damage as well as environmental damage where it exits and enters the ground . This will result in a shock hazard if not corrected. | 4 | Conductors, Misuse of flexible cords. | Cab_tire_in_wall.png | file://x:/photopub/docs/0000000492/0fe0537d-5167-41c5-80ee-3d7489790c86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5a92757_2c99_45ca_b925_9133d06e212d
ELIN-673849-2016 | UW-444442-2016 | 9/28/2016 3:36:55 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | The cab tire is directly buried into drive way and has no mechanical protection where it enters or exits the ground. The primary hazard is that the unapproved cable will break down by force such as a weed eater or just break down from the elements. Either of these scenarios would create a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. | Cab_tire_exiting_ground_.png | file://x:/photopub/docs/0000000492/35ea3138-5521-4636-8439-80c8252b71f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5fb3eb6_ef73_4219_86e1_063b179154db
ELIN-673849-2016 | UW-444442-2016 | 9/28/2016 3:36:55 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | The cab tire is directly buried into drive way and has no mechanical protection where it enters or exits the ground. The primary hazard is that the unapproved cable will break down by force such as a weed eater or just break down from the elements. Either of these scenarios would create a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. | Cab_tire_entering_wall.png | file://x:/photopub/docs/0000000492/186bcf0f-f816-4629-8bc1-92444850a1eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5fb3eb6_ef73_4219_86e1_063b179154db
ELIN-673849-2016 | UW-444442-2016 | 9/28/2016 3:36:55 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | The cab tire is directly buried into drive way and has no mechanical protection where it enters or exits the ground. The primary hazard is that the unapproved cable will break down by force such as a weed eater or just break down from the elements. Either of these scenarios would create a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. | Light_fixture_in_fenced_area.png | file://x:/photopub/docs/0000000492/59f71f97-ffac-4485-8241-ad69434715fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5fb3eb6_ef73_4219_86e1_063b179154db
ELIN-673857-2016 | UW-444447-2016 | 9/29/2016 6:14:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | The buried Cab tire will always be at risk for mechanical damage as well as environmental damage where it exits and enters the ground . This will result in a shock hazard if not corrected. | 4 | Conductors, Misuse of flexible cords. | Buried_cab_tire_2.png | file://x:/photopub/docs/0000000492/88a5be4b-355e-49d4-b558-5e686808a6f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5a92757_2c99_45ca_b925_9133d06e212d
ELIN-673857-2016 | UW-444447-2016 | 9/29/2016 6:14:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | The buried Cab tire will always be at risk for mechanical damage as well as environmental damage where it exits and enters the ground . This will result in a shock hazard if not corrected. | 4 | Conductors, Misuse of flexible cords. | Cab_tire_buried.png | file://x:/photopub/docs/0000000492/9c36b2d4-4635-40a5-9c35-54eeff3f45b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5a92757_2c99_45ca_b925_9133d06e212d
ELIN-673857-2016 | UW-444447-2016 | 9/29/2016 6:14:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | The buried Cab tire will always be at risk for mechanical damage as well as environmental damage where it exits and enters the ground . This will result in a shock hazard if not corrected. | 4 | Conductors, Misuse of flexible cords. | Outside_receptacle_in_fenced_area.png | file://x:/photopub/docs/0000000492/12139e2f-1907-4a7b-a3a9-5438e51e85ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5a92757_2c99_45ca_b925_9133d06e212d
ELIN-673857-2016 | UW-444447-2016 | 9/29/2016 6:14:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | The buried Cab tire will always be at risk for mechanical damage as well as environmental damage where it exits and enters the ground . This will result in a shock hazard if not corrected. | 4 | Conductors, Misuse of flexible cords. | Out_door_receptacle_.png | file://x:/photopub/docs/0000000492/10d914e4-6b7d-432a-bef8-e523da86d085.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5a92757_2c99_45ca_b925_9133d06e212d
ELIN-677887-2016 | EL-444116-2016 | 10/6/2016 8:23:59 AM | ASSESS: EL: Final | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Found consumer's service equipment disconnect (rated 120/208 volt 3 phase service 100 amp) has utility supply conductors terminated onto disconnect line terminal which has no over-current devices for protecting conductors and equipment. When consumer's service equipment has no over-current devices installed for protecting conductors, the service and other electrical equipment downstream is not protected in the event of a short or fault condition and is a possible electrical fire or shock hazard to people or property. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | service_equipment_has_no_fuses_for_protecting_service_conductors_and_equipment.png | file://x:/photopub/docs/0000000497/05b70dae-67a6-4970-b3f1-536cc05f5c1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8fe23ad_824e_47a0_a636_746f78cbf20d
ELIN-678542-2016 | EL-435744-2016 | 10/7/2016 8:17:03 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Found consumer's service equipment disconnect (rated 120/208 volt 3 phase service 100 amp) has utility supply conductors terminated onto disconnect line terminal which has no over-current devices for protecting conductors and equipment. When consumer's service equipment has no over-current devices installed for protecting conductors, the service and other electrical equipment downstream is not protected in the event of a short or fault condition and is a possible electrical fire or shock hazard to people or property. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 100.png | file://x:/photopub/docs/0000000497/65351dcd-acb8-4e25-9fdd-a4cf21dd8711.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__272d1c41_949a_4c57_a62b_4d8d3f50d60b
ELIN-677887-2016 | EL-444116-2016 | 10/6/2016 8:23:59 AM | ASSESS: EL: Final | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Found consumer's service equipment disconnect (rated 120/208 volt 3 phase service 100 amp) has utility supply conductors terminated onto disconnect line terminal which has no over-current devices for protecting conductors and equipment. When consumer's service equipment has no over-current devices installed for protecting conductors, the service and other electrical equipment downstream is not protected in the event of a short or fault condition and is a possible electrical fire or shock hazard to people or property. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Consumers_service_entrance_equipment_and_meterbase.png | file://x:/photopub/docs/0000000497/78481017-90e8-42d0-9884-7697188c8a01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8fe23ad_824e_47a0_a636_746f78cbf20d
ELIN-678542-2016 | EL-435744-2016 | 10/7/2016 8:17:03 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Found consumer's service equipment disconnect (rated 120/208 volt 3 phase service 100 amp) has utility supply conductors terminated onto disconnect line terminal which has no over-current devices for protecting conductors and equipment. When consumer's service equipment has no over-current devices installed for protecting conductors, the service and other electrical equipment downstream is not protected in the event of a short or fault condition and is a possible electrical fire or shock hazard to people or property. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | service_equipment_without_fuses.png | file://x:/photopub/docs/0000000497/31fed7ac-6eb8-47d9-91ef-05806ff72f4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__272d1c41_949a_4c57_a62b_4d8d3f50d60b
ELIN-678236-2016 | EL-440987-2016 | 10/7/2016 7:17:56 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cable is required to be installed in locations with an ambient temperature not exceeding 30 Â°C. When the cable is installed adjacent to heating ducts, a 50mm clearance or thermal barrier is required. This is required so that the increased temperature from the heating duct does not cause the cable to exceed the conductor temperature rating which could lead to insulation breakdown of the conductor. In this installation in a single family dwelling, non-metallic cable was installed where the cable came in contact with the heating ducts. When this cable is energized and under load, the conductor insulation could break down and cause a risk of a fire hazard or equipment breakdown. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_in_contact_with_duct.png | file://x:/photopub/docs/0000000497/715d0173-5e90-464f-ab5a-cda941248996.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2da6f68a_4669_4de1_9336_4d6beafc9f4b
ELIN-678236-2016 | EL-440987-2016 | 10/7/2016 7:17:56 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cable is required to be installed in locations with an ambient temperature not exceeding 30 Â°C. When the cable is installed adjacent to heating ducts, a 50mm clearance or thermal barrier is required. This is required so that the increased temperature from the heating duct does not cause the cable to exceed the conductor temperature rating which could lead to insulation breakdown of the conductor. In this installation in a single family dwelling, non-metallic cable was installed where the cable came in contact with the heating ducts. When this cable is energized and under load, the conductor insulation could break down and cause a risk of a fire hazard or equipment breakdown. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_in_contact_with_ducts_2.png | file://x:/photopub/docs/0000000497/203fc875-f34a-4aaf-82f3-30b950947ac1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2da6f68a_4669_4de1_9336_4d6beafc9f4b
ELIN-669186-2016 | EL-416749-2016 | 9/22/2016 2:44:48 PM | ASSESS: EL: Service Connection | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | 120 v branch circuits connected temporarily without permission and in unsafe manner which may lead to shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 1.png | file://x:/photopub/docs/0000000489/1f18d17b-7cde-4ca5-a2c5-71a97fc6140a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f5be030_f5b3_4680_a515_9c3381322619
ELIN-669186-2016 | EL-416749-2016 | 9/22/2016 2:44:48 PM | ASSESS: EL: Service Connection | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | 120 v branch circuits connected temporarily without permission and in unsafe manner which may lead to shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 2.png | file://x:/photopub/docs/0000000489/dd9372df-bfa7-4d22-8e48-a4e9cd319b36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f5be030_f5b3_4680_a515_9c3381322619
ELIN-663890-2016 | EL-429885-2016 | 9/20/2016 9:47:56 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | The 120 volt wiring at this house has not been adequately stapled. This may lead to the cables being pinched between the wall covering and the wooden stud. This could lead to cable damage which is afire and shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | No_stapling.png | file://x:/photopub/docs/0000000488/0a0449f2-341a-4d31-90c0-cecd21899764.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47fe4d99_103a_4f32_91f9_b93882488dfa
ELIN-663890-2016 | EL-429885-2016 | 9/20/2016 9:47:56 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | The 120 volt wiring at this house has not been adequately stapled. This may lead to the cables being pinched between the wall covering and the wooden stud. This could lead to cable damage which is afire and shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 28__between_plugs.png | file://x:/photopub/docs/0000000488/38106f0c-85a2-4ddd-b6d6-8402515aa682.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47fe4d99_103a_4f32_91f9_b93882488dfa
EDIN-683595-2016 | ED-043104-2013 | 10/13/2016 3:23:02 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | Rear car door restrictor not functioning properly | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Car_door_restrictor.png | file://x:/photopub/docs/0000000499/d470e4e7-1378-4407-9332-90155f55a03a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ba53773_b872_42f2_b987_7e02bdb9c5b9
BPOP-670661-2016 | BPV-405468-2015 | 10/17/2016 3:10:22 PM | ASSESS: Propane PV: Periodic | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | Pressure relief valve missing rain cap | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Missing_rain_cap.png | file://x:/photopub/docs/0000000501/daf86080-e8ce-4be8-b643-bf7e5b7bc739.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7bfcaf7_99f4_4d60_aad2_2e1b37ee876a
ELIN-665316-2016 | UW-438800-2016 | 9/16/2016 5:18:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized wiring in boxes with switches, receptacles, light fixtures and junction boxes are required to have cover plates installed on them. This is required to prevent accidental contact with energized terminals on switches and receptacles and energized conductors at fixtures and junction boxes. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation has energized terminals exposed to contact at switches, receptacles, and wiring/connections exposed to contact, and damage, because required cover plates are not installed. This is a potential shock and fire hazard if persons or objects contact energized terminals/wiring or if wiring or equipment fails and boxes do not contain thermal energy as intended. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_receptacles_in_cabin_without_cover_plates_in_place.png | file://x:/photopub/docs/0000000488/75b6ef7b-1ae4-4ef2-a7ef-10bc8786b6d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c8e24ff_fdb0_4ac2_99ea_c1914981aaae
ELIN-665316-2016 | UW-438800-2016 | 9/16/2016 5:18:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized wiring in boxes with switches, receptacles, light fixtures and junction boxes are required to have cover plates installed on them. This is required to prevent accidental contact with energized terminals on switches and receptacles and energized conductors at fixtures and junction boxes. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation has energized terminals exposed to contact at switches, receptacles, and wiring/connections exposed to contact, and damage, because required cover plates are not installed. This is a potential shock and fire hazard if persons or objects contact energized terminals/wiring or if wiring or equipment fails and boxes do not contain thermal energy as intended. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_switch_and_receptacle_in_crawl_space_without_cover_plates_in_place.png | file://x:/photopub/docs/0000000488/365734a7-d717-44d3-9830-ba49ca437f97.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c8e24ff_fdb0_4ac2_99ea_c1914981aaae
ELIN-665316-2016 | UW-438800-2016 | 9/16/2016 5:18:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized wiring in boxes with switches, receptacles, light fixtures and junction boxes are required to have cover plates installed on them. This is required to prevent accidental contact with energized terminals on switches and receptacles and energized conductors at fixtures and junction boxes. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation has energized terminals exposed to contact at switches, receptacles, and wiring/connections exposed to contact, and damage, because required cover plates are not installed. This is a potential shock and fire hazard if persons or objects contact energized terminals/wiring or if wiring or equipment fails and boxes do not contain thermal energy as intended. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exterior_receptacle_at_house_energized_without_a_cover_plate.png | file://x:/photopub/docs/0000000488/afa4d09f-f2d3-45d9-bbb6-8faf0cc006c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c8e24ff_fdb0_4ac2_99ea_c1914981aaae
GAUP-643184-2016 | UW-433005-2016 | 9/19/2016 4:03:42 PM | ASSESS: GA UP: Equipment Observation | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | Uncertified appliance connected to gas supply. Uncertified appliances which have not been tested for for compliance with a standard may not be safe for use. | 3 | Uncertified appliance connected to gas supply but not in service | Uncertified_burners.png | file://x:/photopub/docs/0000000488/0029eb3a-ee78-46e6-bfb0-16a6761135aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46d6b637_4a13_4ac6_9087_091eb9f185f7
GAIN-637649-2016 | GA-421537-2016 | 9/20/2016 2:04:02 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | Location of vent termination could cause condensation of frost buildup on adjacent surface. | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Vent_termination_not_compliant_.png | file://x:/photopub/docs/0000000488/53bae8b3-7b7a-4a58-adfe-9b6bd0294cbe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08005931_2a50_44d4_a25c_752e2612121a
GAIN-658765-2016 | GA-424139-2016 | 9/20/2016 1:38:48 PM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | Certified connector is not approved for application. | 2 | Certified appliance connector installed but not approved for application | Wrong_appliance_connector_for_application.png | file://x:/photopub/docs/0000000488/9b2b8d74-e86d-44c4-9984-fd10da57d7f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a849b99e_bd99_4c00_8a97_57dec0403b9c
ELIN-664738-2016 | EL-396137-2016 | 9/20/2016 1:53:36 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | nmsc_in_wall.png | file://x:/photopub/docs/0000000488/895f3691-2ffc-48db-9d39-6ad74fe47d72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a465e59_8cec_4268_8a96_73d3ed00fd17
ELIN-661888-2016 | EL-436637-2016 | 10/4/2016 9:55:54 AM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | Conductors not housed in a box or device. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | A.png | file://x:/photopub/docs/0000000495/5772a6ff-4bf6-46c7-9072-db4bb895fc14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f80725e_78b3_4794_83bb_b7d898bee94e
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 9.png | file://x:/photopub/docs/0000000490/eb0b6150-ee79-4a45-bb13-9b57bc711481.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 5.png | file://x:/photopub/docs/0000000490/7b2773f4-8620-443b-9e89-fcbc22ff7d90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 10.png | file://x:/photopub/docs/0000000490/bf1d9a84-2450-4094-acc8-6ecf419fd425.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3.png | file://x:/photopub/docs/0000000490/106e51cb-18c4-4f69-8074-b2d65b32aba0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 11.png | file://x:/photopub/docs/0000000490/fb5b8ece-e8e7-4d81-b063-303473ce5809.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 15.png | file://x:/photopub/docs/0000000490/f46cf65e-f61d-4ebc-bae0-e557736f094a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELIN-670711-2016 | EL-439865-2016 | 9/30/2016 2:53:54 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | This assessment found 15m of service cable coiled up at the panel, on the ground. Service cable is unfused posing a greater shock and fire hazard than a fused cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Service_cable_coil.png | file://x:/photopub/docs/0000000493/82231b93-757a-43b3-a5c1-665c1e9d22f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c47cd427_1a62_48d4_b8d7_94afbb527cca
ELIN-670711-2016 | EL-439865-2016 | 9/30/2016 2:53:54 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | This assessment found 15m of service cable coiled up at the panel, on the ground. Service cable is unfused posing a greater shock and fire hazard than a fused cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Point_of_attachment.png | file://x:/photopub/docs/0000000493/34a303e4-9544-422e-b394-51d124987d1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c47cd427_1a62_48d4_b8d7_94afbb527cca
ELOP-656110-2016 | EL-039256-2013 | 9/29/2016 12:49:20 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Cable on the service pole is subjected to mechanical damage near ground level. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Cable.png | file://x:/photopub/docs/0000000493/23407d4d-8440-40db-beb9-82419f197699.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4C562117_A249_4BA9_9B32_B8B7E6A9FD21
ELOP-656899-2016 | EL-039276-2013 | 9/29/2016 2:29:07 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Cable is not protected and is subject to mechanical damage. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Cable-2.png | file://x:/photopub/docs/0000000493/6db65b79-1828-4c65-aa3b-fc6c16fd05ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__EC4B0DDE_8ABB_4D89_A4E5_2AF2B90121FC
ELOP-656077-2016 | EL-039298-2013 | 9/29/2016 2:08:12 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Cord.png | file://x:/photopub/docs/0000000493/1c86a887-4ea9-4dc4-b205-58a0d2d5e4ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C38B4195_8F69_42D7_A56E_DD3B1296656B
ELOP-656074-2016 | EL-039266-2013 | 9/29/2016 1:31:38 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | AC90 is replacing a flexible cord. | 3 | Conductors Equipment is not approved for the specific use. | Ac90.png | file://x:/photopub/docs/0000000493/155fb5b3-073e-4e31-bf93-b66487075d1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__BA0E63A7_F2E5_4AA2_A0B7_2A6E851A9268
ELHE-699417-2016 | HE-464548-2016 | 11/7/2016 12:59:54 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL052 | Protection and control Circuit breakers connected to branch circuit derived from a 3-wire grounded neutral system are not 2-pole, or the handles of single pole breakers are not interlocked | 3 | 3 | A fault on the heating circuits may not trip the circuit breakers that are not 2Pole - possibility for shock or fire. | 3 | Protection and control Circuit breakers connected to branch circuit derived from a 3-wire grounded neutral system are not 2-pole, or the handles of single pole breakers are not interlocked | Doubled_circuits_wrong_over_current.png | file://x:/photopub/docs/0000000513/f8de8c0c-1e42-4d62-8fe5-15c0f7110f79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de5f6545_a046_44ab_8c4b_f7f90088c72a
ELIN-674050-2016 | EL-444703-2016 | 9/29/2016 1:24:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | In an AC single-phase, 3-wire system, the neutral conductor must be connected to ground to limit the voltage level on the circuit and to protect devices associated with the circuit. The grounded system also facilitates a low-impedance fault current path through the grounded service conductor that enables the overcurrent devices to operate quickly. In this installation for a residential electrical service upgrade, a ground electrode and ground conductor where not installed to the new electrical panel. With out the neutral in the panel being grounded, high voltage levels could be present on the circuit and the over current devices may not react quickly enough. This potentially could create a shock or fire hazard to persons and damage to equipment or conductors. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Meter_location.png | file://x:/photopub/docs/0000000492/b4bb8745-d58c-4275-8c16-a95846360916.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b23daf92_fad2_4e45_a7ae_86f0516b76e2
ELIN-674050-2016 | EL-444703-2016 | 9/29/2016 1:24:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | In an AC single-phase, 3-wire system, the neutral conductor must be connected to ground to limit the voltage level on the circuit and to protect devices associated with the circuit. The grounded system also facilitates a low-impedance fault current path through the grounded service conductor that enables the overcurrent devices to operate quickly. In this installation for a residential electrical service upgrade, a ground electrode and ground conductor where not installed to the new electrical panel. With out the neutral in the panel being grounded, high voltage levels could be present on the circuit and the over current devices may not react quickly enough. This potentially could create a shock or fire hazard to persons and damage to equipment or conductors. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Inside_Panel.png | file://x:/photopub/docs/0000000492/ca429fe4-f089-425d-b2f0-76aba36da047.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b23daf92_fad2_4e45_a7ae_86f0516b76e2
ELIN-683793-2016 | EL-437677-2016 | 10/14/2016 11:02:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL111 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | 2 | 2 |  | 2 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | Unsupported_cables.png | file://x:/photopub/docs/0000000500/cc0baef6-2d20-4c83-98b9-4ab972d787b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de2348cb_8d3c_4dda_a038_ddec5d3da81a
ELIN-683793-2016 | EL-437677-2016 | 10/14/2016 11:02:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL111 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | 2 | 2 |  | 2 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | NMD90_on_heating_duct.png | file://x:/photopub/docs/0000000500/bef802eb-8cc1-4d9a-8559-756f244c4cdd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de2348cb_8d3c_4dda_a038_ddec5d3da81a
ELIN-683793-2016 | EL-437677-2016 | 10/14/2016 11:02:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL111 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | 2 | 2 |  | 2 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | NMD90_heat_duct.png | file://x:/photopub/docs/0000000500/a03ed2c7-aedc-4cd6-8a0d-9d5beecf609a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de2348cb_8d3c_4dda_a038_ddec5d3da81a
ELIN-702076-2016 | EL-425411-2016 | 11/14/2016 9:56:48 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 | 120 volt branch circuits pinched from staples and may cause cable overheating or failure. | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2.png | file://x:/photopub/docs/0000000515/b292da4e-9f9f-4ec1-a131-0f6c7ee70296.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd2024ce_6a62_4722_98ea_824bfcfb4e37
ELIN-702076-2016 | EL-425411-2016 | 11/14/2016 9:56:48 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 | 120 volt branch circuits pinched from staples and may cause cable overheating or failure. | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 1.png | file://x:/photopub/docs/0000000515/0139bc30-5b6a-479f-8e4d-55c91cc69d13.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd2024ce_6a62_4722_98ea_824bfcfb4e37
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 17.png | file://x:/photopub/docs/0000000490/2a90e5fe-9f8b-4e18-b3c2-0accf67a6866.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 12.png | file://x:/photopub/docs/0000000490/26fad793-ff7c-43f4-a483-3405ab3e854f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 14.png | file://x:/photopub/docs/0000000490/2e7a8b9d-4fe8-49b4-8c03-872903667c5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 16.png | file://x:/photopub/docs/0000000490/9969ec97-6361-4e80-ade1-f9a8d03bbba8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 4.png | file://x:/photopub/docs/0000000490/7bdc0a90-c9af-4dcc-97fa-b3befa7a0476.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 6.png | file://x:/photopub/docs/0000000490/049c5e53-5c62-4e2f-97d0-077fd231914a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 8.png | file://x:/photopub/docs/0000000490/0d2b9e36-51fd-4864-87dd-b295ac9f3d7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELIN-691707-2016 | EL-450822-2016 | 10/27/2016 2:27:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | The 125 amp 120/240 volt service grounding conductor is terminated to the can and not the grounded identified conductor. During a fault this could lead to an equipment damage issue. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Wrong_ground_connection.png | file://x:/photopub/docs/0000000506/5a49e0f3-4765-4230-bc25-83b2cdda1c1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac88a676_0c82_46c0_b941_6fcb73bd6d94
ELIN-671925-2016 | EL-397865-2016 | 9/27/2016 12:19:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Protection plate required to protect 3" service conductor conduit. This is a equipment damage condition. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | No_protection_plate_.png | file://x:/photopub/docs/0000000491/e3993170-5abb-4715-a0ac-f76eee9680ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__04a63a23_b6a5_4f17_a983_ddb53971ecbf
ELIN-671931-2016 | EL-396281-2016 | 9/27/2016 1:26:17 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | The ground conductor is not installed into the main distribution and grounded to the neutral system. This is a thermal effect condition. 125 Amps, 120/240 Volt. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_conductor_not_installed_into_main_distribution_and_grounded_to_the_neutral_system_.png | file://x:/photopub/docs/0000000491/04be1a06-1d36-4423-8603-c5d4e21fd7c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e293ea7b_89c9_40a2_a93c_db8ebe3c31ed
BPVOP-697071-2016 | 2288743 | 11/4/2016 3:43:24 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. During the inspection of stationary air receiver, I found a Pressure Relief Device not replaced within the last 5 years as per CSA B51. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD.png | file://x:/photopub/docs/0000000511/65e8bd07-ef99-47d9-be6b-b6f731049e5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__219531eb_4ef2_4a5a_9f80_45b24026b232
ELOP-684350-2016 | 3241 | 11/16/2016 3:33:47 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 4 | Ground fault protection is required on services greater than 1000 amps where the voltage exceeds 150v to ground. This is an explosion hazard should a fault progress to a phase to phase fault. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | Bb.png | file://x:/photopub/docs/0000000517/67d9158b-ac1a-4ad8-9323-a06ba755de8c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30fbd2ed_97f0_425e_919a_83b1bdcd5ad8
ELOP-684350-2016 | 3241 | 11/16/2016 3:33:47 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 4 | Ground fault protection is required on services greater than 1000 amps where the voltage exceeds 150v to ground. This is an explosion hazard should a fault progress to a phase to phase fault. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | Be.png | file://x:/photopub/docs/0000000517/7fe5a4b3-77cd-4cc0-8ba8-10f20b36b818.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30fbd2ed_97f0_425e_919a_83b1bdcd5ad8
ELOP-684192-2016 | 5118257 | 11/16/2016 9:43:31 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | Gradient control mats require connection to the disconnect handle by two separate conductors. This is a potential shock hazard should the one conductor become damaged. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Ab.png | file://x:/photopub/docs/0000000517/6647191b-23f4-4df8-8d8f-5595b53d9ac8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a62550d_b309_4ca3_a5d8_25cede4158ab
ELOP-684350-2016 | 3241 | 11/16/2016 3:33:47 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 4 | Ground fault protection is required on services greater than 1000 amps where the voltage exceeds 150v to ground. This is an explosion hazard should a fault progress to a phase to phase fault. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | Bd.png | file://x:/photopub/docs/0000000517/031febec-a371-4a03-b974-3aa3248bdda4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30fbd2ed_97f0_425e_919a_83b1bdcd5ad8
ELOP-684350-2016 | 3241 | 11/16/2016 3:33:47 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 4 | Ground fault protection is required on services greater than 1000 amps where the voltage exceeds 150v to ground. This is an explosion hazard should a fault progress to a phase to phase fault. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | Bc.png | file://x:/photopub/docs/0000000517/6cc7da53-e5d8-4023-96b8-2782d926b489.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30fbd2ed_97f0_425e_919a_83b1bdcd5ad8
ELOP-702727-2016 | 2913 | 11/15/2016 10:54:57 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Equipment enclosures are required to be bonded to ground. This is a shock hazard. If the metal enclosure becomes accidentally energized the protection devices will not function. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | B.png | file://x:/photopub/docs/0000000517/754941ee-5446-4583-8271-889868d8ac40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__096B2B20_0CE4_4988_9F88_595555557F6E
ELOP-684350-2016 | 3241 | 11/16/2016 3:33:47 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 4 | Ground fault protection is required on services greater than 1000 amps where the voltage exceeds 150v to ground. This is an explosion hazard should a fault progress to a phase to phase fault. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | Bg.png | file://x:/photopub/docs/0000000517/f2a1593b-8650-4c41-ae70-72ab31c2e0bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30fbd2ed_97f0_425e_919a_83b1bdcd5ad8
ELOP-684192-2016 | 5118257 | 11/16/2016 9:43:31 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | Gradient control mats require connection to the disconnect handle by two separate conductors. This is a potential shock hazard should the one conductor become damaged. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Ac.png | file://x:/photopub/docs/0000000517/48298b78-121b-4fd0-963b-c6ca85f788e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a62550d_b309_4ca3_a5d8_25cede4158ab
ELOP-684192-2016 | 5118257 | 11/16/2016 9:43:31 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | Gradient control mats require connection to the disconnect handle by two separate conductors. This is a potential shock hazard should the one conductor become damaged. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Aa.png | file://x:/photopub/docs/0000000517/1274d39b-2fe4-49e8-93a8-9cbf5395047b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a62550d_b309_4ca3_a5d8_25cede4158ab
ELOP-702727-2016 | 2913 | 11/15/2016 10:54:57 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Equipment enclosures are required to be bonded to ground. This is a shock hazard. If the metal enclosure becomes accidentally energized the protection devices will not function. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | A.png | file://x:/photopub/docs/0000000517/430ea7d1-57b1-4aee-8f87-e44b752be3cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__096B2B20_0CE4_4988_9F88_595555557F6E
ELOP-702729-2016 | 2916 | 11/15/2016 12:18:40 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 3 | Cable and telephone service are required to bonded and grounded where they enter buildings. There is an fire and shock hazard from exposure to overhead power lines and lightening. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | D.png | file://x:/photopub/docs/0000000517/09391080-4308-4343-878a-dd5e6ec14c61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4C721A45_DE42_4AC1_8453_1C63B139FF92
ELOP-702729-2016 | 2916 | 11/15/2016 12:18:40 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 3 | Cable and telephone service are required to bonded and grounded where they enter buildings. There is an fire and shock hazard from exposure to overhead power lines and lightening. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | C.png | file://x:/photopub/docs/0000000517/9e15415e-73a6-466d-bdc6-dbf8daa6435a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4C721A45_DE42_4AC1_8453_1C63B139FF92
ELOP-684350-2016 | 3241 | 11/16/2016 3:33:47 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 4 | Ground fault protection is required on services greater than 1000 amps where the voltage exceeds 150v to ground. This is an explosion hazard should a fault progress to a phase to phase fault. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | Bf.png | file://x:/photopub/docs/0000000517/4fb510b0-e984-4e15-8754-54f48967c080.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30fbd2ed_97f0_425e_919a_83b1bdcd5ad8
ELIN-683526-2016 | EL-429867-2016 | 10/14/2016 1:35:52 PM | ASSESS: EL: Final | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Non metallic sheathed cable has the outer jacket burnt. Exterior sheathing protects the internal current carrying conductors, internal conductors require protection as the insulation on these conductors is thin and does not provide substantial protection for the current carrying conductors. Failure of this insulation would provide a risk of fire and shock to property and persons. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Non_metallic_sheathed_cable_jacket_burnt.png | file://x:/photopub/docs/0000000500/c7fe2056-195c-4ed1-9117-2ca44e1d2a9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ef1e9ee_a0d2_40d5_a9a9_62466a7564f8
ELIN-683289-2016 | EL-426006-2016 | 10/14/2016 2:17:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The 400 amp 120/240 volt overhead service includes only 1x 63mm rig mast (second mast is made of EMT). This can create an equipment damage issue with a possible cantilever load in excess of a single 63mm masts capability | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Mast_and_EMT_into_disconnect.png | file://x:/photopub/docs/0000000500/d84992ff-b163-4cf9-b1e8-95542aa3f7f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10223208_aab9_4850_b36c_3673590ba2b8
ELIN-683289-2016 | EL-426006-2016 | 10/14/2016 2:17:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The 400 amp 120/240 volt overhead service includes only 1x 63mm rig mast (second mast is made of EMT). This can create an equipment damage issue with a possible cantilever load in excess of a single 63mm masts capability | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Mast_and_EMT.png | file://x:/photopub/docs/0000000500/c7399b19-10dc-4825-bc08-4a67dc939dac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10223208_aab9_4850_b36c_3673590ba2b8
ELIN-680413-2016 | EL-429911-2016 | 10/14/2016 11:34:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | This assessment found a residential house under construction with an electrical panel exposed to the weather. This equipment is required to be protected from the weather. If the main breaker becomes wet there is a risk of it failing to operate properly posing a shock and fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Panel_exposed.png | file://x:/photopub/docs/0000000500/67148abd-f2f9-44ae-8377-beb9189b705b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f46a3766_93fe_41aa_865b_1f6622fd80a8
ELIN-688384-2016 | EL-455201-2016 | 10/24/2016 4:08:10 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | The 40 amp 120/240 volt range receptacle is mounted too high. The receptacle box is mounted approx 300mm above the floor giving zero clearance from heating appliance, this can create a thermal hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Range_outlet.png | file://x:/photopub/docs/0000000504/5d403a95-cc82-4141-bd22-a9a344c453c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0f6b6b3_a2be_427f_b5d6_37ea2f763d76
GAIN-697098-2016 | GA-455403-2016 | 11/7/2016 3:27:29 PM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | The solenoid gas valve used is not approved for fuel gas and could fail, causing fire or injury | 3 | Non-compliant material/fittings installed | Gas_valve.png | file://x:/photopub/docs/0000000512/e17967c1-1895-4084-bcfd-7ba83ce436f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2b8429f_ea77_4c62_ba24_abf1b73daf68
GAHE-682748-2016 | HE-450926-2016 | 10/21/2016 1:58:46 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dryer.png | file://x:/photopub/docs/0000000505/bfedf043-d03e-4022-bbef-3df2be584e0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__232332a8_5a8a_4089_90e9_91fa36452a90
GAIN-559825-2016 | GA-346736-2016 | 10/24/2016 2:08:05 PM | ASSESS: GA: Final | png | #asFound | GA131 | Equipment service clearance non compliant | 1 | 1 | Appliances are located on a roof with out proper access to service. | 1 | Equipment service clearance non compliant | Roof_access.png | file://x:/photopub/docs/0000000505/5fe96dfc-e92e-46d4-b25e-b29b5675f710.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__347fe1e4_dc9e_4037_a21d_6fb1d1b8522e
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 7.png | file://x:/photopub/docs/0000000490/aa185993-e9e6-4c9d-a04f-95ede2312f93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 1.png | file://x:/photopub/docs/0000000490/81340cf2-5405-4c23-847e-b148210f5717.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 13.png | file://x:/photopub/docs/0000000490/2eafe224-6f5d-44bb-8874-6bb9928293ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
ELHE-663694-2016 | HE-437797-2016 | 9/21/2016 9:28:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 2.png | file://x:/photopub/docs/0000000490/2d7e3b87-35cf-449e-bf95-d46c7e097373.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f350b89_348f_44f2_8ede_faff29d8e374
BPVOP-697070-2016 | 2288736 | 11/3/2016 12:19:11 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP019 | 1.0.2 Clearances/Maintenance - Foundations and supports have deterioration including spalling and cracking that are likely to propagate. | 2 | 2 |  | 2 | 1.0.2 Clearances/Maintenance - Foundations and supports have deterioration including spalling and cracking that are likely to propagate. | Corroded_Supports.png | file://x:/photopub/docs/0000000511/ec42d2ca-801d-41c4-8983-00946ddb1afe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__50bac145_a0ae_463b_9338_2f9782da7738
ELIN-688589-2016 | EL-282758-2015 | 10/28/2016 12:00:24 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | Branch circuits operating on 15 amp breakers and a 40 amp breaker at 240 volts are Non metallic sheathed cable enclosed in walls and in bottom of trusses in a building housing chickens and rabbits. Rodent activity is common in buildings with livestock due to storage of feed, bedding and other attractants. Non metallic sheathed cable is subject to damage that could cause property damage and injury to livestock or persons. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | NMD_enclosed_in_walls_chicken_coop.png | file://x:/photopub/docs/0000000507/0c65189b-97c8-4cb2-ac6a-d6f1d9d31d6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a32dba5_6c0e_41c7_a7ca_a42e39ef394e
EDOP-692957-2016 | 3449015 | 10/26/2016 11:54:56 AM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | During a periodic inspection excessive lubricant was found on the governor rope. The governor relies upon the traction relationship between the governor rope and sheave. If excess lubrication is on the governor rope this may slip through the governor sheave and prevent the activation of the safeties (mechanical safety brakes). The safeties on an elevator provide a safe stop for rider in the event of an over-speeding elevator in the down direction. If the governor is unable to activate the safeties this may possible cause an over speeding elevator to hit the buffer with excessive speed possibly causing injury to the occupants riding in the elevator. | 3 | Defects that are: Not detected by maintenance program Likely to progress | Governor_rope.png | file://x:/photopub/docs/0000000509/916d1536-328b-4f91-b096-275a15903537.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e989833_caf8_4b6c_abdf_efb45fe1270b
ELIN-698862-2016 | EL-436946-2016 | 11/10/2016 10:55:38 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | The cables run inside the attic space are exposed to possible damage from individuals walking in the attic. The tension on the cables after being stepped on can damage the PVC insulation at staples used to hold the cables in place. This can become a shock or fire hazard in the future. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Home_runs.png | file://x:/photopub/docs/0000000514/f611ce7f-fafd-4c2f-8084-acf0e49fcc51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa4d5be9_3408_465f_b02b_0f290534f88a
ELIN-687739-2016 | EL-445408-2016 | 10/26/2016 12:04:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Electrical service/distribution equipment has been exposed to water and the effects of weather. This presents a serious risk of personal injury (shock) or property damage (thermal event) | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | View01_branch_circuit_breakers.png | file://x:/photopub/docs/0000000506/26301e50-de14-4513-ae3e-6d1604a34047.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14722882_ff5e_48c4_b01d_5f7ba3d6cb05
ELIN-687739-2016 | EL-445408-2016 | 10/26/2016 12:04:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Electrical service/distribution equipment has been exposed to water and the effects of weather. This presents a serious risk of personal injury (shock) or property damage (thermal event) | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | View02_main_distribution.png | file://x:/photopub/docs/0000000506/6b8aebab-77f5-40ce-8f4d-df3b460993d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14722882_ff5e_48c4_b01d_5f7ba3d6cb05
ELIN-690154-2016 | EL-445650-2016 | 10/25/2016 12:40:16 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | Armoured feeder cable not protected from mechanical damage or installed using approved methods (bedding material/depth) and located in close proximity to charged water piping. This presents a serious risk of personal injury (shock) or property damage (thermal event) caused by mechanical damage to cable. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Detail01_feeder.png | file://x:/photopub/docs/0000000506/67d3c235-0d07-4b06-9155-5cf9892b48f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4815be4b_34a7_48ed_8dec_ed1a0d303fea
ELIN-680413-2016 | EL-429911-2016 | 10/14/2016 11:34:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | This assessment found a residential house under construction with an electrical panel exposed to the weather. This equipment is required to be protected from the weather. If the main breaker becomes wet there is a risk of it failing to operate properly posing a shock and fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Panel_wet.png | file://x:/photopub/docs/0000000500/80cf693e-8cac-4f17-a9b8-124d713bfea4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f46a3766_93fe_41aa_865b_1f6622fd80a8
ELIN-699726-2016 | UW-464696-2016 | 11/8/2016 7:59:45 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Electrical equipment is not to be installed if it is not approved for the specific use of that equipment. In this installation, the home owner installed exposed non-metallic sheathed cable for a dryer receptacle in an area that may be subject to mechanical damage and did not use a box connector to secure the cable to the device box. If the cable was to become damaged or pulled out of the device box, there is a potential for a shock hazard to persons or a fire hazard to the dwelling. | 3 | Conductors Equipment is not approved for the specific use. | No_Connector.png | file://x:/photopub/docs/0000000513/05574d29-0ecc-4ba5-836f-b8aff4d5d224.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f3f710fb_d892_4698_b3b1_88ad5dfc7103
ELIN-699726-2016 | UW-464696-2016 | 11/8/2016 7:59:45 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Electrical equipment is not to be installed if it is not approved for the specific use of that equipment. In this installation, the home owner installed exposed non-metallic sheathed cable for a dryer receptacle in an area that may be subject to mechanical damage and did not use a box connector to secure the cable to the device box. If the cable was to become damaged or pulled out of the device box, there is a potential for a shock hazard to persons or a fire hazard to the dwelling. | 3 | Conductors Equipment is not approved for the specific use. | NMSC_not_approved_for_use.png | file://x:/photopub/docs/0000000513/69ad09d2-d062-4473-a00a-61e13f3ba55c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f3f710fb_d892_4698_b3b1_88ad5dfc7103
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Blocking_and__blocking_and_ceiling_of_cables_between_floors.png | file://x:/photopub/docs/0000000513/db034966-ac15-4c3e-9447-da3c91cb42ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Fire_safety.png | file://x:/photopub/docs/0000000513/709c053d-8b1c-416b-b809-f7599e64c564.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | No_accumulat.png | file://x:/photopub/docs/0000000513/87b82e20-b777-455a-a97c-7d6d3d95b2c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Clean_up__clean_up_checklist_for_log_area.png | file://x:/photopub/docs/0000000513/874f8e52-5edf-4875-b797-cee44e2e1f9f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
GAIN-643158-2016 | GA-419676-2016 | 10/25/2016 10:57:23 AM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Street elbows and tees are not permitted because these fittings have both male and female threaded ends. This makes alignment of the piping difficult since the direction of the piping does not always correspond with the fully seated position of the fitting. When the connection is backed off to align the piping, leakage may result | 3 | Non-compliant material/fittings installed | Unapproved_ftgs.png | file://x:/photopub/docs/0000000505/4613271d-f155-467f-9314-232901848be8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c00f1e0e_0285_415b_a4ec_9590354735b0
EDIN-684852-2016 | ED-043068-2013 | 10/15/2016 3:33:58 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED052 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 2 | 2 | Ensure every landing is free of any tripping hazards | 2 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | Trip_hazard.png | file://x:/photopub/docs/0000000500/a3f64603-8ce7-4e20-9449-ba79bfc92c0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__50106130_c9b4_4f2a_8de2_02d2d64b3d0a
ELHE-681690-2016 | HE-437797-2016 | 10/11/2016 2:00:00 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 4.png | file://x:/photopub/docs/0000000498/898c6974-aa13-473f-a962-d83504f6a5ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bc03470_be85_4396_bb60_2175370bc503
ELHE-681690-2016 | HE-437797-2016 | 10/11/2016 2:00:00 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 5.png | file://x:/photopub/docs/0000000498/88dba65d-9feb-4ddd-8262-bb0df5314ecc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bc03470_be85_4396_bb60_2175370bc503
ELHE-681690-2016 | HE-437797-2016 | 10/11/2016 2:00:00 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 6.png | file://x:/photopub/docs/0000000498/877c6e5c-172c-4a9e-a720-77701c1ecc58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bc03470_be85_4396_bb60_2175370bc503
ELHE-681690-2016 | HE-437797-2016 | 10/11/2016 2:00:00 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 1.png | file://x:/photopub/docs/0000000498/468c920a-7b6f-4813-a63d-8f228c806478.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bc03470_be85_4396_bb60_2175370bc503
ELHE-681690-2016 | HE-437797-2016 | 10/11/2016 2:00:00 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3.png | file://x:/photopub/docs/0000000498/3c50b656-c62f-4f21-9680-d46af9c1bfe5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bc03470_be85_4396_bb60_2175370bc503
ELHE-681690-2016 | HE-437797-2016 | 10/11/2016 2:00:00 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 2.png | file://x:/photopub/docs/0000000498/49ae48cd-a63d-4a01-a341-81c94fb6b7a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bc03470_be85_4396_bb60_2175370bc503
ELHE-681690-2016 | HE-437797-2016 | 10/11/2016 2:00:00 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Found 120 volt 1440 watts rated cord connected electric fireplace unit is mounted within an inset of drywall which could become overheated and is not installed or used as required for this approved regulated product. When regulated product is not installed or used as per approved installation and use of approved product, the regulated product could become an electrical fire or shock hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 7.png | file://x:/photopub/docs/0000000498/cc81167d-9001-4e59-b034-df14e3dcac61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bc03470_be85_4396_bb60_2175370bc503
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Wet_wood_chips__wet_wood_chips_on_cable_tray_covers-cleaned_regularly.png | file://x:/photopub/docs/0000000513/14faa4de-eae4-4ef0-8afa-6912a5ff6612.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Blocking_of__blocking_of_cable_through_walls.png | file://x:/photopub/docs/0000000513/fa0d74c6-4bcf-45cd-898b-6e6c06e58d8d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Condition_of.png | file://x:/photopub/docs/0000000513/b0038d09-2ea4-4fa6-88a2-739c07958807.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | DynaStar_maintenan.png | file://x:/photopub/docs/0000000513/91704530-8152-4d54-aac2-5479e5d239a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Clean_up__clean_up_log_checklist_various_areas.png | file://x:/photopub/docs/0000000513/e62fc5bb-4ee7-4e47-bf09-c2d83c8d5532.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Come_bustable__combustible_dust_safety_plan.png | file://x:/photopub/docs/0000000513/6cc76e69-eaa0-46aa-95a8-4849aa3a6049.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Clean_up__clean_up_checklist_various_areas_photo_to.png | file://x:/photopub/docs/0000000513/1390cef4-4ee4-473f-ab07-540726f0717b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Clean_up.png | file://x:/photopub/docs/0000000513/f74ee647-ff0a-4a64-a507-57f2afca0019.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Condition_of__condition_of_floor_in_sorter_area_note_worker_cleaning_floor.png | file://x:/photopub/docs/0000000513/806737f2-872d-4329-9bab-df5c4d60ebee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | No_visible.png | file://x:/photopub/docs/0000000513/77cb56f1-eb09-4d65-99a5-707a93627370.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
ELOP-693411-2016 | 419 | 11/9/2016 1:10:29 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | electrical_log_book.png | file://x:/photopub/docs/0000000513/3c93704b-4fe0-45ec-9668-6cfa06d4920c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b01d2ed_1473_4ad9_9666_125401e70040
PROP-599963-2016 | 4308067 | 10/25/2016 6:21:28 PM | ASSESS: PR OP: RAP | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | Expired fire extinguisher, it may not function properly when required | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Expired_extinguisher_.png | file://x:/photopub/docs/0000000505/fa3a7ffa-1f64-4467-a99f-00327465fc94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8628C2FC_B5F7_4462_9B5C_C3D086801669
ELIN-691357-2016 | EL-415332-2016 | 10/27/2016 11:15:12 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Not energized | 0 | No Created Hazard Identified | Switch_and_meterbase.png | file://x:/photopub/docs/0000000506/c3f9fac0-4e8f-4450-935b-0e49a5172f1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e46d0668_46dd_4190_8aa2_aaff53d39c62
ELIN-705685-2016 | EL-430244-2016 | 11/18/2016 9:02:17 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | A sufficient number of 15A or 20A kitchen outlets have not been supplied in the backsplash, this could lead to overloading the only outlet provided. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Counter_outlet_spacing.png | file://x:/photopub/docs/0000000518/6e08c4dd-2887-4177-bd79-696cd20c6d9f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__132cd0da_097b_479a_9cdd_d84d99de09ba
PROP-679997-2016 | 5008139 | 10/7/2016 11:46:35 AM | ASSESS: PR OP: Annual | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Weld on the ladder wrung is broken, wrung could fail while being climbed. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Tower_4_ladder_wrung.png | file://x:/photopub/docs/0000000498/b468b4f3-1510-428b-bff4-dc8250d3ca9e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9418c078_4aa5_4bce_8276_f3f9b7d8df4d
PRIN-594463-2016 | PR-380982-2016 | 10/7/2016 10:01:02 AM | ASSESS: PR IN: Acceptance | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | Smoke detector in machine room does not annunciate in lift shack. Could result in an alarm being missed by operator. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Great_Bear_smoke_detector.png | file://x:/photopub/docs/0000000498/519d8b21-c07f-4e06-8d42-0d6356526c57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26e00034_7386_4060_bebd_aaeffa36ff15
ELOP-697293-2016 | EL-288302-2015 | 11/22/2016 3:59:13 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Extension cords are not approved to be run through walls of a structure and must be checked periodically to ensure there are not damaged prior to use. This is required to ensure that cords do not get damaged and that damaged cords are removed from service. This wood processing facility had an extension cord that was plugged into a 15A 120V receptacle, run over a bathroom structure within the building, and through a ventilation grate to the exterior of the building. The cord was damaged on the interior of the building, did not have a cord end on the exterior of the building, and had exposed and energized conductors approximately 2.5M from the ground. This was a potential shock and fire hazard if persons or objects contacted the energized conductors or if they shorted causing a fault and a resulting electrical arc. | 4 | Conductors, Misuse of flexible cords. | Mill_facility.png | file://x:/photopub/docs/0000000519/6e3884db-ebbf-47cb-9357-2f238385988e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3bea1f1_dbc9_4aee_96c0_efc4bafc063d
GAIN-690249-2016 | GA-440195-2016 | 11/9/2016 3:45:48 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | Unapproved venting system | 3 | Unapproved venting material | Exhaust_pipe.png | file://x:/photopub/docs/0000000515/4b6b32cc-013c-484a-9eb7-321d9f1ccfa8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__80ddce98_f7a8_40b9_80ae_521488eeabee
GAUP-708899-2016 | UW-470575-2016 | 11/22/2016 11:42:13 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | The as found condition was single wall vent pipe installed on a hot water tank within the minimum 6 inch clearance to combustible plastic plumbing pipe. The as found hazard is heat radiating from the single wall vent pipe can damage or potentially cause combustible materials to ignite leading to a fire. | 3 | Non compliant Type C Vent clearance | Pex_clearance_c_Vent.png | file://x:/photopub/docs/0000000519/bacb030f-f62c-4d6c-bc02-4ac7bd57ce14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01822eae_8758_4d37_93d6_a876953c4f6f
GAHE-695106-2016 | HE-461519-2016 | 11/1/2016 10:19:44 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | Outdoor black iron natural gas line unsecured to building and resting on a metal bucket. | 3 | Code prohibited practices or materials | Unsecured_gas_line.png | file://x:/photopub/docs/0000000509/0e7bb74f-6606-421a-a637-e5648ecce4a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__134b213c_d8e9_4d39_a8e9_85ceb57df193
ELHE-695606-2016 | HE-461887-2016 | 11/1/2016 3:58:09 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Old house being used as boarding house. Dangerous use of cords and power bars by tenants. Lack of upkeep/updating by owner. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Ext_cord_wiring.png | file://x:/photopub/docs/0000000509/039401be-9058-4463-8ee8-dcee536ab495.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7425885e_3749_46d1_9c34_d263081daa55
ELHE-695606-2016 | HE-461887-2016 | 11/1/2016 3:58:09 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Old house being used as boarding house. Dangerous use of cords and power bars by tenants. Lack of upkeep/updating by owner. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Broken_switch.png | file://x:/photopub/docs/0000000509/3429eca3-708f-4e5e-ba10-9dc3c0f2f4d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7425885e_3749_46d1_9c34_d263081daa55
ELHE-695606-2016 | HE-461887-2016 | 11/1/2016 3:58:09 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Old house being used as boarding house. Dangerous use of cords and power bars by tenants. Lack of upkeep/updating by owner. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Luminaire.png | file://x:/photopub/docs/0000000509/516a1f2a-331c-4ec8-835f-83c9e0848593.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7425885e_3749_46d1_9c34_d263081daa55
ELHE-695606-2016 | HE-461887-2016 | 11/1/2016 3:58:09 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Old house being used as boarding house. Dangerous use of cords and power bars by tenants. Lack of upkeep/updating by owner. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Shower_switch.png | file://x:/photopub/docs/0000000509/8039d002-5d3c-4027-8c34-d6ec36a3eaa5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7425885e_3749_46d1_9c34_d263081daa55
ELHE-695606-2016 | HE-461887-2016 | 11/1/2016 3:58:09 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Old house being used as boarding house. Dangerous use of cords and power bars by tenants. Lack of upkeep/updating by owner. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Powerbars.png | file://x:/photopub/docs/0000000509/c2215201-0a14-4a7d-b599-44ebee692df6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7425885e_3749_46d1_9c34_d263081daa55
ELOP-694542-2016 | 5183248 | 11/4/2016 12:40:34 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dust_accumulat__dust_accumulation_around_the_motor_control_centre.png | file://x:/photopub/docs/0000000511/ab35ea1c-e797-4a9e-a456-57986fa7a01c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1137b5ad_5898_4ba1_b0ed_214adeb81e48
ELOP-694542-2016 | 5183248 | 11/4/2016 12:40:34 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | As_found_a__as_found_accumulation_of_dust_behind_planer_machine.png | file://x:/photopub/docs/0000000511/852a02e8-0fdb-4a03-89b2-23218c41f52f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1137b5ad_5898_4ba1_b0ed_214adeb81e48
ELOP-694542-2016 | 5183248 | 11/4/2016 12:40:34 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dust_accumulat___dust_accumulation_in_the_finishing_process_mail.png | file://x:/photopub/docs/0000000511/3978d13b-d1b2-4737-b49f-d9533ca25d4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1137b5ad_5898_4ba1_b0ed_214adeb81e48
ELOP-694542-2016 | 5183248 | 11/4/2016 12:40:34 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Al_s_found__al_s_found_accumulation_of_dust_on_electrical_equipment.png | file://x:/photopub/docs/0000000511/ca4963cf-12e5-4ae1-bb4a-8ed5638d052e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1137b5ad_5898_4ba1_b0ed_214adeb81e48
ELOP-694542-2016 | 5183248 | 11/4/2016 12:40:34 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | As_found__as_found_accumulation_of_dust.png | file://x:/photopub/docs/0000000511/0d195c91-c591-4e3c-81c9-625b0722c074.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1137b5ad_5898_4ba1_b0ed_214adeb81e48
ELOP-694542-2016 | 5183248 | 11/4/2016 12:40:34 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | As_found__as_found_accumulation_of_dust_on_top_of_electrical_equipment.png | file://x:/photopub/docs/0000000511/368424c5-9d84-43f9-98c3-9a0f8176f895.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1137b5ad_5898_4ba1_b0ed_214adeb81e48
ELOP-694542-2016 | 5183248 | 11/4/2016 12:40:34 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | As_found__dust_accumulat__dust_accumulation_from_material_prior_to_being_processed.png | file://x:/photopub/docs/0000000511/acebf229-1f15-4606-979a-f9992f65e97e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1137b5ad_5898_4ba1_b0ed_214adeb81e48
ELOP-694542-2016 | 5183248 | 11/4/2016 12:40:34 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | As_found__as_found_accumulation_of_dust_for_hopper_motor.png | file://x:/photopub/docs/0000000511/57f110ca-416f-4905-86a1-b9e7f755593d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1137b5ad_5898_4ba1_b0ed_214adeb81e48
ELOP-694542-2016 | 5183248 | 11/4/2016 12:40:34 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dust_clean_up__dust_clean_up_records.png | file://x:/photopub/docs/0000000511/50b5a5a5-69bc-4b5f-8c26-e9771b353831.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1137b5ad_5898_4ba1_b0ed_214adeb81e48
ELOP-694542-2016 | 5183248 | 11/4/2016 12:40:34 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dust_accumulati___dust_accumulation_under_product_receiving_line.png | file://x:/photopub/docs/0000000511/cabc5f38-83c7-4e73-b7a3-4abc8ec8a1cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1137b5ad_5898_4ba1_b0ed_214adeb81e48
ELOP-694542-2016 | 5183248 | 11/4/2016 12:40:34 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Dust_mitigatio__dust_mitigation_plan.png | file://x:/photopub/docs/0000000511/5b7b656d-7b48-4165-8c4b-8df0b65cacae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1137b5ad_5898_4ba1_b0ed_214adeb81e48
ELIN-699133-2016 | UW-463584-2016 | 11/3/2016 12:01:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | There is damage to the cable covering. This can lead to a shock hazard situation. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Cable_damage.png | file://x:/photopub/docs/0000000512/146e2141-b9d5-4f9a-b4b0-cb0e4708a675.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92a4cedf_f676_4630_a1c6_626a387697cd
ELIN-696946-2016 | EL-462833-2016 | 11/7/2016 1:56:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Service conductors are #4/0 for a 200 amp service. #250 conductor size is required for 200 amp services unless the contractor provides a load calculation to meet the requirements of table 39. This a thermal effect condition. 200Amp, 120/240 Volt. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | _feeder_cable_size_for_200_amp_service_.png | file://x:/photopub/docs/0000000512/962ae346-86da-4207-b15a-053b8c90db14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9299b717_fb2b_4fdb_b3a3_b4717e9aece8
ELIN-697110-2016 | EL-459677-2016 | 11/7/2016 9:41:44 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | No mechanical protection for rigid PVC service conductor conduit and ACWU feeder. Protection plate required to prevent damage from screws, nails or staples from penetrating the service conductor conduits from the outside. 200 Amp. 120/240 Volt. This is an equipment damage condition for the service conductors. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | No_protection_plate_to_protect_service_conductors_.png | file://x:/photopub/docs/0000000512/46e48272-6111-404d-83e8-571a3c87977a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb135639_04e6_4612_ac99_636803898f86
BPOP-701781-2016 | BPV-466287-2016 | 11/22/2016 4:24:06 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | 500 gallon Propane tank is installed within 15" of storage shed. This does not meet minimal requirements for a safe installation. If a gas leak developed and ignition took place the shed would burn preventing access to shut off Propane valve. Resulting fire would cause severe damage to nearby properties in this residential area. | 3 | Clearance to combustible not met | 500_Gallon_propane_tank_against_wall.png | file://x:/photopub/docs/0000000519/15beac29-c7cb-459e-99d4-c44cd6e6ee47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6de194a5_afec_41e2_a1fe_87fdefa18e08
BPOP-701781-2016 | BPV-466287-2016 | 11/22/2016 4:24:06 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | 500 gallon Propane tank is installed within 15" of storage shed. This does not meet minimal requirements for a safe installation. If a gas leak developed and ignition took place the shed would burn preventing access to shut off Propane valve. Resulting fire would cause severe damage to nearby properties in this residential area. | 3 | Clearance to combustible not met | Non_compliant_tank_instalation.png | file://x:/photopub/docs/0000000519/935ed66e-200f-4523-b437-91c7e2098d49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6de194a5_afec_41e2_a1fe_87fdefa18e08
ELHE-705419-2016 | HE-468677-2016 | 11/17/2016 10:13:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | 240 volt range cable relocated and cable not protected or terminated in box and poses shock, fire hazard. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Manager_whom_performed_work.png | file://x:/photopub/docs/0000000517/16afceb5-8f4a-4361-b6bb-bed15f0275c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ffcf19cf_eda7_4c6b_ba19_8ee96738f120
ELHE-705419-2016 | HE-468677-2016 | 11/17/2016 10:13:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | 240 volt range cable relocated and cable not protected or terminated in box and poses shock, fire hazard. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Bath_light.png | file://x:/photopub/docs/0000000517/deba203f-9aa6-412a-bb2b-01b3670137af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ffcf19cf_eda7_4c6b_ba19_8ee96738f120
ELHE-705419-2016 | HE-468677-2016 | 11/17/2016 10:13:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | 240 volt range cable relocated and cable not protected or terminated in box and poses shock, fire hazard. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Receptacle_work.png | file://x:/photopub/docs/0000000517/5d4c9677-c96e-49aa-ba46-b853efb8117f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ffcf19cf_eda7_4c6b_ba19_8ee96738f120
ELHE-705419-2016 | HE-468677-2016 | 11/17/2016 10:13:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | 240 volt range cable relocated and cable not protected or terminated in box and poses shock, fire hazard. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Range.png | file://x:/photopub/docs/0000000517/553b228a-1943-40a5-a2d7-e4e76ad7b743.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ffcf19cf_eda7_4c6b_ba19_8ee96738f120
ELHE-705419-2016 | HE-468677-2016 | 11/17/2016 10:13:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | 240 volt range cable relocated and cable not protected or terminated in box and poses shock, fire hazard. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Directory.png | file://x:/photopub/docs/0000000517/fb71e6bf-489c-4d8f-970b-abd0cf9df455.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ffcf19cf_eda7_4c6b_ba19_8ee96738f120
BPVOP-686402-2016 | 5074031 | 10/18/2016 1:14:39 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment it is determined that machine mounted horizontal air receiver (2.1m long and 0.76m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve.png | file://x:/photopub/docs/0000000502/132c117f-d45e-4f71-a022-c5d7a5ce16a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b793053_d471_49a1_a91c_db5563234ff7
GAHE-670429-2016 | HE-442268-2016 | 10/18/2016 12:23:27 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Hanger_not_functioning_properly.png | file://x:/photopub/docs/0000000502/c53e1182-6b47-4ce1-aa8b-309eae8c258a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2f44fc7_7e31_4056_9214_decd05bb83f2
GAHE-670429-2016 | HE-442268-2016 | 10/18/2016 12:23:27 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Piping.png | file://x:/photopub/docs/0000000502/67ba4d15-984c-4390-95d0-ff29551ac7fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2f44fc7_7e31_4056_9214_decd05bb83f2
GAHE-670429-2016 | HE-442268-2016 | 10/18/2016 12:23:27 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Piping_in_meter_cage.png | file://x:/photopub/docs/0000000502/cf8f4535-1cb3-4f3d-b8d5-1fcaaf8daf5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2f44fc7_7e31_4056_9214_decd05bb83f2
ELOP-694542-2016 | 5183248 | 11/4/2016 12:40:34 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Continual_improveme__continual_improvement_documentation.png | file://x:/photopub/docs/0000000511/ca958b9b-91bb-4b4d-9a68-5858b1a3b41f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1137b5ad_5898_4ba1_b0ed_214adeb81e48
ELOP-694542-2016 | 5183248 | 11/4/2016 12:40:34 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | As_found__as_found_condition_under_conveyor_system.png | file://x:/photopub/docs/0000000511/042fdb9f-e6c7-418e-82f9-54140c4aeaf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1137b5ad_5898_4ba1_b0ed_214adeb81e48
ELOP-694542-2016 | 5183248 | 11/4/2016 12:40:34 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Documentation_of__documentation_of_dust_training_I_ve_employees.png | file://x:/photopub/docs/0000000511/11cc8f92-0339-4a47-a0d2-13e7d9c93a8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1137b5ad_5898_4ba1_b0ed_214adeb81e48
ELIN-702975-2016 | EL-446472-2016 | 11/23/2016 3:15:31 PM | ASSESS: EL: Final | png | #asFound | EL208 | All Classes, All Zones Area is classified: seals are not located or installed where required. | 4 | 3 | Seal missing where wiring enters hazardous location. Should hazardous vapours enter the conduit system they may migrate into the none hazardous breaker panel where a spark could ignite the flammable vapour causing explosion or fire. | 4 | All Classes, All Zones Area is classified: seals are not located or installed where required. | Picture_1.png | file://x:/photopub/docs/0000000520/e535eb67-84e4-438c-8bc2-ee78aa790428.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12718dbc_1ccd_4a9e_b12d_b858d439b09e
GAIN-705750-2016 | GA-353749-2016 | 11/18/2016 3:54:32 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | Found industrial boiler installed with no combustion air supply to room. If boiler was left to run without an exterior door open, it would result in incomplete combustion and the production of excessive carbon monoxide. This would pose a serious threat of CO poisoning to anyone who entered the room or was working in the immediate vicinity. | 4 | Combustion air supply missing | No_combustion_or_ventilation_air.png | file://x:/photopub/docs/0000000518/24879211-8126-4b5d-9a31-69536a027aa5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4515d22_d9de_4f02_9f17_2da23838a607
ELIN-698741-2016 | EL-448417-2016 | 11/8/2016 10:14:16 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | NMSC cable has no connector on it where the cable enters the panel enclosure. 120 Volt. This is a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. | No_connector_on_NMD-90_cable_entering_panel_enclosure.png | file://x:/photopub/docs/0000000513/4f58877b-789d-4142-b908-1f60df0b3c45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__362744fe_2aed_4dc7_8899_7aee21f81a50
ELIN-708024-2016 | EL-307988-2015 | 11/22/2016 10:19:45 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | No arc fault circuit interrupt protection provided for branch circuit supplying receptacles in bedrooms, increasing the risk of an electrical fire resulting should an electrical arc occur. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Non-TR_rated_receptacle.png | file://x:/photopub/docs/0000000519/da3e3264-07d9-4552-9fd6-5ab492286bfc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e93c59ca_7958_4fcb_a541_528d6d66f0dc
PROP-599962-2016 | 2224082 | 11/22/2016 7:49:08 PM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Machine room guards are not adequate, moving parts could be exposed to contact. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Machine_guarding.png | file://x:/photopub/docs/0000000520/ceb6e744-6dc7-4471-874e-6ae59fe69168.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7C78BF7D_60CB_4B19_87A3_28DA2FE475E7
PRIN-700287-2016 | PR-430675-2016 | 11/22/2016 8:40:45 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | Diesel drive exhausts through building to roofline, hot exhaust pie could cause a fire. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Exhaust_through_attic.png | file://x:/photopub/docs/0000000520/8c9ca647-0eb9-4a1f-a6f6-a7c8eb3030a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06891f2c_a4c7_409c_aaad_25125dbf95a4
ELOP-697293-2016 | EL-288302-2015 | 11/22/2016 3:59:13 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Extension cords are not approved to be run through walls of a structure and must be checked periodically to ensure there are not damaged prior to use. This is required to ensure that cords do not get damaged and that damaged cords are removed from service. This wood processing facility had an extension cord that was plugged into a 15A 120V receptacle, run over a bathroom structure within the building, and through a ventilation grate to the exterior of the building. The cord was damaged on the interior of the building, did not have a cord end on the exterior of the building, and had exposed and energized conductors approximately 2.5M from the ground. This was a potential shock and fire hazard if persons or objects contacted the energized conductors or if they shorted causing a fault and a resulting electrical arc. | 4 | Conductors, Misuse of flexible cords. | Cord_plugged_into_receptacle_by_the_washrooms.png | file://x:/photopub/docs/0000000519/d7a7992a-fac0-40e0-8f67-5e60ff017fee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3bea1f1_dbc9_4aee_96c0_efc4bafc063d
ELOP-697293-2016 | EL-288302-2015 | 11/22/2016 3:59:13 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Extension cords are not approved to be run through walls of a structure and must be checked periodically to ensure there are not damaged prior to use. This is required to ensure that cords do not get damaged and that damaged cords are removed from service. This wood processing facility had an extension cord that was plugged into a 15A 120V receptacle, run over a bathroom structure within the building, and through a ventilation grate to the exterior of the building. The cord was damaged on the interior of the building, did not have a cord end on the exterior of the building, and had exposed and energized conductors approximately 2.5M from the ground. This was a potential shock and fire hazard if persons or objects contacted the energized conductors or if they shorted causing a fault and a resulting electrical arc. | 4 | Conductors, Misuse of flexible cords. | Cord_damaged_were_ti_runs_over_bethrooms_to_exterior_of_building.png | file://x:/photopub/docs/0000000519/2bcdf38c-e0c9-492e-ab05-6ae3a8da095b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3bea1f1_dbc9_4aee_96c0_efc4bafc063d
ELIN-664937-2016 | EL-437981-2016 | 9/26/2016 3:54:47 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found energized and exposed 120 volt conductors in outlet box while outlet box is missing covers. When electrical equipment or conductors are energized and exposed due to no covers installed on boxes, the electrical equipment is a possible electrical fire or shock hazard people or property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | cover_missing_on_energized_exposed_conductors.png | file://x:/photopub/docs/0000000491/5b79e8fb-9ffb-4d32-a39a-8b558d1e26ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__288e2f40_c86b_4842_bcf6_81dab849af5a
ELIN-664937-2016 | EL-437981-2016 | 9/26/2016 3:54:47 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found energized and exposed 120 volt conductors in outlet box while outlet box is missing covers. When electrical equipment or conductors are energized and exposed due to no covers installed on boxes, the electrical equipment is a possible electrical fire or shock hazard people or property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | All_branch_circuits_connected_to_power_sully_system_while_not_safe_to_connect_load_ends.png | file://x:/photopub/docs/0000000491/5458cfc5-c68d-4c86-9792-0f7b51abde82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__288e2f40_c86b_4842_bcf6_81dab849af5a
ELIN-664937-2016 | EL-437981-2016 | 9/26/2016 3:54:47 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found energized and exposed 120 volt conductors in outlet box while outlet box is missing covers. When electrical equipment or conductors are energized and exposed due to no covers installed on boxes, the electrical equipment is a possible electrical fire or shock hazard people or property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | exposed_energized_conductors_in_box_with_cover_missing.png | file://x:/photopub/docs/0000000491/7f3a5696-6955-4cf3-99a7-d1373bb0b294.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__288e2f40_c86b_4842_bcf6_81dab849af5a
BPVIN-670520-2016 | UW-442327-2016 | 9/27/2016 10:57:39 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP120 | 3.0.1 Safeties will not function - Safety devices not functional, by-passed or missing with no back up corresponding safety/ operating control device | 5 | 5 | During the inspection of an Air Receiver part of a system was found a plug instead of the PRD. Also, in the system was found a PRD with a set point at 200 psig, while the vessel MAWP is 150 psig. | 5 | 3.0.1 Safeties will not function - Safety devices not functional, by-passed or missing with no back up corresponding safety/ operating control device | Plug_instead_of_PRD.png | file://x:/photopub/docs/0000000491/78bbe433-199c-48c8-ad95-d3549575c792.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__edf6c2d9_f04b_44a4_b2c5_a3086afee18e
ELIN-692613-2016 | EL-441894-2016 | 10/28/2016 9:37:27 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Three conductor number 10 armoured cable was installed underground. this type of cable is not approved for under ground use, and the likelihood of shock from moisture penetrating the cable insulation is likely. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Armoured_cable__armoured_cable_installed_underground.png | file://x:/photopub/docs/0000000507/75ad5146-5981-4e83-80f6-c2d4668df537.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8d610b8_2d4f_4be9_a39f_80e6ab39b0a3
ELIN-692613-2016 | EL-441894-2016 | 10/28/2016 9:37:27 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Three conductor number 10 armoured cable was installed underground. this type of cable is not approved for under ground use, and the likelihood of shock from moisture penetrating the cable insulation is likely. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Photo_to__Photo_two_armoured_cable_installed_underground.png | file://x:/photopub/docs/0000000507/dbfffe62-085f-44c3-b930-ddf0666c136b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8d610b8_2d4f_4be9_a39f_80e6ab39b0a3
BPVOP-729960-2016 | UW-483142-2016 | 10/21/2016 | ASSESS: BPV OP: Compliance REF/PV | png | #asFound | BP149 | 4.1.1 Incorrect readings/alarms - Refrigerant vapour detector out of calibration | 3 | 3 | Air flow meter instead of code required refrigerant leak detector | 3 | 4.1.1 Incorrect readings/alarms - Refrigerant vapour detector out of calibration | Air_Flow_meter_instead_of_leak_detector.png | file://x:/photopub/docs/0000000536/d91815b5-50b7-4036-a402-64e5b280ce17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb4b427c_2740_480b_83d9_4f00281a176f
GAIN-747965-2017 | GA-493700-2017 | 2/3/2017 8:48:37 AM | ASSESS: GA: Rough-In | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Hazard_.png Intake venting separated in same space as fireplace. Insufficiency combustion air would be available to the appliance. Rich burning condition resulting in the production of carbon monoxide | 3 | Appliance not installed according to installation instructions | Hazard_.png | file://x:/photopub/docs/0000000553/237dc0d3-41a1-4ffb-b6d8-89c1b9f7a040.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aed39ab1_2683_4da2_9a9c_39af427a45bf
GAUP-743774-2017 | UW-493658-2017 | 1/23/2017 12:12:45 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound Uncapped gas lines | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Uncapped_gas_line.png Found an uncapped gas line on an active gas system, this has potential for a uncontrolled release of gas which could cause fire or explosion | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Uncapped_gas_line.png | file://x:/photopub/docs/0000000547/a65dc9b4-4397-4ac4-b035-6aa80ba12d59.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17924ac4_b86d_45e0_87e9_5afeddf07b15
BPVOP-721902-2016 | 2273644 | 12/12/2016 8:59:53 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP047 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | 5 | 5 | During the external inspection of a Domestic Hot Water Storage Tank with MAWP of 150 psig, a 3x3 area of the top head was found corroded and leaking. | 5 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | Fully_corroded_and_leaking.png | file://x:/photopub/docs/0000000532/841d29f6-6acf-4f4f-b5eb-b01fcc42dce9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e3e63148_86c8_4121_923c_a2870bf55bf1
BPVOP-721890-2016 | 2273645 | 12/12/2016 4:01:15 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP214 | 5.1.1 Work done: unqualified ind - Unsafe or incorrect repair done by unlicensed contractor or unqualified individual. | 4 | 4 | During the inspection of a Domestic Hot Water Tank with MAWP of 150 psig, an unauthorised welded repair that is leaking was found. No welding permitted is printed on the tank. | 4 | 5.1.1 Work done: unqualified ind - Unsafe or incorrect repair done by unlicensed contractor or unqualified individual. | Unsafe_and_not_allowed_repair.png | file://x:/photopub/docs/0000000532/755a8124-3384-4cc2-8f7b-690749820d88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd80a7c4_c6b2_4c82_80e5_0a30c7bd07b5
EDIN-716133-2016 | ED-410480-2016 | 12/1/2016 10:41:43 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | The hoistway that the lift is installed in is significantly larger than it needs to be as it was originally designed for a larger elevator. This change in design left a large space beside the lift that someone working on the roof of the lift could fall down. With the lift at the top landing someone could fall 18' to the concrete floor below. | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Top_of_car_after_handrail_was_added.png | file://x:/photopub/docs/0000000524/8468ceda-0bf4-440d-9f83-be6806537254.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11e917e0_f9e3_4603_9da6_019fe5960d93
GAIN-717872-2016 | GA-476406-2016 | 1/4/2017 10:53:12 AM | ASSESS: GA: Rough-In | png | #asFound | GA070 | Undersized hose or appliance connector | 3 | 3 | 1) Gas piping, tubing and hoses must be sized to meet the requirements of the total btu load of the appliance being supplied 2) All hoses are to long and undersized for the appliance being supplied. 3) Undersized gas piping or hose can effect the appliance burner operation, possibly result in hazardous appliance operation that may produce Carbon Monoxide. | 3 | Undersized hose or appliance connector | Undersized_gas_hose_to_heaters_.png | file://x:/photopub/docs/0000000538/b6aef0a5-ec3f-40da-a1a1-4d7a4314c182.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69d98c93_d7ab_4c7d_b152_688b25210846
GAIN-717872-2016 | GA-476406-2016 | 1/4/2017 10:53:12 AM | ASSESS: GA: Rough-In | png | #asFound | GA070 | Undersized hose or appliance connector | 3 | 3 | 1) Gas piping, tubing and hoses must be sized to meet the requirements of the total btu load of the appliance being supplied 2) All hoses are to long and undersized for the appliance being supplied. 3) Undersized gas piping or hose can effect the appliance burner operation, possibly result in hazardous appliance operation that may produce Carbon Monoxide. | 3 | Undersized hose or appliance connector | Unprotected_regulator_relief_openings.png | file://x:/photopub/docs/0000000538/c2608ce5-61d6-42b9-b6c7-94144b54bf05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69d98c93_d7ab_4c7d_b152_688b25210846
GAIN-717872-2016 | GA-476406-2016 | 1/4/2017 10:53:12 AM | ASSESS: GA: Rough-In | png | #asFound | GA070 | Undersized hose or appliance connector | 3 | 3 | 1) Gas piping, tubing and hoses must be sized to meet the requirements of the total btu load of the appliance being supplied 2) All hoses are to long and undersized for the appliance being supplied. 3) Undersized gas piping or hose can effect the appliance burner operation, possibly result in hazardous appliance operation that may produce Carbon Monoxide. | 3 | Undersized hose or appliance connector | temporary_heaters_no_combustion_air.png | file://x:/photopub/docs/0000000538/7046eae0-7090-4fe1-aeeb-0ccf76c2a656.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69d98c93_d7ab_4c7d_b152_688b25210846
ELHE-729192-2016 | HE-484531-2016 | 12/23/2016 5:49:46 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | This is an example of work that was done by unqualified workers that had no supervision as declared by Robert Taylor FSR. Hazard was LB in wall with no access. The non compliance is being corrected from another C of I. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Installation_done_by_unqualified_workers.png | file://x:/photopub/docs/0000000537/12e3731f-c6a5-4c79-a91d-98780fe91a0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7926b58_ff09_4b1c_b94f_99d84a5ac320
PROP-741434-2017 | PR-492475-2017 | 1/19/2017 2:02:50 AM | ASSESS: PR OP: Annual | png | #asFound Skirting missing near end | PR025 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Section_of_skirting_missing.png Passenger conveyors are to be provided with skirting along the full length of the conveyor. It was observed that a short section of skirting was missing (approximately.5m length). The cavern below the edge of the conveyor results in an entrapment hazard. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Section_of_skirting_missing.png | file://x:/photopub/docs/0000000549/ae03dba7-5f22-4c57-a455-214b903eab36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__80b9c9b0_d0f1_47bc_b369_817e18c2d041
ELIN-722759-2016 | EL-402872-2016 | 12/14/2016 7:56:13 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 15 amp 120 volt receptacles branch circuits have not been provided with AFCI protection, this could pose a fire risk and harm to persons. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Panel_schedule.png | file://x:/photopub/docs/0000000532/ff999a71-71b6-429b-a014-b71314b8ac5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12108494_417e_4c9e_a4ba_bc8743f383cf
BPVIN-663699-2016 | BPV-401255-2016 | 1/17/2017 9:28:11 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP103 | 3.0.1 Safeties will not function - No labels/ identification or electrical Schematic diagram | 2 | 2 | #No_identification_.png | 2 | 3.0.1 Safeties will not function - No labels/ identification or electrical Schematic diagram | No_identification_.png | file://x:/photopub/docs/0000000544/d1e88543-0f09-40aa-8f86-0e46ed9a0b50.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8e8e03a_62c5_48f7_a531_e02799666373
ELIN-746717-2017 | EL-466698-2016 | 1/30/2017 1:44:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #DB2_.png DB2 raceway is exposed above grade level providing inadequate mechanical protection for conductors | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | DB2_.png | file://x:/photopub/docs/0000000550/fa3a869f-3c33-4ff1-8ab9-90edfc93ca93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1876dc31_1856_4382_bb64_325b69636b89
GAWP-748908-2017 | GA-439586-2016 | 1/31/2017 2:29:12 PM | ASSESS: GA Work In Progress | png | #asFound Pressure regulator set pressure 2 psi. | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #Meter_pressure_regulator.png Furnace installed without an appliance regulator on a 2psi supply line. The appliance will be over fired leading to excessive heat and premature failure of the heat exchanger. | 4 | Appliance regulator not installed, incorrect delivery pressure | Meter_pressure_regulator.png | file://x:/photopub/docs/0000000550/0a9e6c49-09da-4a84-9c69-a5b8f8b413fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d12a9660_6986_4310_8ebb_ed052c184184
GAWP-748904-2017 | GA-439583-2016 | 1/31/2017 2:28:54 PM | ASSESS: GA Work In Progress | png | #asFound Gas supply pressure 2 psi | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #Gas_meter_regulator.png Furnace installed without an appliance regulator on a 2psi supply line. The appliance will be over fired leading to excessive heat and premature failure of the heat exchanger. | 4 | Appliance regulator not installed, incorrect delivery pressure | Gas_meter_regulator.png | file://x:/photopub/docs/0000000550/6c550d20-6949-476f-a64a-d8ee2ddd9177.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cddc711e_c2b0_4f7e_be6b_65f8c7151660
GAIN-714743-2016 | GA-440135-2016 | 2/11/2017 12:32:26 PM | ASSESS: GA: Final | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | #Grain_dryer1.png,Grain_dryer2.png,Grain_dryer3.png Grain dryer burner and gas valve component installed 15 feet and 25 feet off of the ground, no safe accessibility to burner and components for initial fire up and servicing. | 2 | Appliance installed in a proposed hazardous location | Grain_dryer2.png | file://x:/photopub/docs/0000000556/714c3f0f-5d26-4469-909b-5093d756fe4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1929e4fa_d9c5_48ff_8af4_4168592f86c8
GAHE-755441-2017 | HE-500406-2017 | 2/10/2017 3:40:32 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Base.png Single wall base tee 1" away from wood and back side of drywall in mechanical room. Minimum 6" clearance required to prevent materials heating up and causing a fire. | 3 | Non compliant Type C Vent clearance | Base.png | file://x:/photopub/docs/0000000556/a118637e-7cd1-4eb9-a383-e10b33d65f08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__914bfc42_b0d3_47a7_874c_2656fddcd0ba
GAIN-714743-2016 | GA-440135-2016 | 2/11/2017 12:32:26 PM | ASSESS: GA: Final | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | #Grain_dryer1.png,Grain_dryer2.png,Grain_dryer3.png Grain dryer burner and gas valve component installed 15 feet and 25 feet off of the ground, no safe accessibility to burner and components for initial fire up and servicing. | 2 | Appliance installed in a proposed hazardous location | Grain_dryer3.png | file://x:/photopub/docs/0000000556/bac1ed56-2827-4472-a2b9-81fc50b81e56.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1929e4fa_d9c5_48ff_8af4_4168592f86c8
GAUP-755504-2017 | UW-500190-2017 | 2/10/2017 4:43:15 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Red_willow1.png,Red_willow2.png Found gas piping connected from gas meter to furnace with no cap installed on dirt pocket at furnace and no contractor on site. In the event someone turns on the gas meter the crawl space could be filled with uncontrollable gas and causing a fire or explosion. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Red_willow2.png | file://x:/photopub/docs/0000000556/32a6c151-47b9-4a78-a1e5-7da83a3de332.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__35738ad5_bc90_4835_8fea_4b03be0d3eca
GAUP-755504-2017 | UW-500190-2017 | 2/10/2017 4:43:15 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Red_willow1.png,Red_willow2.png Found gas piping connected from gas meter to furnace with no cap installed on dirt pocket at furnace and no contractor on site. In the event someone turns on the gas meter the crawl space could be filled with uncontrollable gas and causing a fire or explosion. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Red_willow1.png | file://x:/photopub/docs/0000000556/bc01523e-3a56-4aff-8554-6419bc38bc40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__35738ad5_bc90_4835_8fea_4b03be0d3eca
GAIN-714743-2016 | GA-440135-2016 | 2/11/2017 12:32:26 PM | ASSESS: GA: Final | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | #Grain_dryer1.png,Grain_dryer2.png,Grain_dryer3.png Grain dryer burner and gas valve component installed 15 feet and 25 feet off of the ground, no safe accessibility to burner and components for initial fire up and servicing. | 2 | Appliance installed in a proposed hazardous location | Grain_dryer1.png | file://x:/photopub/docs/0000000556/0689cba2-7357-4a8b-9be8-f30d8d03f654.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1929e4fa_d9c5_48ff_8af4_4168592f86c8
GAWP-716243-2016 | GA-474402-2016 | 12/2/2016 11:00:06 AM | ASSESS: GA Work In Progress | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Copper gas line connection at back of stove had a broken flare end so the open gas line was only inserted into the flare nut connection. This would allow gas to escape if the shut off valve was turned to the on position. Escaping gas could cause a fire or explosion. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Connection_at_back_of_stove.png | file://x:/photopub/docs/0000000525/1c88d964-f0da-4a51-8652-5463d7a1c76d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e12d35a7_5ca8_441c_af9d_cfddffd2484c
GAWP-716243-2016 | GA-474402-2016 | 12/2/2016 11:00:06 AM | ASSESS: GA Work In Progress | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Copper gas line connection at back of stove had a broken flare end so the open gas line was only inserted into the flare nut connection. This would allow gas to escape if the shut off valve was turned to the on position. Escaping gas could cause a fire or explosion. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Broken_copper_flare.png | file://x:/photopub/docs/0000000525/e42a402e-a9c9-4d1e-a1a5-85e558378a54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e12d35a7_5ca8_441c_af9d_cfddffd2484c
ELIN-712628-2016 | EL-465608-2016 | 12/5/2016 8:41:23 AM | ASSESS: EL: Service Connection | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | An existing 100 amp 120/240 volt overhead service has had the Main Panel upgraded to a 200 amp rated panel board with a 200 amp main breaker. This poses a potential shock hazard and chance of equipment and conductor damage as the main service conductors can be overloaded as the Main Breaker size is larger than the Service rating. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 200A_Main_Panel.png | file://x:/photopub/docs/0000000526/11275c41-2090-443e-b227-609a3ea10279.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13c77c86_d71b_4c1f_b454_c32816bd3a40
ELIN-709252-2016 | EL-417402-2016 | 12/5/2016 10:38:57 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | A 15 amp receptacle has been added to power a cord connected garburator but the receptacle has not been AFCI protected, this poses a hazard to equipment and persons. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Panel_Schedule.png | file://x:/photopub/docs/0000000526/fd583ead-6c59-4548-a1e8-c2d15b0cac7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd823f52_e8c0_4c05_9179_ccc30de92586
ELOP-756994-2017 | 1556 | 2/15/2017 11:36:19 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound Tandem (retrofit) circuit breakers in 12 circuit panel. | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | #Panel_B_interior.png Electrical operating permit assessment on elementary school. A circuit breaker panel in the school has had more circuit breakers added to it than the panel is labelled as being approved for. Danger of thermal damage and fire as the smaller retrofit type circuit breakers may not contain thermal energy due to the panel having more circuits than it is approved for. | 3 | Protection and control Loading of distribution equipment exceeded | Panel_B_interior.png | file://x:/photopub/docs/0000000557/839a0a74-72dd-4446-a750-021f8bd31b44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__023d64f4_671b_46d9_8e85_b85802a634cb
BPVIN-756631-2017 | BPV-500940-2017 | 1/23/2017 2:24:05 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound Cracked weld on structural attachment | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PSV_not_accessible1.png,PSV_not_accessible2.png All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacment of pressure relief valves of these three pressure reservoirs. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PSV_not_accessible2.png | file://x:/photopub/docs/0000000557/1825174b-e082-48a9-b008-ab7a4c3e63e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12c83329_cb33_4679_b7c3_32ee7d9aed61
BPVIN-756631-2017 | BPV-500940-2017 | 1/23/2017 2:24:05 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound PSV are so oriented that I was unable to see nameplate even after climbing to top of this vessel via caged ladder. | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PSV_not_accessible1.png,PSV_not_accessible2.png All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacment of pressure relief valves of these three pressure reservoirs. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PSV_not_accessible1.png | file://x:/photopub/docs/0000000557/ba3079f7-cf04-4e53-bd1e-f6a0b8106d2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12c83329_cb33_4679_b7c3_32ee7d9aed61
ELOP-656609-2016 | 2039 | 12/6/2016 4:51:07 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL189 | Installation of electrical equipment • Equipment is showing signs of deterioration; and • repairs or maintenance required. | 3 | 3 | Transformer is showing signs of deterioration. The Hazard is that without testing and maintenance of this equipment the result could be a "short circuit event"with undetermined damage to equipment or persons. | 3 | Installation of electrical equipment • Equipment is showing signs of deterioration; and • repairs or maintenance required. | Transformer_with_rusted_skin_.png | file://x:/photopub/docs/0000000526/60023cbc-e437-4789-af6b-283379d0311a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4D2FAC6A_E480_4459_8005_3246F6B5C73E
ELOP-656613-2016 | 2042 | 12/5/2016 2:38:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | 3" knock out in switch is missing this is a entry point for rodents and accidental contact for persons . The hazard could be shock and or damage to equipment. FSR has declared that non-compliance is now corrected | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Hole_in_switch.png | file://x:/photopub/docs/0000000526/f256b339-f7a8-4c62-ae7b-bcd8b0c6d4bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55CF5591_BAF4_4B97_A4A2_69BCAD46DF01
BPVOP-752951-2017 | 2284551 | 2/8/2017 9:50:40 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 | #Horiz.png | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Horiz.png | file://x:/photopub/docs/0000000555/c8742308-4039-4c94-8aa9-8f5aae78db81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2e148cf_1007_4f21_b576_5682ba8ce61b
GAHE-740065-2017 | HE-491677-2017 | 1/17/2017 9:51:56 AM | ASSESS: GA HE: Hazard Elimination | JPG | #asFound Overfired pot burner. | GA148 | Over fired equipment | 4 | 4 | #image1.JPG While assessing a hazard that was reported to me, I found what appears to be a failed regulator which is causing several pieces of commercial cooking equipment to over fire. Should this be left unchecked the equipment could overheat and catch fire. | 4 | Over fired equipment | image1.JPG | file://x:/photopub/docs/0000000544/a124f8f1-f59e-4e7b-a702-37635183b7cd.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd66bfcf_96bb_4c5f_b6ca_0a3a761c5534
ELOP-708241-2016 | 4599 | 12/1/2016 11:04:02 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL298 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Panels (H) and main electrical panel in maintenance shop do not have 1 meter of working space and have obstructed means of egress. This could be hazard if a person needs to access to these panels to turn off a branch circuit feeding a possible electrical hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Desk_built_in_front_of_panel.png | file://x:/photopub/docs/0000000526/8bcabd23-9dba-4072-9947-01612edf4e19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e47970f8_e84f_400d_9d14_8d615826ed85
ELOP-656612-2016 | 2041 | 12/6/2016 6:54:48 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Outer flex has been separated , exposing conductors to further mechanical damage. The hazard is a possible short circuit event with thermal and shock potential. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | De-energized_branch_circuit_.png | file://x:/photopub/docs/0000000526/fd0167a8-eedb-40e1-b30a-e0fd17ba3666.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43207E7B_2F24_47A0_B61C_2379E62C8A60
ELIN-707103-2016 | EL-466582-2016 | 12/1/2016 11:45:45 AM | ASSESS: EL: Final | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 4 | A new 60 amp 240 volt sub service was installed from a used manufactured home to an outbuilding. A power Bar lacking necessary evidence of approval had been permanently connected to the panel board. Additionally the equipment was not designed to properly protect downstream overcurrent devices. Equipment lacking certification may present a hazard for fire or injury to persons. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_power_bar.png | file://x:/photopub/docs/0000000525/868243a1-4e54-414e-9ea6-c1c409288a25.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__497bebb0_3275_468c_bf03_681eca66b75e
ELIN-715537-2016 | EL-423472-2016 | 12/5/2016 12:02:59 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | CAFCI protection not provided. CAFCI are special a breaker that can detect arcing faults. It is code to install these on general use 15 and 20 amp receptacles in dwellings as studies have shown that this is where most fires occur. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | a.png | file://x:/photopub/docs/0000000526/eeb1714a-62e7-449d-a5a6-ae5601ca84bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30410505_758a_4247_a67a_6b23ea79230f
GAHE-747637-2017 | HE-496057-2017 | 1/28/2017 6:54:45 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Tank_lid.png Propane tank had no protective dome lid. This is a hazard as primary valves are exposed to the elements and could be broken or wont have access to shut off valve in the event of an emergency. | 2 | Physical protection of piping and tubing absent. | Tank_lid.png | file://x:/photopub/docs/0000000549/c1c6675f-f504-468e-bad7-ab175856a4bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8790e1c_5ab5_4147_9445_03edcbaeb14a
EDIN-728234-2016 | ED-404272-2016 | 12/21/2016 3:29:03 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | The Hoistway is to protected from entry by unauthorized personnel. During a construction use inspection it was found a large access opening was found leading from the roof to the Hoistway. If an unauthorized person were to enter the Hoistway via the opening he will be exposed to an extreme fall hazard down the Hoistway. It was found the general contractor failed to close up the access opening. This 16 stop traction MRL elevator is located in a newly constructed residential building. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Opening_at_the_top_of_hoistway.png | file://x:/photopub/docs/0000000534/17693567-4421-4a42-b1af-551ce5a52e8e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91be9552_9337_4d23_8be3_9bf4d69ac36e
ELIN-748675-2017 | EL-495664-2017 | 1/31/2017 1:18:58 PM | ASSESS: EL: Service Connection | png | #asFound Consumer service cable is subjected to mechanical damage in the garage. | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #R6.png Thermal and shock hazard fro mechanical damage to service cable. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | R6.png | file://x:/photopub/docs/0000000551/22ce4531-392c-40dd-a2e7-706ad52ec534.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7ee266d_0ea5_44c2_8f8b_c88395461bec
BPVOP-719492-2016 | 2298043 | 12/8/2016 9:50:57 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig , I found a Pressure Relief Device not replaced within the last 3 years and no NDT was done as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | PRD___.png | file://x:/photopub/docs/0000000528/41d2c80c-f11e-45c1-8307-3feac05e0627.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__05ca81a8_cab2_4eaf_9898_606191005e2d
BPVIN-719537-2016 | BPV-477669-2016 | 12/8/2016 10:04:46 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP 200 psig, I found a Pressure Relief Device not replaced within the last 3 years as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | PRd.png | file://x:/photopub/docs/0000000528/af483b4c-6ad8-40e3-b476-dc7a20c0e110.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9dce237_76bc_43a3_9125_a44b6cf30bcb
BPVOP-719488-2016 | 2298045 | 12/8/2016 9:21:00 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver from 1962 with MAWP 200 psig, I found that Pressure Relief Device not replaced within the last 3 years and not NDE was done as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Overall.png | file://x:/photopub/docs/0000000528/f2f244f2-7e6c-48dd-ba3b-b17d38d668ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc8978a8_69d5_4e2c_a232_706a53bc7bf7
BPVOP-719488-2016 | 2298045 | 12/8/2016 9:21:00 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver from 1962 with MAWP 200 psig, I found that Pressure Relief Device not replaced within the last 3 years and not NDE was done as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | PRD_.png | file://x:/photopub/docs/0000000528/614bec67-ebd8-4dc3-a8e3-88958cde8787.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc8978a8_69d5_4e2c_a232_706a53bc7bf7
BPVOP-731859-2017 | 2266227 | 12/16/2016 3:09:37 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP058 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | 3 | 3 | High pressure steam boiler, maximum allowable working pressure 670 psi. A pinhole leak at a weld was discovered by power engineers. If left un repaired the leak may cut and wash the piping, this may lead to further equipment damage, rupture or injury to personnel. | 3 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | 10_roaster.png | file://x:/photopub/docs/0000000538/ad746bea-0fba-4dde-b85e-163df9ec808e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__19f90f05_0372_4b38_9f54_e57bdb07b035
GAHE-744379-2017 | HE-494031-2017 | 1/24/2017 9:20:29 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Range_top.png The as found hazard was a commercial cooktop without proper clearance to combustable materials. This is a hazard because the heat generated by the appliance could cause a fire. | 3 | Clearance to combustible not met | Range_top.png | file://x:/photopub/docs/0000000547/54bf5b97-ac4b-4aa4-b0ab-38e8789892a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fedb70fb_274c_4fac_a4ae_ef6fc964a408
ELIN-737353-2017 | EL-421838-2016 | 1/16/2017 2:54:29 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_without_cover_plates_1.png,Energized_without_cover_plates_2.png Energized devices did not have cover plates installed. This condition could lead to a potential shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_without_cover_plates_2.png | file://x:/photopub/docs/0000000543/1cee5345-da7e-43f6-b9ff-84fba60601a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__50d882cb_f928_4f42_afae_df67be94064f
ELIN-737353-2017 | EL-421838-2016 | 1/16/2017 2:54:29 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_without_cover_plates_1.png,Energized_without_cover_plates_2.png Energized devices did not have cover plates installed. This condition could lead to a potential shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_without_cover_plates_1.png | file://x:/photopub/docs/0000000543/24542631-f7d7-409d-bcf1-b210d578b0c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__50d882cb_f928_4f42_afae_df67be94064f
ELIN-715537-2016 | EL-423472-2016 | 12/5/2016 12:02:59 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | CAFCI protection not provided. CAFCI are special a breaker that can detect arcing faults. It is code to install these on general use 15 and 20 amp receptacles in dwellings as studies have shown that this is where most fires occur. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | B.png | file://x:/photopub/docs/0000000526/66b918ad-c102-4052-932d-0345e3c7a311.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30410505_758a_4247_a67a_6b23ea79230f
ELHE-728028-2016 | HE-483988-2016 | 12/21/2016 1:34:17 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 4 | 4 | Main distribution center is not readily accessible due to a work bench built in front of it. Ready access has not been maintained in case a breaker must be turned off to de-energize a piece of electrical equipment. The panels have not been maintained is a safe manner as is indicated by openings left vacant where breakers have been removed. | 4 | General Location of equipment does not allow for proper access to disconnecting means | Main_distribution_1197_Collins.png | file://x:/photopub/docs/0000000536/bbf037be-2daa-4952-b95b-554f8c0b3c43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c23c927_443b_4ad5_93b3_bd98bbc35aa4
EDIN-734369-2017 | ED-382905-2016 | 1/6/2017 3:21:58 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | Car door eccentrics loose | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Eccentric_loose.png | file://x:/photopub/docs/0000000540/2992dead-adc9-4365-958e-aae116b38ed9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24723119_c3f0_4daa_abbd_e7ae0ca4d204
GAIN-726360-2016 | GA-479786-2016 | 12/28/2016 9:56:48 AM | ASSESS: GA: Final | png | #asFound | GA134 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | 2 | 2 | Incorrect wiring used and passing through the appliance unprotected. Wiring in contact with sharp edge of unit heater. Possibility of electrical arcing or fire if shielding rubbed through. | 2 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | Wiring.png | file://x:/photopub/docs/0000000536/86cf1473-54fb-4798-89cf-c7707359f4b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f8f0427_c1ed_40d3_9268_79e2508e4cd0
ELIN-723362-2016 | EL-474836-2016 | 12/29/2016 8:33:55 AM | ASSESS: EL: Final | png | #asFound | EL052 | Protection and control Circuit breakers connected to branch circuit derived from a 3-wire grounded neutral system are not 2-pole, or the handles of single pole breakers are not interlocked | 3 | 3 | 3 wire branch circuits have 2 energized conductors and are to be protected by a 2 pole breaker which opens both poles de-energizing both conductors at once. If 2 single pole breakers are used without interlock for a 3 wire branch circuit and only one of the conductors is de-energized by opening one of the breakers then there is still one energized conductor in the box at the other end of the cable. This creates a hazard to the person who may be working in the box at the other end, having tested one wire as safe and assuming the other wire is also de-energized as it it would be if protected correctly by a 2 pole breaker. | 3 | Protection and control Circuit breakers connected to branch circuit derived from a 3-wire grounded neutral system are not 2-pole, or the handles of single pole breakers are not interlocked | Breakers_at_top_right_are_not_interlocked.png | file://x:/photopub/docs/0000000536/48f83f8d-6e76-463c-a9c7-5b2022661079.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__16cda673_102b_4b6b_9404_f7bf5f590eb8
ELOP-748236-2017 | 3531 | 2/16/2017 12:31:59 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL276 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | 2 | 2 | #Emergency_light.png Emergency lighting unit without evidence of periodic testing. Without proper lighting in the case of an emergency or power outage safe egress from the facility may be limited. | 2 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | Emergency_light.png | file://x:/photopub/docs/0000000559/be9eeeff-7342-49d8-a2ec-45c5ffc78ebc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__887a3ede_7bfb_453c_a5e7_a0b96c6a5513
ELOP-748238-2017 | 3529 | 2/16/2017 11:00:24 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL276 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | 2 | 2 | #Emergency_lighting21.png,Emergency_lighting22.png Emergency lighting unit without evidence of periodic testing. Without proper lighting in the case of an emergency or power outage safe egress from the facility may be limited. | 2 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | Emergency_lighting22.png | file://x:/photopub/docs/0000000559/fc8918b2-b698-49f3-8cc4-195142aa10eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__efc9ce1c_6678_43b6_a07e_c353981f9829
ELHE-746554-2017 | HE-495536-2017 | 9/9/2016 9:01:38 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Panel_cover_missing1.png,Panel_cover_missing2.png Panel covers removed on energized panels leaving exposed electrical parts and a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Panel_cover_missing1.png | file://x:/photopub/docs/0000000559/c88f4e5e-7d50-4dde-b7cd-1d41ace50f6f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b73b902f_2fd1_4d38_8c90_ad769587baa6
ELHE-746554-2017 | HE-495536-2017 | 9/9/2016 9:01:38 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Panel_cover_missing1.png,Panel_cover_missing2.png Panel covers removed on energized panels leaving exposed electrical parts and a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Panel_cover_missing2.png | file://x:/photopub/docs/0000000559/c8f39e70-e551-4fd2-99f0-98e891015393.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b73b902f_2fd1_4d38_8c90_ad769587baa6
ELIN-730197-2016 | EL-280757-2015 | 12/29/2016 11:24:43 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | Live receptacles without a cover plate is a shock hazard as an individual may come into contact with live electrical parts. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | B.png | file://x:/photopub/docs/0000000536/54f57e7c-dd78-4ced-9b6f-7ab98085a80e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3efe0134_c9ae_4a88_83a6_d8532f56c80c
ELIN-730197-2016 | EL-280757-2015 | 12/29/2016 11:24:43 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | Live receptacles without a cover plate is a shock hazard as an individual may come into contact with live electrical parts. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | C.png | file://x:/photopub/docs/0000000536/116ca8c1-f735-4465-a8b0-e20a656160bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3efe0134_c9ae_4a88_83a6_d8532f56c80c
ELIN-730197-2016 | EL-280757-2015 | 12/29/2016 11:24:43 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | Live receptacles without a cover plate is a shock hazard as an individual may come into contact with live electrical parts. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | A.png | file://x:/photopub/docs/0000000536/76b5d6d0-f71c-4d9a-833f-15c33d3431cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3efe0134_c9ae_4a88_83a6_d8532f56c80c
ELIN-730197-2016 | EL-280757-2015 | 12/29/2016 11:24:43 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | Live receptacles without a cover plate is a shock hazard as an individual may come into contact with live electrical parts. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | D.png | file://x:/photopub/docs/0000000536/0844ed82-ce71-47c0-b80f-96a77355703e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3efe0134_c9ae_4a88_83a6_d8532f56c80c
PROP-718191-2016 | 2224049 | 12/7/2016 3:18:46 PM | ASSESS: PR OP: Annual | png | #asFound | PR044 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | 3 | 3 | Lift was not operating for public at the time of inspection. No annunciation of a fault occurred when the counterweight limit switches (x2) were actuated. It was determined that the limit switches were electrically bypassed in a junction box (bypassed by connecting the incoming and outgoing conductors with an insulated wire cap connector). This could result in a condition in that a counter weight reaching it's limit of travel would not be detected and not cause the ropeway to become inoperable. This would result in a risk were it could be possible to operate the ropeway without proper haul rope tension. This Inturn could cause a deropement hazard. | 3 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | Counter_weight_limit_switch_bridged.png | file://x:/photopub/docs/0000000528/94c0ec06-4d33-4a13-893e-9ebaf1d3e441.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da327ab8_bed3_40e6_b5ba_3b3f30795e39
ELOP-748238-2017 | 3529 | 2/16/2017 11:00:24 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL276 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | 2 | 2 | #Emergency_lighting21.png,Emergency_lighting22.png Emergency lighting unit without evidence of periodic testing. Without proper lighting in the case of an emergency or power outage safe egress from the facility may be limited. | 2 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | Emergency_lighting21.png | file://x:/photopub/docs/0000000559/7177f943-fe71-47aa-9677-269745524954.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__efc9ce1c_6678_43b6_a07e_c353981f9829
ELOP-744443-2017 | 4299646 | 2/17/2017 10:03:40 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound Label of UL and their file number. It does not bear acceptable evidence of electrical approval for use in BC. | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Labelling.png Reinspection of non-compliances on a food processing plant that processes fruits. An apple coring machine that processes apples does not bear acceptable evidence of electrical approval. Previously, an employee was seriously injured by this machine. The machine has been altered. With the labelling on this machine it can not proven to be safe for use. It is therefore, not approved for use. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Labelling.png | file://x:/photopub/docs/0000000559/d2a36b36-08a3-4f20-bdde-92a9fffdc31e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c103ea1_7a6b_4ce4_a5a8_1511e09c1530
BPVOP-752362-2017 | 2265732 | 2/6/2017 2:03:43 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP212 | 5.1.1 Work done: unqualified ind - Repair or alteration done by unlicensed contractor or unqualified individual | 3 | 3 | #Repair_work_1.png,Repair_work_2.png,Repair_work_3.png,Repair_work_4.png,Contractor.png A person must hold a contractors license in order to perform regulated work. I found repair work was done by an individual, who did not possess a boiler contractors licence for work carried out on a 30psi hot water boiler.This can result in an incident due to the unlicensed individual is unfamiliar of the code requirements for the scope of work performed. | 3 | 5.1.1 Work done: unqualified ind - Repair or alteration done by unlicensed contractor or unqualified individual | Repair_work_1.png | file://x:/photopub/docs/0000000554/ab044b14-f7df-45af-8f16-9aae044ad478.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d11dd77_6739_4f8f_a2eb_a6673ef28fbd
BPVOP-752362-2017 | 2265732 | 2/6/2017 2:03:43 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP212 | 5.1.1 Work done: unqualified ind - Repair or alteration done by unlicensed contractor or unqualified individual | 3 | 3 | #Repair_work_1.png,Repair_work_2.png,Repair_work_3.png,Repair_work_4.png,Contractor.png A person must hold a contractors license in order to perform regulated work. I found repair work was done by an individual, who did not possess a boiler contractors licence for work carried out on a 30psi hot water boiler.This can result in an incident due to the unlicensed individual is unfamiliar of the code requirements for the scope of work performed. | 3 | 5.1.1 Work done: unqualified ind - Repair or alteration done by unlicensed contractor or unqualified individual | Repair_work_4.png | file://x:/photopub/docs/0000000554/818d62e7-16fe-4a5f-82d7-f02186a0f0b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d11dd77_6739_4f8f_a2eb_a6673ef28fbd
BPVOP-752362-2017 | 2265732 | 2/6/2017 2:03:43 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP212 | 5.1.1 Work done: unqualified ind - Repair or alteration done by unlicensed contractor or unqualified individual | 3 | 3 | #Repair_work_1.png,Repair_work_2.png,Repair_work_3.png,Repair_work_4.png,Contractor.png A person must hold a contractors license in order to perform regulated work. I found repair work was done by an individual, who did not possess a boiler contractors licence for work carried out on a 30psi hot water boiler.This can result in an incident due to the unlicensed individual is unfamiliar of the code requirements for the scope of work performed. | 3 | 5.1.1 Work done: unqualified ind - Repair or alteration done by unlicensed contractor or unqualified individual | Repair_work_2.png | file://x:/photopub/docs/0000000554/92afae71-766f-47bb-981c-532f905a05bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d11dd77_6739_4f8f_a2eb_a6673ef28fbd
BPVOP-752362-2017 | 2265732 | 2/6/2017 2:03:43 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP212 | 5.1.1 Work done: unqualified ind - Repair or alteration done by unlicensed contractor or unqualified individual | 3 | 3 | #Repair_work_1.png,Repair_work_2.png,Repair_work_3.png,Repair_work_4.png,Contractor.png A person must hold a contractors license in order to perform regulated work. I found repair work was done by an individual, who did not possess a boiler contractors licence for work carried out on a 30psi hot water boiler.This can result in an incident due to the unlicensed individual is unfamiliar of the code requirements for the scope of work performed. | 3 | 5.1.1 Work done: unqualified ind - Repair or alteration done by unlicensed contractor or unqualified individual | Repair_work_3.png | file://x:/photopub/docs/0000000554/f653923c-5652-4473-b0cd-c9cee7217a19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d11dd77_6739_4f8f_a2eb_a6673ef28fbd
ELIN-721063-2016 | EL-456108-2016 | 12/12/2016 4:20:17 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 2 | Arc-fault protection is required on new branch circuits 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation at a single family dwelling, two new 15 amp circuits where installed with arc-fault receptacles at the first device. Armoured cable or conduit was not used to protect the circuit between the panel and the first device. If a series or parallel arc was to occur in this branch circuit between the electrical panel and first device, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard inside the dwelling. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | AFCI_Receptacles.png | file://x:/photopub/docs/0000000530/dce74472-01f0-4396-bc26-3f30e853b9d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51650ccb_651b_4e5c_9733_152c9b057dc8
ELIN-721063-2016 | EL-456108-2016 | 12/12/2016 4:20:17 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 2 | Arc-fault protection is required on new branch circuits 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation at a single family dwelling, two new 15 amp circuits where installed with arc-fault receptacles at the first device. Armoured cable or conduit was not used to protect the circuit between the panel and the first device. If a series or parallel arc was to occur in this branch circuit between the electrical panel and first device, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard inside the dwelling. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Load_centre_with_no_AFCI_breaker_.png | file://x:/photopub/docs/0000000530/e01456a4-e46f-4f1c-b335-8d6a8871f274.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51650ccb_651b_4e5c_9733_152c9b057dc8
GAHE-732002-2017 | HE-486233-2017 | 1/3/2017 12:51:25 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA163 | Use of appliance/accessories that creates a immediate hazard (Risk Registry Item GA-04) | 5 | 5 | An unapproved Burner installed to a gas line is left burning unattended. Appliance is not a certified appliance, left in an unsafe manner. Appliance could fall over, cause a gas leak or explosion. Burner is not approved for this type of use without and safeties installed for flame rectification. | 5 | Use of appliance/accessories that creates a immediate hazard (Risk Registry Item GA-04) | Ransome_burner_RTA.png | file://x:/photopub/docs/0000000537/acf48328-942e-46b7-8a57-f403b3676b8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72a2384b_4c66_402c_a590_92107b3d7023
BPVOP-722089-2016 | 2885658 | 12/12/2016 4:09:43 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP072 | 1.2.3 Boiler construction - Stains on insulation indicating corrosion under insulation. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Stains on insulation indicating corrosion under insulation. | corrosion.png | file://x:/photopub/docs/0000000530/69c91a4b-653d-4d9e-ab09-4da3c2992b43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74cae088_9837_4cf3_8b8a_1c4998ee5b04
BPVIN-722177-2016 | BPV-479770-2016 | 12/12/2016 4:45:42 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 165 psig, I found a Pressure Relief Device not replaced within the last 3 years as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | PRD_.png | file://x:/photopub/docs/0000000530/4388f4a2-3d1b-401b-8e24-f9de78008b63.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f8f440b_5df0_4f7b_abfb_c304757d83bd
BPVOP-721901-2016 | 4073461 | 12/12/2016 12:13:54 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP218 | 5.1.2 Validation: work performed - Maintenance procedures are not documented | 2 | 2 |  | 2 | 5.1.2 Validation: work performed - Maintenance procedures are not documented | Overheating.png | file://x:/photopub/docs/0000000530/da313cb2-cc1d-4844-b9b6-35ff7af41b41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0c1a3ad_74c6_4350_83b6_0ad6dac56418
ELIN-747507-2017 | EL-495630-2017 | 1/31/2017 9:36:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 2 | #A.png No expansion joint installed. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | A.png | file://x:/photopub/docs/0000000551/a3f61cfa-d384-4576-b04a-b0e102d4417c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c58cb9d6_7f13_4500_a190_672608671923
BPVIN-737550-2017 | BPV-392006-2016 | 1/26/2017 11:12:13 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Nameplate_1.png,Nameplate_2.png The total heating surface for two boilers is 174 square meters. It is a fifth class plant and need continuous attendance of a qualified operator. No operator was found during inspection. It can result in lack of operation and maintenance. Potential accidents exists due to lack of qualified operator. See the attached nameplate as reference. MDRs is added to the attachment as well. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Nameplate_2.png | file://x:/photopub/docs/0000000555/339f8929-a9ad-4d22-846a-3a5dbf65af32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__faa57dd4_66d4_4a6b_be2a_2b3533a3403f
BPVIN-737550-2017 | BPV-392006-2016 | 1/26/2017 11:12:13 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Nameplate_1.png,Nameplate_2.png The total heating surface for two boilers is 174 square meters. It is a fifth class plant and need continuous attendance of a qualified operator. No operator was found during inspection. It can result in lack of operation and maintenance. Potential accidents exists due to lack of qualified operator. See the attached nameplate as reference. MDRs is added to the attachment as well. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Nameplate_1.png | file://x:/photopub/docs/0000000555/0c6de82f-1795-43d6-a671-8713d705a233.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__faa57dd4_66d4_4a6b_be2a_2b3533a3403f
ELIN-723103-2016 | UW-480485-2016 | 12/13/2016 2:36:36 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Incorrect junction boxes used. Armoured cable is not terminated with proper fittings and connectors. Should a short circuit occur on the cable, any available fault current would not be dissipated. This could lead to either a fire or shock should someone accidentally handle the cable. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Incorrect_wirin__incorrect_wiring_method_used.png | file://x:/photopub/docs/0000000530/14c7ceb6-f3e6-4865-80e3-b97649d090dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84c22197_7186_4690_af05_879d865efcb9
ELIN-723103-2016 | UW-480485-2016 | 12/13/2016 2:36:36 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Incorrect junction boxes used. Armoured cable is not terminated with proper fittings and connectors. Should a short circuit occur on the cable, any available fault current would not be dissipated. This could lead to either a fire or shock should someone accidentally handle the cable. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Armoured_cable__armoured_cable_used_in_plastic_device_boxes_no_connecters_used.png | file://x:/photopub/docs/0000000530/f806436f-0e14-4f6c-988b-8d1cea22b2a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84c22197_7186_4690_af05_879d865efcb9
ELIN-714701-2016 | EL-445937-2016 | 12/14/2016 1:43:48 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The service conduit has no expansion joint as the conduit exits the ground. When the ground settles in spring the underground raceway can get pulled off the meterbase, and create a shock hazard by exposing BC Hydro conductors. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Meterbase.png | file://x:/photopub/docs/0000000531/9d02c238-054a-432c-8979-16b3005caf02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54265f3c_524a_4a3e_83ee_665a972480e6
ELIN-714701-2016 | EL-445937-2016 | 12/14/2016 1:43:48 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The service conduit has no expansion joint as the conduit exits the ground. When the ground settles in spring the underground raceway can get pulled off the meterbase, and create a shock hazard by exposing BC Hydro conductors. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_conduit.png | file://x:/photopub/docs/0000000531/8b8d6f5f-9b71-4923-8c01-83d8035088ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54265f3c_524a_4a3e_83ee_665a972480e6
ELIN-721266-2016 | EL-417640-2016 | 12/9/2016 2:59:19 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Nonmetallic_sheath__nonmetallic_sheath_cable_used_outdoors_temporary_construction_permit_had_been_closed_by_the_contractor.png | file://x:/photopub/docs/0000000529/c193a8fa-dcc1-4f9c-8393-5fe2d058a86f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd8faaa0_edec_46f0_a988_a373733295e5
ELIN-721266-2016 | EL-417640-2016 | 12/9/2016 2:59:19 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Nonmetallic_sheath__nonmetallic_sheath_cable_and_yellow_banana_box_or_not_approved_for_wet_locations.png | file://x:/photopub/docs/0000000529/18e8df99-d6d6-46a2-afe5-a0c6d3ffd5e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd8faaa0_edec_46f0_a988_a373733295e5
ELIN-723484-2016 | EL-464244-2016 | 12/15/2016 3:31:25 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Un-used opening in panel. This is a shock hazard as an individual could make contact with live parts. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | D.png | file://x:/photopub/docs/0000000531/f5c45339-5c75-459d-ab84-7dfe2b5a4636.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85f6d14e_4e59_43be_b59d_6c49f9cefa49
ELIN-723484-2016 | EL-464244-2016 | 12/15/2016 3:31:25 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Un-used opening in panel. This is a shock hazard as an individual could make contact with live parts. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | E.png | file://x:/photopub/docs/0000000531/072c1b7a-d958-42ba-b136-ad7cc9dca797.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85f6d14e_4e59_43be_b59d_6c49f9cefa49
ELIN-723484-2016 | EL-464244-2016 | 12/15/2016 3:31:25 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Un-used opening in panel. This is a shock hazard as an individual could make contact with live parts. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | C.png | file://x:/photopub/docs/0000000531/784bf966-e80f-4a51-830e-096606e0a5eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85f6d14e_4e59_43be_b59d_6c49f9cefa49
ELIN-723484-2016 | EL-464244-2016 | 12/15/2016 3:31:25 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Un-used opening in panel. This is a shock hazard as an individual could make contact with live parts. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | A.png | file://x:/photopub/docs/0000000531/99913608-97f5-4015-ac44-4a034761783f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85f6d14e_4e59_43be_b59d_6c49f9cefa49
ELIN-723484-2016 | EL-464244-2016 | 12/15/2016 3:31:25 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Un-used opening in panel. This is a shock hazard as an individual could make contact with live parts. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | B.png | file://x:/photopub/docs/0000000531/dad93f9d-1f2e-401a-acee-39e2e73a47f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85f6d14e_4e59_43be_b59d_6c49f9cefa49
ELIN-743831-2017 | EL-424827-2016 | 1/26/2017 10:48:40 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Exterior_outlet_in_deck_area_with_energized_conductors_and_no_cover_provided_.png Energized 120v conductors in outlet box located in upper deck area are not properly terminated. The outlet box, intended for a receptacle, does not have a device and has no cover, leaving energized conductors exposed and increasing the likelihood of accidental electric shock if contacted. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exterior_outlet_in_deck_area_with_energized_conductors_and_no_cover_provided_.png | file://x:/photopub/docs/0000000548/f367e984-7b7d-4137-964b-e10cd38aedad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ddaf34c_79d3_496e_9077_62a5d62ff199
GAHE-745677-2017 | HE-494982-2017 | 1/27/2017 1:20:30 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | #Propane_system_Cypress_bowl1.png,Propane_system_Cypress_bowl2.png The as found hazard was a propane dispensing station without an emergency shut off means. This could result in personnel not being able to shut off liquid propane in the event of a malfunction or emergency. | 4 | Missing mandatory safety controls | Propane_system_Cypress_bowl1.png | file://x:/photopub/docs/0000000548/0952b90d-db12-4cf8-9190-7687a32254c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f728ee3_badd_45a3_9702_6b6a3933a314
ELIN-720367-2016 | EL-465642-2016 | 12/13/2016 1:29:47 PM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | Receptacles are required to have cover plates to protect against objects making contact with the energized terminals on the side of the receptacle. At a new coffee shop that was preparing to open, the electrical contractor had requested a final inspection before he had installed the cover plates for the receptacles at the drive through window. A potential shock hazard exists to persons working at the coffee shop if they make accidentally contact with the energized terminal of the receptacles. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Receptacles_with_no_plates_.png | file://x:/photopub/docs/0000000530/37e35d0d-54ba-4fcc-9ec7-597a4c84b8c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5146c007_7222_44b2_95bb_1ea3dd6abd92
ELHE-738540-2017 | HE-490353-2017 | 1/27/2017 2:14:03 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 4 | 4 | #Electrical_panel_in_closet1.png,Electrical_panel_in_closet2.png Electrical panels in dwellings must be located in areas that are readily accessible, not subject to damage, and provide 1 meter working clearance in front of the panel. For these reasons, the electrical code does not allow electrical panels to be mounted in clothes closets. During assessment of a mobile home, the electrical panel was found in the side wall of a narrow closet facing inwards. The owner had removed the panel cover in preparation for the assessment. It appeared that the electrical panel had been turned around to face into the closet. The working space in front of the panel was now reduced to 500mm and the branch circuits where exposed to possible mechanical damage. The limited access to the electrical panel could create a potential shock hazard for any persons having to work on the panel or electrical equipment inside the dwelling. Clothing stored inside the closet and in front of the panel could also create a fire hazard for | 4 | General Location of equipment does not allow for proper access to disconnecting means | Electrical_panel_in_closet1.png | file://x:/photopub/docs/0000000549/f27cae22-299d-43f8-bca9-e79e182e5ad0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dba636_b38d_49ed_8090_a0470ff46534
ELHE-738540-2017 | HE-490353-2017 | 1/27/2017 2:14:03 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 4 | 4 | #Electrical_panel_in_closet1.png,Electrical_panel_in_closet2.png Electrical panels in dwellings must be located in areas that are readily accessible, not subject to damage, and provide 1 meter working clearance in front of the panel. For these reasons, the electrical code does not allow electrical panels to be mounted in clothes closets. During assessment of a mobile home, the electrical panel was found in the side wall of a narrow closet facing inwards. The owner had removed the panel cover in preparation for the assessment. It appeared that the electrical panel had been turned around to face into the closet. The working space in front of the panel was now reduced to 500mm and the branch circuits where exposed to possible mechanical damage. The limited access to the electrical panel could create a potential shock hazard for any persons having to work on the panel or electrical equipment inside the dwelling. Clothing stored inside the closet and in front of the panel could also create a fire hazard for | 4 | General Location of equipment does not allow for proper access to disconnecting means | Electrical_panel_in_closet2.png | file://x:/photopub/docs/0000000549/8a1b5eb3-6275-4b4c-b447-7b2952cff1a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dba636_b38d_49ed_8090_a0470ff46534
GAIN-743982-2017 | GA-488890-2017 | 1/27/2017 1:45:13 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #King_George_4.png,King_george.png Appliance sidewall vented, not listed as an approved method by manufacturer. Possibly of spillage of exhaust products due to improper draft. Possible risk of carbon oxide . | 3 | Appliance not installed according to installation instructions | King_George_4.png | file://x:/photopub/docs/0000000549/199e6d9a-87d9-4be3-821e-0ad5703bcd14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__100c1e1b_62f2_4a40_9012_ff1719ad90a2
BPVOP-723316-2016 | 2256020 | 11/7/2016 8:20:07 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Non compliant to Safety Order SO B6 0505303 | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Overall.png | file://x:/photopub/docs/0000000530/065c8260-be09-4bab-95d1-f11c81d25b8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c13d790_24d5_42a8_a2ca_11c4c0762ea6
BPVOP-723316-2016 | 2256020 | 11/7/2016 8:20:07 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Non compliant to Safety Order SO B6 0505303 | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Relief_valve.png | file://x:/photopub/docs/0000000530/a5ec91b7-8627-41bc-bd67-fbf2a88916c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c13d790_24d5_42a8_a2ca_11c4c0762ea6
BPVOP-723316-2016 | 2256020 | 11/7/2016 8:20:07 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Non compliant to Safety Order SO B6 0505303 | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Nameplate.png | file://x:/photopub/docs/0000000530/841f19d8-0bcb-41c9-8fc5-c1710cad4d1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c13d790_24d5_42a8_a2ca_11c4c0762ea6
ELHE-748488-2017 | HE-496447-2017 | 2/2/2017 7:58:35 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cable connector was not used for entering cable into electrical panel | EL135 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | 3 | 3 | #Electrical_work__electrical_work_performed_by_handyman1.png,Electrical_work__electrical_work_performed_by_handyman2.png,Electrical_work__electrical_work_performed_by_handyman3.png,Electrical_work__electrical_work_performed_by_handyman4.png,Electrical_work__electrical_work_performed_by_handyman5.png,Electrical_work__electrical_work_performed_by_handyman6.png Electrical work has been performed by a handyman who incorrectly entered nonmetallic sheath cable into electrical junction boxes by cutting and removing part of the electrical junction box. Energized conductors are exposed and there is a chance that some one could accidentally touch electrical terminals of switches. | 3 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | Electrical_work__electrical_work_performed_by_handyman4.png | file://x:/photopub/docs/0000000552/e058c262-7422-481c-be42-8a0a80c26710.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cef38eeb_527f_48bb_9df6_e21627476ce8
ELHE-748488-2017 | HE-496447-2017 | 2/2/2017 7:58:35 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Handyman covered the non metallic shift cable with a wire mould | EL135 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | 3 | 3 | #Electrical_work__electrical_work_performed_by_handyman1.png,Electrical_work__electrical_work_performed_by_handyman2.png,Electrical_work__electrical_work_performed_by_handyman3.png,Electrical_work__electrical_work_performed_by_handyman4.png,Electrical_work__electrical_work_performed_by_handyman5.png,Electrical_work__electrical_work_performed_by_handyman6.png Electrical work has been performed by a handyman who incorrectly entered nonmetallic sheath cable into electrical junction boxes by cutting and removing part of the electrical junction box. Energized conductors are exposed and there is a chance that some one could accidentally touch electrical terminals of switches. | 3 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | Electrical_work__electrical_work_performed_by_handyman2.png | file://x:/photopub/docs/0000000552/a1de92fe-1a33-40f8-adea-e7a8b7d820c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cef38eeb_527f_48bb_9df6_e21627476ce8
ELHE-748488-2017 | HE-496447-2017 | 2/2/2017 7:58:35 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Form of wire moldnused from electrical panel to receptacle | EL135 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | 3 | 3 | #Electrical_work__electrical_work_performed_by_handyman1.png,Electrical_work__electrical_work_performed_by_handyman2.png,Electrical_work__electrical_work_performed_by_handyman3.png,Electrical_work__electrical_work_performed_by_handyman4.png,Electrical_work__electrical_work_performed_by_handyman5.png,Electrical_work__electrical_work_performed_by_handyman6.png Electrical work has been performed by a handyman who incorrectly entered nonmetallic sheath cable into electrical junction boxes by cutting and removing part of the electrical junction box. Energized conductors are exposed and there is a chance that some one could accidentally touch electrical terminals of switches. | 3 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | Electrical_work__electrical_work_performed_by_handyman3.png | file://x:/photopub/docs/0000000552/33fe4d20-5389-4440-bdd0-b636d59e03f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cef38eeb_527f_48bb_9df6_e21627476ce8
ELHE-748488-2017 | HE-496447-2017 | 2/2/2017 7:58:35 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Sides of junction boxes were cut so that nonmetallic sheath cable could enter junction box | EL135 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | 3 | 3 | #Electrical_work__electrical_work_performed_by_handyman1.png,Electrical_work__electrical_work_performed_by_handyman2.png,Electrical_work__electrical_work_performed_by_handyman3.png,Electrical_work__electrical_work_performed_by_handyman4.png,Electrical_work__electrical_work_performed_by_handyman5.png,Electrical_work__electrical_work_performed_by_handyman6.png Electrical work has been performed by a handyman who incorrectly entered nonmetallic sheath cable into electrical junction boxes by cutting and removing part of the electrical junction box. Energized conductors are exposed and there is a chance that some one could accidentally touch electrical terminals of switches. | 3 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | Electrical_work__electrical_work_performed_by_handyman5.png | file://x:/photopub/docs/0000000552/ca6ebc15-d8c0-46bc-96ac-66aa9091f79a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cef38eeb_527f_48bb_9df6_e21627476ce8
ELHE-748488-2017 | HE-496447-2017 | 2/2/2017 7:58:35 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Same photo from before, sides of junction boxes had been cut by handyman | EL135 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | 3 | 3 | #Electrical_work__electrical_work_performed_by_handyman1.png,Electrical_work__electrical_work_performed_by_handyman2.png,Electrical_work__electrical_work_performed_by_handyman3.png,Electrical_work__electrical_work_performed_by_handyman4.png,Electrical_work__electrical_work_performed_by_handyman5.png,Electrical_work__electrical_work_performed_by_handyman6.png Electrical work has been performed by a handyman who incorrectly entered nonmetallic sheath cable into electrical junction boxes by cutting and removing part of the electrical junction box. Energized conductors are exposed and there is a chance that some one could accidentally touch electrical terminals of switches. | 3 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | Electrical_work__electrical_work_performed_by_handyman6.png | file://x:/photopub/docs/0000000552/e37a4622-0485-4aec-88e4-b7dba20a2217.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cef38eeb_527f_48bb_9df6_e21627476ce8
ELHE-748488-2017 | HE-496447-2017 | 2/2/2017 7:58:35 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Existing 8 Circuit Load Center, two conductor number 14 nonmetallic sheath cable taken two new receptacle for heating circuit in bedroom | EL135 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | 3 | 3 | #Electrical_work__electrical_work_performed_by_handyman1.png,Electrical_work__electrical_work_performed_by_handyman2.png,Electrical_work__electrical_work_performed_by_handyman3.png,Electrical_work__electrical_work_performed_by_handyman4.png,Electrical_work__electrical_work_performed_by_handyman5.png,Electrical_work__electrical_work_performed_by_handyman6.png Electrical work has been performed by a handyman who incorrectly entered nonmetallic sheath cable into electrical junction boxes by cutting and removing part of the electrical junction box. Energized conductors are exposed and there is a chance that some one could accidentally touch electrical terminals of switches. | 3 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | Electrical_work__electrical_work_performed_by_handyman1.png | file://x:/photopub/docs/0000000552/983dc331-65f7-488f-9bf5-83ed3666ef9f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cef38eeb_527f_48bb_9df6_e21627476ce8
PROP-598631-2016 | 2224091 | 12/14/2016 1:51:40 PM | ASSESS: PR OP: RAP | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | Heater element unguarded, could be a burn and/or fire hazard | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Heater_element_unguarded.png | file://x:/photopub/docs/0000000531/f3562c75-5609-462f-873e-c960f12238b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1CD056E8_AC7D_4F52_9C3A_144CE9247523
BPVIN-737214-2017 | BPV-489161-2017 | 1/12/2017 | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound No Canadian Registration Number | BP005 | 1.0.1 Temp/Pressure ratings not met - Manufacturer's Data Report deficiencies | 1 | 1 | #Nameplate_no_crn.png On assessment of a pressure vessel with a maximum allowable working pressure of 600kpa and a maximum allowable working temperature of 94 degrees Celsius the nameplate had no Canadian registration number. | 1 | 1.0.1 Temp/Pressure ratings not met - Manufacturer's Data Report deficiencies | Nameplate_no_crn.png | file://x:/photopub/docs/0000000542/825a4e3f-3cdc-4ac6-8376-e4812cc4016a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a08d49f2_56c1_4285_90fb_aca057bcedce
ELHE-749008-2017 | HE-486320-2017 | 1/31/2017 10:43:37 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Propane_area.png Unapproved equipment and wiring within an hazardous area creating a potential explosion hazard. Equipment was disconnected prior to the site visit. This is for tacking purposes. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Propane_area.png | file://x:/photopub/docs/0000000550/9ab68d9b-2dba-46c3-94c2-758ee933fe5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14f4bc6c_c716_48c5_8cbe_4994017c0f06
GAOP-753571-2017 | 2170705 | 2/20/2017 8:17:45 AM | ASSESS: GA OP: Periodic | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | #Clearance_to_combustible_materials_not_met_.png Clearance to combustible material from propane tank not met. In the event of a fire combustible material surrounding propane tank could contribute to the fire. | 2 | Installation clearances or set backs to propane containers not met | Clearance_to_combustible_materials_not_met_.png | file://x:/photopub/docs/0000000559/8abe0ede-2386-48f7-a845-5d758860a587.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75b802a7_f8f9_4eeb_bfd1_772f166948a6
ELIN-737814-2017 | EL-464176-2016 | 1/13/2017 10:28:15 AM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #U_g_nmd90_cable_1.png,U_g_nmd90_cable_2.png,U_g_nmd90_cable_3.png The 40 amp 120/240 volt feeder to the garage uses NMD90 cable u/g. This cable is not approved for a wet location and may deteriorate to the point this can become a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | U_g_nmd90_cable_3.png | file://x:/photopub/docs/0000000543/902a7244-155b-42b7-b6b5-4781921a462a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c6a2805_297d_49e9_9417_f269b9dc65ff
ELIN-736303-2017 | EL-470810-2016 | 1/12/2017 2:00:59 PM | ASSESS: EL: Service Connection | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Switches_within_1_meter_of_tub.png The 15 amp 120 volt power for lighting switches are located within 500mm of the bathtub and not GFCI protected, this is a shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Switches_within_1_meter_of_tub.png | file://x:/photopub/docs/0000000543/a3884eae-3bdf-4f13-a18f-f6724ac2d3a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e11c286_afd8_4a7e_9e93_ea9d533b1309
ELIN-737814-2017 | EL-464176-2016 | 1/13/2017 10:28:15 AM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #U_g_nmd90_cable_1.png,U_g_nmd90_cable_2.png,U_g_nmd90_cable_3.png The 40 amp 120/240 volt feeder to the garage uses NMD90 cable u/g. This cable is not approved for a wet location and may deteriorate to the point this can become a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | U_g_nmd90_cable_2.png | file://x:/photopub/docs/0000000543/54accc99-8e3e-43e5-b5c0-6a2a33fb983e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c6a2805_297d_49e9_9417_f269b9dc65ff
ELIN-737814-2017 | EL-464176-2016 | 1/13/2017 10:28:15 AM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #U_g_nmd90_cable_1.png,U_g_nmd90_cable_2.png,U_g_nmd90_cable_3.png The 40 amp 120/240 volt feeder to the garage uses NMD90 cable u/g. This cable is not approved for a wet location and may deteriorate to the point this can become a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | U_g_nmd90_cable_1.png | file://x:/photopub/docs/0000000543/1ed6841c-64da-44e8-a405-e4adba4b3a61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c6a2805_297d_49e9_9417_f269b9dc65ff
ELIN-721289-2016 | EL-456665-2016 | 1/11/2017 11:44:54 AM | ASSESS: EL: Final | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 | #Incomplete_panel_directory.png Panel board directory is not complete. Marking of circuits is required to enable speedy location of control devices if necessary to open circuits. | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Incomplete_panel_directory.png | file://x:/photopub/docs/0000000543/7930280f-6682-4c94-81e8-888d826a7d37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa4ceb81_0aea_4025_9989_8ea806ad613c
ELOP-722885-2016 | 464 | 12/20/2016 8:44:49 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL232 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | 4 | 3 | Wood dust accumulation over 1/8" on an insulated water line at height. Wood dust accumulations at height represent a dust explosion hazard. | 4 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Area has not been classified. Wood Dust Safety Order not addressed. | Dust_at_height.png | file://x:/photopub/docs/0000000534/f6413584-754d-4044-8869-597498c51d49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6458a40d_7eac_4053_a131_94d316bc2fb2
GAIN-708614-2016 | GA-371178-2016 | 1/26/2017 12:29:24 PM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Air.png Combustion air taken from mechanical room, combustion air termination filled with insulation and blocked | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Air.png | file://x:/photopub/docs/0000000548/0a953e87-2cb5-4bc9-ad51-2c7649b720dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d804afc0_596a_4b41_8419_8d75174d0036
ELIN-741128-2017 | EL-461690-2016 | 1/20/2017 4:32:24 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #A1.png,A2.png Non metallic sheathed cables installed in attic subject to damage from walking. Cables in attic with a greater vertical distance between the cable joist and the rafters of 1m require protection. This is a fire and shock hazard as the cables can be damaged from individuals stepping on the cables. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | A2.png | file://x:/photopub/docs/0000000546/ebfda319-f294-486b-b9ab-9d96b7193180.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ba02452_5e60_4094_917e_76a4bca20fc6
ELIN-741128-2017 | EL-461690-2016 | 1/20/2017 4:32:24 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #A1.png,A2.png Non metallic sheathed cables installed in attic subject to damage from walking. Cables in attic with a greater vertical distance between the cable joist and the rafters of 1m require protection. This is a fire and shock hazard as the cables can be damaged from individuals stepping on the cables. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | A1.png | file://x:/photopub/docs/0000000546/847b4c8d-4084-4875-a4a7-440fcfe4263f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ba02452_5e60_4094_917e_76a4bca20fc6
GAIN-721321-2016 | GA-468724-2016 | 12/14/2016 10:27:45 AM | ASSESS: GA: Rough-In | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | Missing combustion air for the water heater , this can cause burner malfunction and could cause carbon monoxide poisoning. | 4 | Combustion air supply missing | Water_heater_.png | file://x:/photopub/docs/0000000531/5c6bd3a3-10fd-4de6-9b5a-2b3f247fcd93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03b6f873_7b34_42f3_85b7_d76f173a9b94
BPOP-710883-2016 | BPV-435856-2016 | 12/28/2016 10:59:50 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA023 | Inadequate protection Low traffic | 2 | 2 | Tanks required protection from earth moving equipment | 2 | Inadequate protection Low traffic | 1648_davies_shop_area.png | file://x:/photopub/docs/0000000535/3f2e0a70-3e6d-4cdc-9cc0-06e4a1aaa0de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d4ce7f2_4d16_4129_b384_29616c69f441
BPOP-710883-2016 | BPV-435856-2016 | 12/28/2016 10:59:50 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA023 | Inadequate protection Low traffic | 2 | 2 | Tanks required protection from earth moving equipment | 2 | Inadequate protection Low traffic | Davies_2.png | file://x:/photopub/docs/0000000535/eb761f4d-300b-452f-8c5a-e051850e20a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d4ce7f2_4d16_4129_b384_29616c69f441
ELIN-740202-2017 | EL-491772-2017 | 1/24/2017 10:55:00 AM | ASSESS: EL: Service Connection | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 2 | #80_amp_breaker_on_15_and_20_amp_receptacles.png Electrical equipment with suspicious approval label has been provided by an owner for use in an indoor gardening operation. The equipment is designed to be fed with 80 amps at 240 volts. The 15 amp and 20 amp receptacles that are part of this equipment lack the necessary overcurrent protection required. Serious damage or fire to electrical equipment and property can occur on all portions of cord connected equipment when not properly protected from an overcurrent condition. This can also lead to injury of persons. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 80_amp_breaker_on_15_and_20_amp_receptacles.png | file://x:/photopub/docs/0000000549/02a2a264-f0c2-4e3c-9d33-096ebdbdd6f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__041f5c5a_0a46_4356_af8c_7d83c2fea1f7
ELIN-749138-2017 | EL-485191-2016 | 2/1/2017 4:15:33 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #NMD901.png,NMD902.png A 6/3 non-metallic-sheathed cable has been installed in a wet location and inside a raceway, both are not approved uses of the cable. This poses potential damage to the cable, other equipment and a shock hazard to persons. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | NMD902.png | file://x:/photopub/docs/0000000551/bf10cbe3-781c-428b-ab1f-13ed3acf5368.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3f1740e_0b76_4061_9fde_3fd6d9f068da
ELIN-749138-2017 | EL-485191-2016 | 2/1/2017 4:15:33 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #NMD901.png,NMD902.png A 6/3 non-metallic-sheathed cable has been installed in a wet location and inside a raceway, both are not approved uses of the cable. This poses potential damage to the cable, other equipment and a shock hazard to persons. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | NMD901.png | file://x:/photopub/docs/0000000551/72dedf1c-a846-49c2-835a-c51c01aaa0bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3f1740e_0b76_4061_9fde_3fd6d9f068da
PROP-598635-2016 | 2224038 | 12/14/2016 6:37:14 PM | ASSESS: PR OP: RAP | png | #asFound | PR000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Tabor_t-bar_return.png | file://x:/photopub/docs/0000000532/966c9352-0ba4-43b1-ad46-f835679e6f48.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__003B039A_2AF5_4443_BBBC_A20A3B9C440E
BPVOP-729593-2016 | 2256014 | 1/5/2017 2:04:21 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided for hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Emergency_shutdown_missing_switch.png | file://x:/photopub/docs/0000000539/0a58071d-a990-45de-a008-27b32d8efe76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e435622c_5594_4dd9_82db_fe608c77396c
BPVOP-729594-2016 | 2256017 | 1/5/2017 2:51:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided for hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | ESD_switch_not_installed.png | file://x:/photopub/docs/0000000539/912d3715-2b85-4f6c-a0df-7dc0ff732ef0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e67d5b96_bcd1_48cf_9563_12a01a8448b4
GAIN-731732-2017 | GA-486064-2017 | 1/6/2017 9:11:16 AM | ASSESS: GA: Rough-In | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Unprotected_tubing.png | file://x:/photopub/docs/0000000539/555c89d6-aa0e-4d8c-99ab-988e795fcfc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__062c82fb_8a2e_4128_8c5d_d0632083dc37
GAIN-730975-2016 | GA-482000-2016 | 1/6/2017 9:20:59 AM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | Lack of pressure relief valve could cause over pressure in water heater which could lead to explosion | 3 | Appliance not installed according to installation instructions | No_pressure_relief.png | file://x:/photopub/docs/0000000539/b60e339f-bda6-4d00-8b5c-c93a2f9ea29d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6cce8615_8b7a_4c3b_ae62_1eeff1c2d818
ELIN-719418-2016 | EL-476442-2016 | 12/13/2016 8:42:23 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | System grounding electrode exposed on surface of grade (blasted rock) and not in direct contact with exterior soil. Without the system being properly referenced to ground there is a serious risk of system safety protocols failing to operate during a fault condition resulting in persona, injury (shock) or property damage (thermal event). | 3 | Installation Grounding; Electrode or grounding conductor are not present. | View01_system_grounding_electrode.png | file://x:/photopub/docs/0000000532/6f26a675-27f7-493f-98e0-5723b5f70481.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba9ff073_dc1c_437c_b024_117c12e26458
ELIN-716653-2016 | EL-462034-2016 | 12/2/2016 8:44:57 AM | ASSESS: EL: Final | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | Main residential service panel is in a location that is not readily accessible or has 1 meter clearance in front of the panel Main residential service panels located in an area that is not readily accessible or has 1 meter clearance in front of the panel may present an obstacle for adequate system operation | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Panel_no_access.png | file://x:/photopub/docs/0000000528/2046776b-5e72-4a78-84f0-67b1cef71be7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd319b3c_1cbe_452c_bdff_46ba558bbe83
ELIN-728340-2016 | EL-484243-2016 | 12/22/2016 11:22:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | The ground conductor from the electrode is not continuous and is terminated with a split bolt. This is a thermal hazard condition. 100 Amp, 120/240 Volt. | 4 | Installation Grounding; conductor is not continuous. | Branch_circuit_enters_in_main_breaker_compartment_for_service_conductors_only.png | file://x:/photopub/docs/0000000534/19599b75-65c7-41f7-aa4a-2516ad70789d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef503e54_1840_4039_bb98_c6bfbaa67692
ELIN-728340-2016 | EL-484243-2016 | 12/22/2016 11:22:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | The ground conductor from the electrode is not continuous and is terminated with a split bolt. This is a thermal hazard condition. 100 Amp, 120/240 Volt. | 4 | Installation Grounding; conductor is not continuous. | Ground_conductor_is_not_continuous_and_is_terminated_with_a_split_bolt.png | file://x:/photopub/docs/0000000534/04fadba9-1af1-4d06-afab-7fad3d170ebf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef503e54_1840_4039_bb98_c6bfbaa67692
ELIN-728340-2016 | EL-484243-2016 | 12/22/2016 11:22:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | The ground conductor from the electrode is not continuous and is terminated with a split bolt. This is a thermal hazard condition. 100 Amp, 120/240 Volt. | 4 | Installation Grounding; conductor is not continuous. | Unused_openings_in_the_branch_circuit_section_of_main_distribution.png | file://x:/photopub/docs/0000000534/f21d0e9b-4a4c-4db8-8087-fbc33841a878.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef503e54_1840_4039_bb98_c6bfbaa67692
GAIN-730349-2016 | GA-415625-2016 | 12/30/2016 1:49:18 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | Air intake pointing upwards through the roof top termination allowing rain/moisture to to collect in the appliance combustion chamber with a possibility of premature failure of the appliances | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Venting.png | file://x:/photopub/docs/0000000536/46f34f86-7c71-41a3-9b3d-8f74cd0681d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d8fa3ba_a166_41aa_9b02_da24311a55a9
GAIN-703769-2016 | GA-425191-2016 | 12/13/2016 9:03:53 AM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Riser.png | file://x:/photopub/docs/0000000531/e38d971c-585b-4f65-a5dc-1023099c5f68.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b71c47a_6ac6_4137_b4fe_2f1a4efef59f
GAIN-705856-2016 | GA-465198-2016 | 12/13/2016 9:18:42 AM | ASSESS: GA: Final | png | #asFound | GA045 | Gas connector passes through wall, floor, ceiling, partition or into appliance | 2 | 2 |  | 2 | Gas connector passes through wall, floor, ceiling, partition or into appliance | Connector.png | file://x:/photopub/docs/0000000531/0ea8d141-73f3-473e-9bd0-2ac3d745d04b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1200d97e_d779_4104_9505_3f30ba75be87
GAIN-705856-2016 | GA-465198-2016 | 12/13/2016 9:18:42 AM | ASSESS: GA: Final | png | #asFound | GA045 | Gas connector passes through wall, floor, ceiling, partition or into appliance | 2 | 2 |  | 2 | Gas connector passes through wall, floor, ceiling, partition or into appliance | Street90.png | file://x:/photopub/docs/0000000531/6e388b04-a7e0-44a5-a699-964c8171d6f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1200d97e_d779_4104_9505_3f30ba75be87
ELOP-735165-2017 | 4666236 | 1/26/2017 11:39:50 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_breaker_spaces_21.png,Open_breaker_spaces_22.png 600 volt panel breakers spaces open on energized panels leaving exposed electrical parts and a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_breaker_spaces_22.png | file://x:/photopub/docs/0000000548/a22e66d6-4228-4694-8922-4769af30c54f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2676124_1365_4956_b353_7b083e070a6a
ELOP-735165-2017 | 4666236 | 1/26/2017 11:39:50 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_breaker_spaces_21.png,Open_breaker_spaces_22.png 600 volt panel breakers spaces open on energized panels leaving exposed electrical parts and a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_breaker_spaces_21.png | file://x:/photopub/docs/0000000548/d000ad71-a3a4-46d1-8f22-38f7735c4501.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2676124_1365_4956_b353_7b083e070a6a
ELIN-749809-2017 | EL-439260-2016 | 2/6/2017 2:34:20 PM | ASSESS: EL: Final | png | #asFound | EL192 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, within area of energized parts. | 4 | 4 | #Exposed_and_energized1.png,Exposed_and_energized2.png,Exposed_and_energized3.png Energized circuits exposed to contact. Shock hazard. | 4 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, within area of energized parts. | Exposed_and_energized2.png | file://x:/photopub/docs/0000000554/24343cbd-fa2f-4497-87b6-d5a8bf2129e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49fd3fdd_2ad8_4a26_802f_9527b2481122
BPVIN-305320-2015 | BPV-199342-2015 | 11/30/2016 10:14:53 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP022 | 1.0.2 Clearances/Maintenance - Insufficient clearance for operation, maintenance and inspection. | 2 | 2 | Upon assessment it is found that clearance around boiler is not to code. It will be difficult to perform maintenance. | 2 | 1.0.2 Clearances/Maintenance - Insufficient clearance for operation, maintenance and inspection. | Boiler_with_inadequate_clearance.png | file://x:/photopub/docs/0000000525/57c75480-d7e2-4f24-92b2-62281ac093d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc02c3c0_b272_403b_aba1_4659b7cb4b6f
ELHE-716660-2016 | HE-476024-2016 | 12/5/2016 10:29:09 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL070 | Effective bonding and grounding The identified conductor is not provided or is not longer functional. | 4 | 4 | 240 volt subfeed neutral to mobile home has strands cut to fit neutral bar and created voltage spike. Continuation of connection may lead to further spiking and damage or persons or property. | 4 | Effective bonding and grounding The identified conductor is not provided or is not longer functional. | Cable.png | file://x:/photopub/docs/0000000526/1dbdfb67-9ff3-4458-b142-9488f64d8169.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a12111ee_e653_4171_a902_c0d4ef6401e1
ELHE-716660-2016 | HE-476024-2016 | 12/5/2016 10:29:09 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL070 | Effective bonding and grounding The identified conductor is not provided or is not longer functional. | 4 | 4 | 240 volt subfeed neutral to mobile home has strands cut to fit neutral bar and created voltage spike. Continuation of connection may lead to further spiking and damage or persons or property. | 4 | Effective bonding and grounding The identified conductor is not provided or is not longer functional. | Main_panel.png | file://x:/photopub/docs/0000000526/bbbaf0fb-5d65-4fe3-9f4d-42f29a113478.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a12111ee_e653_4171_a902_c0d4ef6401e1
ELHE-716660-2016 | HE-476024-2016 | 12/5/2016 10:29:09 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL070 | Effective bonding and grounding The identified conductor is not provided or is not longer functional. | 4 | 4 | 240 volt subfeed neutral to mobile home has strands cut to fit neutral bar and created voltage spike. Continuation of connection may lead to further spiking and damage or persons or property. | 4 | Effective bonding and grounding The identified conductor is not provided or is not longer functional. | Feeder_termination.png | file://x:/photopub/docs/0000000526/048d95b8-585f-4d1c-a01c-70c7bf2245ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a12111ee_e653_4171_a902_c0d4ef6401e1
ELHE-716660-2016 | HE-476024-2016 | 12/5/2016 10:29:09 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL070 | Effective bonding and grounding The identified conductor is not provided or is not longer functional. | 4 | 4 | 240 volt subfeed neutral to mobile home has strands cut to fit neutral bar and created voltage spike. Continuation of connection may lead to further spiking and damage or persons or property. | 4 | Effective bonding and grounding The identified conductor is not provided or is not longer functional. | Sub_feed_neutral_damage.png | file://x:/photopub/docs/0000000526/4d697b2d-96ec-4a11-ae33-f445ad128ea8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a12111ee_e653_4171_a902_c0d4ef6401e1
GAIN-568582-2016 | GA-374412-2016 | 1/3/2017 7:54:32 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | 30 gauge elbow used on venting of pizza oven, fire hazard | 3 | Unapproved venting material | Pizza_oven.png | file://x:/photopub/docs/0000000538/510439f7-3e30-4470-9544-f705922280c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e830ccc0_8caa_44d0_b6bb_da289233aae2
ELIN-749809-2017 | EL-439260-2016 | 2/6/2017 2:34:20 PM | ASSESS: EL: Final | png | #asFound | EL192 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, within area of energized parts. | 4 | 4 | #Exposed_and_energized1.png,Exposed_and_energized2.png,Exposed_and_energized3.png Energized circuits exposed to contact. Shock hazard. | 4 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, within area of energized parts. | Exposed_and_energized3.png | file://x:/photopub/docs/0000000554/4bbf620c-679e-4a10-a53d-116827f8a04e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49fd3fdd_2ad8_4a26_802f_9527b2481122
ELIN-749809-2017 | EL-439260-2016 | 2/6/2017 2:34:20 PM | ASSESS: EL: Final | png | #asFound | EL192 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, within area of energized parts. | 4 | 4 | #Exposed_and_energized1.png,Exposed_and_energized2.png,Exposed_and_energized3.png Energized circuits exposed to contact. Shock hazard. | 4 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, within area of energized parts. | Exposed_and_energized1.png | file://x:/photopub/docs/0000000554/7268ae9c-d8cb-4358-8af3-1f6892bdbd08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49fd3fdd_2ad8_4a26_802f_9527b2481122
BPVOP-717156-2016 | 4183558 | 12/5/2016 11:02:25 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP163 | 5.0.1 Operator non-compliance - Safety orders not followed or adhered to | 3 | 3 | Upon assessment it is determined that machine mounted air receiver (1.5m long and .50m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 5.0.1 Operator non-compliance - Safety orders not followed or adhered to | Safety_valve.png | file://x:/photopub/docs/0000000526/af336aeb-4119-4c30-9a70-ee7c4b19e815.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3481ef6b_dfce_4243_9eeb_3b1d83e7a680
BPVOP-717160-2016 | 2268372 | 12/5/2016 11:40:25 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP163 | 5.0.1 Operator non-compliance - Safety orders not followed or adhered to | 3 | 3 | Upon assessment of machine mounted horizontal air receiver (1.2m long and .5m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, it was determined that vessel has exceeded 20 years of service life without having complete examination (complete examination for vessel over 20 years shall include the use of surface and volumetric NDE testing as applicable, to determine thickness and identify defects such as cracking, corrosion and pitting). Minimum thickness of pressure boundary (shell, nozzle, weld etc.) determines the MAWP and presence of corrosion, cracking and pitting may cause failure of pressure boundary at a pressure well below MAWP. In the event of failure of pressure boundary, shooting/propelling effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 5.0.1 Operator non-compliance - Safety orders not followed or adhered to | VESSEL_OVER_20_YEARS_OF_AGE.png | file://x:/photopub/docs/0000000526/a77fef43-5c9a-4774-9131-a93e5a44939e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0fd417bf_01c3_40f6_b4c6_46c0d404530a
BPVOP-717160-2016 | 2268372 | 12/5/2016 11:40:25 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP163 | 5.0.1 Operator non-compliance - Safety orders not followed or adhered to | 3 | 3 | Upon assessment of machine mounted horizontal air receiver (1.2m long and .5m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, it was determined that vessel has exceeded 20 years of service life without having complete examination (complete examination for vessel over 20 years shall include the use of surface and volumetric NDE testing as applicable, to determine thickness and identify defects such as cracking, corrosion and pitting). Minimum thickness of pressure boundary (shell, nozzle, weld etc.) determines the MAWP and presence of corrosion, cracking and pitting may cause failure of pressure boundary at a pressure well below MAWP. In the event of failure of pressure boundary, shooting/propelling effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 5.0.1 Operator non-compliance - Safety orders not followed or adhered to | SAFETY_VALVE.png | file://x:/photopub/docs/0000000526/473da615-227c-4dda-87ef-801e507bc375.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0fd417bf_01c3_40f6_b4c6_46c0d404530a
ELIN-751214-2017 | EL-425810-2016 | 2/6/2017 2:15:56 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #Temp_feeder_cable1.png,Temp_feeder_cable2.png The energized 100 amp 120/240 volt feeder cable fed from temporary service is laid out on floor exposing it to mechanical damage and can lead to a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Temp_feeder_cable2.png | file://x:/photopub/docs/0000000554/90590830-3278-4978-a8a5-d6c92ee23366.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95323d31_7e8a_45cc_b92e_0c57bb75ffa6
EDOP-716437-2016 | 2037309 | 12/2/2016 11:11:27 AM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED055 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | 4 | 4 | Two missing teeth on one combplate . | 4 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | Bottom_egress_combplates.png | file://x:/photopub/docs/0000000525/3c28d6fa-18e0-4617-ad97-6ba167936ad1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ed5fc8e_30ce_43d8_9d09_6ea636fdc219
EDOP-716437-2016 | 2037309 | 12/2/2016 11:11:27 AM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED055 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | 4 | 4 | Two missing teeth on one combplate . | 4 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | Unit_10264.png | file://x:/photopub/docs/0000000525/d86e80c6-9ebc-43fe-bc25-8dc90d07e940.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ed5fc8e_30ce_43d8_9d09_6ea636fdc219
EDOP-716437-2016 | 2037309 | 12/2/2016 11:11:27 AM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED055 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | 4 | 4 | Two missing teeth on one combplate . | 4 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | Top_entrance_combplates.png | file://x:/photopub/docs/0000000525/8f1dbafc-eb23-409d-a26e-733c99259dd2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ed5fc8e_30ce_43d8_9d09_6ea636fdc219
GAUP-723458-2016 | UW-456826-2016 | 12/14/2016 2:11:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA039 | Painting of exterior piping | 1 | 1 | Outdoor black iron piping must be painted to prevent corrosion. | 1 | Painting of exterior piping | Outdoor_piping_unpainted.png | file://x:/photopub/docs/0000000531/54a20bf0-134b-44fc-9d05-c2280b3ac515.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d117ab6_23c1_405b_937c_261af7e79cb3
GAIN-715933-2016 | GA-464909-2016 | 12/14/2016 2:32:43 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Physical protection of gas connector not in place. Certified gas connector can be damaged when appliance on wheels is moved. | 2 | Physical protection of piping and tubing absent. | No_non_combustible_restraint_device.png | file://x:/photopub/docs/0000000531/75a609f3-bbb8-48fa-a53c-f8d3c5605967.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58fc0d53_2726_4148_b3ac_3323a57e3bdc
ELIN-751214-2017 | EL-425810-2016 | 2/6/2017 2:15:56 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #Temp_feeder_cable1.png,Temp_feeder_cable2.png The energized 100 amp 120/240 volt feeder cable fed from temporary service is laid out on floor exposing it to mechanical damage and can lead to a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Temp_feeder_cable1.png | file://x:/photopub/docs/0000000554/b0ecd00c-3ffa-4eb4-aacf-bc5be552d9b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95323d31_7e8a_45cc_b92e_0c57bb75ffa6
ELIN-745382-2017 | EL-289279-2015 | 2/7/2017 11:04:49 AM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Residence_overcurrent_termination.png The 100 amp 120/240 volt consumer service conductors terminated at the main overcurrent device at the residence have had strands cut and removed for termination. The damage caused to the conductor creates a thermal hazard that may exceed temperature termination ratings of the overcurrent device and conductor at the equipment | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Residence_overcurrent_termination.png | file://x:/photopub/docs/0000000554/9ed347dd-0d42-431b-8f42-4e3f264935c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34f64f6c_57e2_4e58_9cd2_3798b93d76bb
BPVOP-724949-2016 | UW-481939-2016 | 12/15/2016 6:18:08 PM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve(s) on this high pressure (80PSIG) air receiver. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_device_.png | file://x:/photopub/docs/0000000531/d0bad249-5f22-4dda-8e5c-6e3248da7f4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfcbcba9_daf7_47bb_93d5_c7133ff13f02
ELIN-715947-2016 | EL-475475-2016 | 12/5/2016 4:23:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | In AC systems,the grounded service conductor is required to be connected to a ground electrode at the supply side of the service disconnect only. This is to prevent neutral currents from circulating through the bonding system and to carry any unbalanced fault currents back to the source. In this installation for a 600A / 600V temporary service in a container, the ground conductor was connected to a bonding lug inside the fused disconnect switch. If an electrical fault was to occur, there is the potential for unbalanced fault currents to flow through the metal of the service switch and create a shock hazard for any persons in contact with the electrical service equipment. | 4 | Installation Grounding; conductor is not continuous. | Inside_container_.png | file://x:/photopub/docs/0000000526/6e3bafef-7aff-4565-a80c-1bd7e71ecb23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e0d6b7f_8aab_4221_907c_76403e43db88
PROP-715798-2016 | PR-469872-2016 | 12/9/2016 8:20:56 AM | ASSESS: PR OP: Annual | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Tag line was not installed, carriage could fall if chainfall failed | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Tag_line_on_tensioning_at_drive.png | file://x:/photopub/docs/0000000528/b73a0768-4b5a-42b7-afb5-f515907d1fd3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d42ff8cf_4314_4bad_89e5_f6bf7e1cad17
GAIN-735723-2017 | GA-225786-2015 | 2/6/2017 12:12:25 PM | ASSESS: GA: Final | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 2 | #Vent.png | 2 | Non compliant Type B Vent Clearance | Vent.png | file://x:/photopub/docs/0000000555/7d17bc00-858d-475d-b91c-38c358fa13be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__976b9d5e_f30b_4119_b39d_4a403226ccdd
GAIN-728853-2016 | GA-465712-2016 | 12/23/2016 11:53:00 AM | ASSESS: GA: Rough-In | png | #asFound | GA120 | Mechanical Air/ventilation supply present, missing interlock | 3 | 3 | The as found condition is an mechanical exhaust fan at the termination of a combustion vent without an interlock with the appliances. Without an interlock, exhaust fan failure will affect the correct venting of appliances and could result in products of combustion remaining within the building envelop and subjecting occupants to carbon monoxide poisoning. | 3 | Mechanical Air/ventilation supply present, missing interlock | Commonvent_with_exhaustfan.png | file://x:/photopub/docs/0000000535/01d28371-e692-4a99-a326-492e32f7b9ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10a87ce3_e85b_47cf_9d98_da748d09d771
ELIN-738568-2017 | EL-490265-2017 | 1/23/2017 12:45:50 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Conduit.png NMD cabling is not approved for use within conduit | 3 | Conductors Equipment is not approved for the specific use. | Conduit.png | file://x:/photopub/docs/0000000547/7b787065-31d5-4058-baa4-a54b3f2d4832.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5a99c12_8e97_4ee1_aab7_fa6ea5f0d761
ELIN-715947-2016 | EL-475475-2016 | 12/5/2016 4:23:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | In AC systems,the grounded service conductor is required to be connected to a ground electrode at the supply side of the service disconnect only. This is to prevent neutral currents from circulating through the bonding system and to carry any unbalanced fault currents back to the source. In this installation for a 600A / 600V temporary service in a container, the ground conductor was connected to a bonding lug inside the fused disconnect switch. If an electrical fault was to occur, there is the potential for unbalanced fault currents to flow through the metal of the service switch and create a shock hazard for any persons in contact with the electrical service equipment. | 4 | Installation Grounding; conductor is not continuous. | Grounds_to_bonding_lug.png | file://x:/photopub/docs/0000000526/1adfa7a0-deb8-4451-8bc0-f9512f110049.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e0d6b7f_8aab_4221_907c_76403e43db88
ELOP-721075-2016 | 1974 | 12/7/2016 2:33:40 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound 34" clearance in front of 1600 amp PDC with single point of egress. | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | #PDC_clearance.png In the main distribution electrical room, the 1600 amp 120/208V distribution equipment has clearance of only 34" in front of it and the room has only one point of egress. Should a fault occur within this equipment a worker in the room may have to pass in front of the equipment to exit the room, putting them at risk of possible arc flash injury. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | PDC_clearance.png | file://x:/photopub/docs/0000000541/517b6bdf-7d99-4044-a52b-1a6e30cf060f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10486618_6a24_4788_8acf_549bf484fd6a
BPVIN-742901-2017 | BPV-493350-2017 | 1/20/2017 6:34:15 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP212 | 5.1.1 Work done: unqualified ind - Repair or alteration done by unlicensed contractor or unqualified individual | 3 | 3 | #Air,After_Welding.png During the inspection of an Machine Mounted Air Receiver with MAWP of 150 PSIg a small crack was found at the toe of the leg to vessel weld. I asked the owner to carefully remove the crack and confirm it with Magnetic Testing. They ground too much and removed material off the vessel then welded the excavation without approval. This can contribute to the failure of the vessel. | 3 | 5.1.1 Work done: unqualified ind - Repair or alteration done by unlicensed contractor or unqualified individual | After_Welding.png | file://x:/photopub/docs/0000000546/6ba9979d-3af9-454b-8fa5-09cf55de947b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c7a1182_fede_44dd_a996_ce8e84e9aae2
ELIN-714770-2016 | EL-474662-2016 | 12/5/2016 2:08:45 PM | ASSESS: EL: Final | png | #asFound Found several luminaires removed and terminations and splicing was done without use of junction boxes and covers with boxes and cables supported. FSR did this work intentionally for temporary wiring use. ESO asked if temporary wiring meant it is a lesser standard of wiring and is it cetaceans by code to have exposed energized conductors and FSR said and agreed this wiring was not safe or compliant with the code and would disconnect it and make it safe and disconnected immediately. ESO asked if FSR put in inspection request for authorizing this for connection to the power supply system before the connection was made. FSR said no he did not request inspection for connection of electrical Equipment. ESO said that the electrical equipment is therefore not authorized for connection to the power supply system. | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #energized_exposed_conductors_spliced__intentionally_for_lighting_use1.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use2.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use3.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use4.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use5.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use6.png Found energized exposed conductor splicing done without installation and use of junction box with cover installed and supported as required for energized electrical equipment. When electrical equipment is exposed and energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | energized_exposed_conductors_spliced__intentionally_for_lighting_use1.png | file://x:/photopub/docs/0000000545/4146f955-c10c-4b71-8e9b-870947b9c355.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01de70d4_166f_46a8_88b8_f7f8860fc3e7
ELIN-743695-2017 | EL-482879-2016 | 1/23/2017 12:38:58 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 4 | #Box_ceiling.png Ceiling boxes installed are not rated for use with ceiling fans | 4 | Installation of electrical equipment Fixtures without suitable support. | Box_ceiling.png | file://x:/photopub/docs/0000000547/e13bc4fe-c5b5-4f17-ad42-e9211ec3641d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7ddc943_bf36_4a1b_8d89_8ad9940a4575
ELIN-716658-2016 | EL-443816-2016 | 12/6/2016 10:39:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | 120/240 volt non-metallic cable in contact with heating source. This could cause equipment damage. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD90_in_contact_with_heating_source.png | file://x:/photopub/docs/0000000527/d8d40d35-5b7b-476c-998d-ff2a16be7301.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d36e92b2_a39a_4958_bab8_34e2a7cbc11e
GAIN-726767-2016 | GA-482860-2016 | 12/20/2016 3:50:46 PM | ASSESS: GA: Rough-In | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | The hazard is 3 close nipples installed on meter piping. It is hazardous because close nipples lack strength and could break under force. | 3 | Non-compliant material/fittings installed | Close_nipple.png | file://x:/photopub/docs/0000000533/ecedd973-40f9-40a1-ba61-c659c096b5da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9001673_b97f_485a_af1c_49bc49cecebb
GAHE-727312-2016 | HE-483622-2016 | 12/20/2016 2:01:07 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | The hazard was 4 x 100 pound propane cylinders which had been installed less than 10 feet from a source of ignition. This is a hazard because if the propane cylinders were to relieve, the propane gas could be ignited by the source of ignition. | 3 | Clearance to combustibles not maintained | Temp_heater.png | file://x:/photopub/docs/0000000533/29ef1046-e7ab-4d41-8ab4-feb1ca546795.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8448f5fe_3425_47d0_83ab_eb311844d143
GAIN-717023-2016 | GA-476216-2016 | 12/16/2016 11:08:10 AM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Shut-off_valve_bent_from_contact.png | file://x:/photopub/docs/0000000533/f2772125-198f-4307-be6f-58793db1f72d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f363ddb_53fb_4311_9115_e7edfd1bc355
GAIN-694114-2016 | GA-458696-2016 | 12/16/2016 2:34:18 PM | ASSESS: GA: Final | png | #asFound | GA113 | Special/ positive vent system undersized for the length of run/elbows but appliance operates | 2 | 2 |  | 2 | Special/ positive vent system undersized for the length of run/elbows but appliance operates | Incorrect_vent_design_.png | file://x:/photopub/docs/0000000533/c340d241-df4d-4e74-b989-69c11f6590cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63617f8f_5330_442a_9724_67353b547826
ELIN-714770-2016 | EL-474662-2016 | 12/5/2016 2:08:45 PM | ASSESS: EL: Final | png | #asFound Found several luminaires removed and terminations and splicing was done without use of junction boxes and covers with boxes and cables supported. FSR did this work intentionally for temporary wiring use. ESO asked if temporary wiring meant it is a lesser standard of wiring and is it cetaceans by code to have exposed energized conductors and FSR said and agreed this wiring was not safe or compliant with the code and would disconnect it and make it safe and disconnected immediately. ESO asked if FSR put in inspection request for authorizing this for connection to the power supply system before the connection was made. FSR said no he did not request inspection for connection of electrical Equipment. ESO said that the electrical equipment is therefore not authorized for connection to the power supply system. | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #energized_exposed_conductors_spliced__intentionally_for_lighting_use1.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use2.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use3.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use4.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use5.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use6.png Found energized exposed conductor splicing done without installation and use of junction box with cover installed and supported as required for energized electrical equipment. When electrical equipment is exposed and energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | energized_exposed_conductors_spliced__intentionally_for_lighting_use2.png | file://x:/photopub/docs/0000000545/78ec6ac4-d045-4a1d-928f-36d53e788af0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01de70d4_166f_46a8_88b8_f7f8860fc3e7
ELIN-714770-2016 | EL-474662-2016 | 12/5/2016 2:08:45 PM | ASSESS: EL: Final | png | #asFound Junction box and cover missing for live wires | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #energized_exposed_conductors_spliced__intentionally_for_lighting_use1.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use2.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use3.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use4.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use5.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use6.png Found energized exposed conductor splicing done without installation and use of junction box with cover installed and supported as required for energized electrical equipment. When electrical equipment is exposed and energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | energized_exposed_conductors_spliced__intentionally_for_lighting_use5.png | file://x:/photopub/docs/0000000545/8039eeb3-f9a5-4bed-bfe4-0abf77cfc450.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01de70d4_166f_46a8_88b8_f7f8860fc3e7
ELIN-714770-2016 | EL-474662-2016 | 12/5/2016 2:08:45 PM | ASSESS: EL: Final | png | #asFound Junction box and cover missing for live wires | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #energized_exposed_conductors_spliced__intentionally_for_lighting_use1.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use2.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use3.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use4.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use5.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use6.png Found energized exposed conductor splicing done without installation and use of junction box with cover installed and supported as required for energized electrical equipment. When electrical equipment is exposed and energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | energized_exposed_conductors_spliced__intentionally_for_lighting_use3.png | file://x:/photopub/docs/0000000545/1eef6a87-74c4-4d36-bb39-d94e28ebed82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01de70d4_166f_46a8_88b8_f7f8860fc3e7
ELIN-714770-2016 | EL-474662-2016 | 12/5/2016 2:08:45 PM | ASSESS: EL: Final | png | #asFound no support of cables | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #energized_exposed_conductors_spliced__intentionally_for_lighting_use1.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use2.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use3.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use4.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use5.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use6.png Found energized exposed conductor splicing done without installation and use of junction box with cover installed and supported as required for energized electrical equipment. When electrical equipment is exposed and energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | energized_exposed_conductors_spliced__intentionally_for_lighting_use4.png | file://x:/photopub/docs/0000000545/f689c332-12c9-44e5-b6f3-e7b8bd2f04cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01de70d4_166f_46a8_88b8_f7f8860fc3e7
ELIN-714770-2016 | EL-474662-2016 | 12/5/2016 2:08:45 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #energized_exposed_conductors_spliced__intentionally_for_lighting_use1.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use2.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use3.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use4.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use5.png,energized_exposed_conductors_spliced__intentionally_for_lighting_use6.png Found energized exposed conductor splicing done without installation and use of junction box with cover installed and supported as required for energized electrical equipment. When electrical equipment is exposed and energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | energized_exposed_conductors_spliced__intentionally_for_lighting_use6.png | file://x:/photopub/docs/0000000545/3fcc6b94-ce7b-4206-a47c-6e1d4bfe9ee3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01de70d4_166f_46a8_88b8_f7f8860fc3e7
GAWP-741250-2017 | GA-413929-2016 | 1/18/2017 2:40:02 PM | ASSESS: GA Work In Progress | png | #asFound PP venting on Cat 1 appliance | GA105 | Unapproved venting material | 3 | 3 | #Pp_venting_on_Cat1.png The as found condition is a water heater installed with incorrect venting material. The hazard is that the plastic venting installed on the appliance could be compromised by the high heat of the flue gas, resulting in damage to the vent and the release of harmful products of combustion into a living area | 3 | Unapproved venting material | Pp_venting_on_Cat1.png | file://x:/photopub/docs/0000000545/140569e3-0a3d-41e5-acc1-a1c194502249.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4594f3af_9c78_42a6_a336_344f4a4eefb7
ELIN-742652-2017 | EL-490046-2017 | 1/23/2017 10:07:49 AM | ASSESS: EL: Service Connection | png | #asFound No fault rating on label of disconnect switch | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #rating_of_switch.png Service connection for new temporary construction service. The configuration of the service does not meet with BC Hydro guidelines for secondary services. A modified disconnect switch does not bear a fault rating and therefore, may not withstand a fault on the system. Shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | rating_of_switch.png | file://x:/photopub/docs/0000000546/3d3bb98c-6f8f-452a-9a0e-b7f5702308bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b357599_9d65_459f_bffd_2b4f7504cead
ELIN-740916-2017 | EL-491463-2017 | 1/19/2017 11:28:15 AM | ASSESS: EL: Service Connection | png | #asFound Tree limb in close contact to triplex, once the triplex is relocated it will be in contact with a tree limb | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Photos_of__Photos_of_electrical_service_and_tree1.png,Photos_of__Photos_of_electrical_service_and_tree2.png Once the triplex is relocated to the temporary construction service the triplex will be in contact with a tree limb. Wearing down of the cable insulation is likely by the tree limb, which will cause the tree to become energized there by electrifying the area and possibly electrocuting anyone who walks near the tree. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Photos_of__Photos_of_electrical_service_and_tree1.png | file://x:/photopub/docs/0000000545/74c8dc20-986b-49fc-acdc-1bd81fa02f31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca8f9885_e7d7_4899_b6d0_6bc6f2dfff51
ELIN-740916-2017 | EL-491463-2017 | 1/19/2017 11:28:15 AM | ASSESS: EL: Service Connection | png | #asFound As found condition on the electrical service | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Photos_of__Photos_of_electrical_service_and_tree1.png,Photos_of__Photos_of_electrical_service_and_tree2.png Once the triplex is relocated to the temporary construction service the triplex will be in contact with a tree limb. Wearing down of the cable insulation is likely by the tree limb, which will cause the tree to become energized there by electrifying the area and possibly electrocuting anyone who walks near the tree. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Photos_of__Photos_of_electrical_service_and_tree2.png | file://x:/photopub/docs/0000000545/9bf7ce9b-1ddc-41ea-b318-7a7fc29e2365.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca8f9885_e7d7_4899_b6d0_6bc6f2dfff51
ELIN-738007-2017 | EL-486665-2017 | 1/14/2017 10:03:54 AM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #Meter_base_has_been_mounted_to_pole_using_OSB_plywood.png Meter base has been mounted on pole using OSB plywood. The plywood will not withstand the weather conditions to which it will be exposed causing it to deteriorate over time and the meter base could come loose from the pole. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Meter_base_has_been_mounted_to_pole_using_OSB_plywood.png | file://x:/photopub/docs/0000000549/7678af1f-f0f5-4d7e-97a2-840f9be9b7b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__870ecd17_7073_4cdd_ae6a_8dc0b7f21302
ELIN-733744-2017 | EL-486504-2017 | 1/13/2017 4:15:26 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Grounding_conductor_connected_in_distribution_side_of_combination_panel_.png Neutral has been connected to ground on the load side of the main disconnect. Connection of the neutral to ground must not be made at any point beyond the supply side of the service disconnect. This ensures there are no neutral currents circulating through the bonding system on the load side of the service disconnecting means. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Grounding_conductor_connected_in_distribution_side_of_combination_panel_.png | file://x:/photopub/docs/0000000549/fb53c562-d6b8-44ff-9ba0-40d92531297c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3011a165_44b3_411e_b162_1af26f65a5eb
ELOP-714851-2016 | EL-240331-2015 | 12/8/2016 3:49:47 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Male end of cord attached to bare energized conductors | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 320_Ewan_001.png | file://x:/photopub/docs/0000000536/17be9378-e7ff-46f4-9da3-7978596d504e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72979db4_be51_4bec_b8db_3ba049985794
ELIN-744681-2017 | EL-443088-2016 | 1/31/2017 10:05:24 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Exterior_receptacles_1.png,Exterior_receptacles_2.png The 15 amp 120 volt GFCI protected exterior receptacles do not include in-use covers and this could lead to moisture entering the enclosure with an extension cord inserted by-passing the GFCI protection, this could lead to a shock hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Exterior_receptacles_2.png | file://x:/photopub/docs/0000000551/292e2985-2ba4-4f00-9678-140ce98769b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ea3f328_d73d_43ee_91b2_9af08e526220
ELIN-744681-2017 | EL-443088-2016 | 1/31/2017 10:05:24 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Exterior_receptacles_1.png,Exterior_receptacles_2.png The 15 amp 120 volt GFCI protected exterior receptacles do not include in-use covers and this could lead to moisture entering the enclosure with an extension cord inserted by-passing the GFCI protection, this could lead to a shock hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Exterior_receptacles_1.png | file://x:/photopub/docs/0000000551/c6ff61e7-b661-4a3f-8b3b-e5c9451e7ddc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ea3f328_d73d_43ee_91b2_9af08e526220
GAIN-750104-2017 | GA-370276-2016 | 2/2/2017 8:04:26 AM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Dan_webb1.png,Dan_webb2.png No enough combustion can cause the appliance to create carbon monoxide and cause co poisoning to the occupants. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Dan_webb1.png | file://x:/photopub/docs/0000000552/0343e7c5-d572-4050-947a-f003cce3436d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eeb48ccd_7e78_423e_b998_600dbf48c390
GAIN-750104-2017 | GA-370276-2016 | 2/2/2017 8:04:26 AM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Dan_webb1.png,Dan_webb2.png No enough combustion can cause the appliance to create carbon monoxide and cause co poisoning to the occupants. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Dan_webb2.png | file://x:/photopub/docs/0000000552/e3a3dc3b-afa5-46e5-8db4-d4602873faf3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eeb48ccd_7e78_423e_b998_600dbf48c390
BPVOP-752362-2017 | 2265732 | 2/6/2017 2:03:43 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP212 | 5.1.1 Work done: unqualified ind - Repair or alteration done by unlicensed contractor or unqualified individual | 3 | 3 | #Repair_work_1.png,Repair_work_2.png,Repair_work_3.png,Repair_work_4.png,Contractor.png A person must hold a contractors license in order to perform regulated work. I found repair work was done by an individual, who did not possess a boiler contractors licence for work carried out on a 30psi hot water boiler.This can result in an incident due to the unlicensed individual is unfamiliar of the code requirements for the scope of work performed. | 3 | 5.1.1 Work done: unqualified ind - Repair or alteration done by unlicensed contractor or unqualified individual | Contractor.png | file://x:/photopub/docs/0000000555/00c07ddb-50e1-468c-b329-5b67f07157cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d11dd77_6739_4f8f_a2eb_a6673ef28fbd
GAHE-742794-2017 | HE-493251-2017 | 1/20/2017 2:57:14 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA112 | Leaking or Failing special venting system (Carbon Monoxide present in space) | 5 | 5 | #Venting.png The as found condition is a damaged and incorrectly installed vent system serving two natural draft appliances is spilling products of combustion into the structure within which they are installed. The as found hazard is products of combustion from gas burning appliances subjects inhabitants of the structure to Carbon Monoxide, potentially leading to serious injury or death. | 5 | Leaking or Failing special venting system (Carbon Monoxide present in space) | Venting.png | file://x:/photopub/docs/0000000546/f039f875-3f4b-4734-b56d-bb5a0436300c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f153dab_fd52_4fe4_b0b3_b6259a2ba522
ELIN-735493-2017 | EL-220462-2015 | 1/12/2017 1:46:40 PM | ASSESS: EL: Final | png | #asFound Missing knock out filler in 600 volt panel. | EL000 | No Created Hazard Identified | 0 | 0 | #6.png 600 volt panel with knock out filler missing. This is a shock hazard, as an individual could come into contact with live electrical equipment. | 0 | No Created Hazard Identified | 6.png | file://x:/photopub/docs/0000000542/fd4fcc9c-28d2-4703-b713-a514566ab187.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67f51512_25de_4a44_bff1_b787f9c234df
ELIN-754422-2017 | EL-480058-2016 | 2/9/2017 2:49:55 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Main_Panel_Construction_Use.png A new 200 amp 120/240 volt Panel is located in a home under construction but has not been provided with weather and mechanical protection. This poses a hazard to the equipment but also to persons using the panel. The panel is also not protected from unauthorized persons, and this could pose a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_Panel_Construction_Use.png | file://x:/photopub/docs/0000000556/939a06e7-1aaf-41ff-bf57-6672ae743869.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb85d3ad_3171_481e_9b55_026bd2adcc26
ELIN-725882-2016 | EL-446239-2016 | 1/3/2017 2:56:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | A new duplex with a 200 amp 240 volt service is being constructed. The service cables are installed leaving 3 plus meters of unprotected service conductors lacking effective over current protection to both the main house and suite panel boards. These conductors are to be limited in length to a maximum of 1.5 meters to reduce the potential for conductor damage that could lead to property damage or injury to persons. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Total_of_3_to_3_1_meters_service_cable_main_house_panel_and_suite_panel_feeders.png | file://x:/photopub/docs/0000000538/acee2f79-eaa8-4f97-af6c-52c770e8c38f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78c61765_6e95_4127_9eb4_7147ad3cf773
ELIN-756298-2017 | EL-425810-2016 | 2/15/2017 12:28:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #NMSC_cabling1.png,NMSC_cabling2.png,NMSC_cabling3.png,NMSC_cabling4.png The use of 3c#8cu NMSC as portable cable in one feeder, and 3c#8cu NMSC 'permanent' wiring connected to temporary service power c/w exposed NMSC laying on the surface floor on second location exposes the cabling to mechanical damage and can lead to both a thermal and a shock hazard | 3 | Conductors Equipment is not approved for the specific use. | NMSC_cabling4.png | file://x:/photopub/docs/0000000557/0d3e7749-a563-4dbb-b34c-07c72a5ea11e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cba62003_9a5c_4401_ab87_88386e6aebe3
ELIN-756298-2017 | EL-425810-2016 | 2/15/2017 12:28:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #NMSC_cabling1.png,NMSC_cabling2.png,NMSC_cabling3.png,NMSC_cabling4.png The use of 3c#8cu NMSC as portable cable in one feeder, and 3c#8cu NMSC 'permanent' wiring connected to temporary service power c/w exposed NMSC laying on the surface floor on second location exposes the cabling to mechanical damage and can lead to both a thermal and a shock hazard | 3 | Conductors Equipment is not approved for the specific use. | NMSC_cabling1.png | file://x:/photopub/docs/0000000557/b032fbf7-c65a-40e1-b3a6-7098a43c859d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cba62003_9a5c_4401_ab87_88386e6aebe3
ELIN-756298-2017 | EL-425810-2016 | 2/15/2017 12:28:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #NMSC_cabling1.png,NMSC_cabling2.png,NMSC_cabling3.png,NMSC_cabling4.png The use of 3c#8cu NMSC as portable cable in one feeder, and 3c#8cu NMSC 'permanent' wiring connected to temporary service power c/w exposed NMSC laying on the surface floor on second location exposes the cabling to mechanical damage and can lead to both a thermal and a shock hazard | 3 | Conductors Equipment is not approved for the specific use. | NMSC_cabling2.png | file://x:/photopub/docs/0000000557/40571fdb-b9a6-4dde-adf6-2c29f4520796.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cba62003_9a5c_4401_ab87_88386e6aebe3
BPVIN-728698-2016 | BPV-442808-2016 | 12/21/2016 12:00:39 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 | Safety valve installed with the spindle in horizontal position this is not in accordance with code and manufactures requirements which may contribute to an incident. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Safety_valve_in_horizontal_position.png | file://x:/photopub/docs/0000000534/1e4ad060-bfd1-4d0d-836c-41b75d929375.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed3fe966_77d5_44f7_8d3f_6fce4996e344
BPVIN-728698-2016 | BPV-442808-2016 | 12/21/2016 12:00:39 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 | Safety valve installed with the spindle in horizontal position this is not in accordance with code and manufactures requirements which may contribute to an incident. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Boiler_nameplate.png | file://x:/photopub/docs/0000000534/cf63e46e-7d06-46ad-88a8-000e06af8d8d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed3fe966_77d5_44f7_8d3f_6fce4996e344
BPVIN-728698-2016 | BPV-442808-2016 | 12/21/2016 12:00:39 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 | Safety valve installed with the spindle in horizontal position this is not in accordance with code and manufactures requirements which may contribute to an incident. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Boiler_general_view.png | file://x:/photopub/docs/0000000534/a5797699-3bb7-4a15-84a4-d1e26168563a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed3fe966_77d5_44f7_8d3f_6fce4996e344
ELIN-742693-2017 | EL-346283-2016 | 1/23/2017 12:17:41 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #P8.png Fire hazard from possible mechanical damage to non metallic sheathed cable insulation. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | P8.png | file://x:/photopub/docs/0000000546/28315413-92f7-4cc5-a998-a95a157ba913.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96beddb0_0ddb_4a41_88f1_e2c2eac7aab3
GAHE-750160-2017 | HE-497536-2017 | 2/1/2017 6:56:41 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | #Excess.png Black iron nipple installed into propane tank opening, no excess flow or internal safety control. In the event of a pipe breakage there would be no restriction to control the release of propane. | 4 | Missing mandatory safety controls | Excess.png | file://x:/photopub/docs/0000000551/3795ed61-d1d3-4e37-88ec-13e69e8f5172.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31e23d89_db21_49b9_94e8_acb4a604c79a
ELIN-720657-2016 | EL-352988-2016 | 12/9/2016 2:24:02 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | Boxes larger than 100mm in dimension are required to be supported on two sides of the box. This is required to support the box and the devices connected to them to prevent the box from moving or becoming detached from the structure. This installation for a new triplex residential building under construction has range and dryer outlet boxes that are not supported on two sides of the box. Left uncorrected this is a potential fire and shock hazard if boxes become detached from their supports and wiring is damaged from strain where it is connected to the box and the devices. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Dryer_box_supported_on_one_side_only__.png | file://x:/photopub/docs/0000000529/ef46141b-3228-4f20-b811-a92d2808ceb6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bcd5cf1_5e16_4fd6_a160_8ba6c12c03e1
ELIN-756298-2017 | EL-425810-2016 | 2/15/2017 12:28:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #NMSC_cabling1.png,NMSC_cabling2.png,NMSC_cabling3.png,NMSC_cabling4.png The use of 3c#8cu NMSC as portable cable in one feeder, and 3c#8cu NMSC 'permanent' wiring connected to temporary service power c/w exposed NMSC laying on the surface floor on second location exposes the cabling to mechanical damage and can lead to both a thermal and a shock hazard | 3 | Conductors Equipment is not approved for the specific use. | NMSC_cabling3.png | file://x:/photopub/docs/0000000557/574489d3-5fab-4481-b696-2ab960487cfd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cba62003_9a5c_4401_ab87_88386e6aebe3
ELIN-750217-2017 | UW-497560-2017 | 2/2/2017 2:46:19 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 4 | #Light_Fixtures1.png,Light_Fixtures2.png 15 amp 120 volt energized light fixtures are hanging from the connection wiring and are not supported to the outlet box. This poses a shock hazard to persons and potential damage to the fixture and wiring. | 4 | Installation of electrical equipment Fixtures without suitable support. | Light_Fixtures2.png | file://x:/photopub/docs/0000000552/d4d64ae7-0310-453a-b437-29e7c68852db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2f40676_ede1_4f9e_9534_7e41d02cd67b
ELIN-750217-2017 | UW-497560-2017 | 2/2/2017 2:46:19 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 4 | #Light_Fixtures1.png,Light_Fixtures2.png 15 amp 120 volt energized light fixtures are hanging from the connection wiring and are not supported to the outlet box. This poses a shock hazard to persons and potential damage to the fixture and wiring. | 4 | Installation of electrical equipment Fixtures without suitable support. | Light_Fixtures1.png | file://x:/photopub/docs/0000000552/3a86f3a2-bec5-4db7-850b-486db8962228.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2f40676_ede1_4f9e_9534_7e41d02cd67b
BPVOP-743891-2017 | 2294183 | 1/23/2017 1:39:47 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | #Overdue_and_under-capacity.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 1997 and was under capacity as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Overdue_and_under-capacity.png | file://x:/photopub/docs/0000000546/f1c5d05b-d507-42a0-bf19-53190daa9629.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc420bc1_b392_481e_b177_6f6c559ae0ee
BPVOP-743880-2017 | 2994142 | 1/23/2017 4:33:52 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #manuf_in_1998.png Upon the assessment of an Electric Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 1998 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | manuf_in_1998.png | file://x:/photopub/docs/0000000546/77d40d9e-36be-489e-bc14-99ef5ad73010.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab8d25a8_15af_46a3_a8d4_d68a95c1da9f
BPVOP-743882-2017 | 2984926 | 1/23/2017 2:55:46 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Manuf_year_20041.png,Manuf_year_20042.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 2004 and was overdue as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Manuf_year_20042.png | file://x:/photopub/docs/0000000546/ddc6d284-26a5-48cf-96dc-d4a1a185f5d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48fddaf2_6194_4ce1_b643_dbafa2c49097
BPVOP-743885-2017 | 2294179 | 1/23/2017 5:56:17 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Manufact_2007.png Upon the assessment of a Hot Water Boiler with MAWP of 50 psig, was found that the Safety Relief Valve was installed in 2007 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Manufact_2007.png | file://x:/photopub/docs/0000000546/982ebcd3-4729-4f35-be1c-b31e80cc5dc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__375a4456_8db1_45e8_b80a_301f0edab8c6
BPVOP-743882-2017 | 2984926 | 1/23/2017 2:55:46 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Manuf_year_20041.png,Manuf_year_20042.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 2004 and was overdue as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Manuf_year_20041.png | file://x:/photopub/docs/0000000546/6e9ac777-b638-401e-a1aa-f3a3df8a4362.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48fddaf2_6194_4ce1_b643_dbafa2c49097
BPVOP-743889-2017 | 2294177 | 1/23/2017 5:26:15 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Manuf_in_2007.png Upon the assessment of a Hot Water Boiler with MAWP of 50 psig, was found that the Safety Relief Valve was installed in 1998 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Manuf_in_2007.png | file://x:/photopub/docs/0000000546/9ee9f8ba-bf96-42b1-bb60-245dd71e6a54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8f869be_fa58_413f_a062_e1a735171976
BPVOP-743879-2017 | 2294181 | 1/23/2017 6:49:39 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Manufactured_2007.png Upon the assessment of a Hot Water Boiler with MAWP of 50 psig, was found that the Safety Relief Valve was installed in 2007 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Manufactured_2007.png | file://x:/photopub/docs/0000000546/252f93e6-f600-4517-b696-d3c57b3f8ebd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3fcee1e4_90f4_4b61_aae4_e1e8df4ae2a0
GAHE-750144-2017 | HE-497530-2017 | 2/1/2017 7:18:55 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | #T1.png,T2.png 500 USWG propane tank installed approximately 2 feet away from dwelling and point of egress. In the event of a fire or leak, propane could enter the dwelling causing fire or explosion | 2 | Installation clearances or set backs to propane containers not met | T1.png | file://x:/photopub/docs/0000000551/920ed57b-72fb-4b91-bde0-bcb7a1bc9f17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf75cf43_e5bb_4efe_bc96_25236b513f8e
GAHE-750144-2017 | HE-497530-2017 | 2/1/2017 7:18:55 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | #T1.png,T2.png 500 USWG propane tank installed approximately 2 feet away from dwelling and point of egress. In the event of a fire or leak, propane could enter the dwelling causing fire or explosion | 2 | Installation clearances or set backs to propane containers not met | T2.png | file://x:/photopub/docs/0000000551/3b3a9818-d20c-4bad-a90e-c9bfc3828bf2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf75cf43_e5bb_4efe_bc96_25236b513f8e
BPVOP-743115-2017 | 2257982 | 1/21/2017 9:20:41 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 | #Minor_scale.png | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | Minor_scale.png | file://x:/photopub/docs/0000000546/1104172d-3fb7-4970-b3a2-f2c4f2cc3189.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb597e2f_fbb1_48c8_99e4_d5de6439bf51
GAIN-752226-2017 | GA-494666-2017 | 2/8/2017 10:19:06 AM | ASSESS: GA: Final | png | #asFound Unvented agricultural heater installed in area used for human occupancy. | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Chore_time_heater.png Unvented heater designed for use in livestock barns installed in an area used for human occupancy with inadequate ventilation. This may result in asphyxiation or carbon monoxide poisoning to the occupants of the space. | 3 | Appliance not installed according to installation instructions | Chore_time_heater.png | file://x:/photopub/docs/0000000555/f949acb1-6840-4831-8c33-1fce8cce4556.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d23fd748_6819_4877_a571_6acf31cec172
ELIN-720657-2016 | EL-352988-2016 | 12/9/2016 2:24:02 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | Boxes larger than 100mm in dimension are required to be supported on two sides of the box. This is required to support the box and the devices connected to them to prevent the box from moving or becoming detached from the structure. This installation for a new triplex residential building under construction has range and dryer outlet boxes that are not supported on two sides of the box. Left uncorrected this is a potential fire and shock hazard if boxes become detached from their supports and wiring is damaged from strain where it is connected to the box and the devices. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Dryer_box_supported_on_one_side_only_.png | file://x:/photopub/docs/0000000529/9306e8c7-32ff-45e4-b7d2-a0525bb2106b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bcd5cf1_5e16_4fd6_a160_8ba6c12c03e1
ELIN-720657-2016 | EL-352988-2016 | 12/9/2016 2:24:02 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | Boxes larger than 100mm in dimension are required to be supported on two sides of the box. This is required to support the box and the devices connected to them to prevent the box from moving or becoming detached from the structure. This installation for a new triplex residential building under construction has range and dryer outlet boxes that are not supported on two sides of the box. Left uncorrected this is a potential fire and shock hazard if boxes become detached from their supports and wiring is damaged from strain where it is connected to the box and the devices. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Dryer_box_supported_on_one_side_only.png | file://x:/photopub/docs/0000000529/125958ac-f70b-462c-8d66-7a61fa0b80f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bcd5cf1_5e16_4fd6_a160_8ba6c12c03e1
ELIN-739518-2017 | EL-486227-2017 | 1/17/2017 11:52:11 AM | ASSESS: EL: Service Connection | png | #asFound Service mast with only 2 support clamps and is without a guy wire support. | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #1.png Service mast do not have adequate support. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 1.png | file://x:/photopub/docs/0000000544/9932734c-3b40-4192-8c81-31bae379e21f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45abef11_0963_460e_9873_adde7a08f47a
ELHE-727826-2016 | HE-483669-2016 | 1/17/2017 1:53:09 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #11.png,12.png,13.png Outlets and junction boxes without covers may cause shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 13.png | file://x:/photopub/docs/0000000544/feb26456-7374-4d64-a0e0-c296eefd3ae9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__549742c5_ff97_40c4_8d8c_85bae0fe574f
ELHE-727826-2016 | HE-483669-2016 | 1/17/2017 1:53:09 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #11.png,12.png,13.png Outlets and junction boxes without covers may cause shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 12.png | file://x:/photopub/docs/0000000544/4070524b-a9c9-4ed0-8f31-5372d776e6eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__549742c5_ff97_40c4_8d8c_85bae0fe574f
ELHE-727826-2016 | HE-483669-2016 | 1/17/2017 1:53:09 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Outlets and boxes without covers. | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #11.png,12.png,13.png Outlets and junction boxes without covers may cause shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 11.png | file://x:/photopub/docs/0000000544/4cb2ee0b-266d-4014-95ec-4d9b87a862b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__549742c5_ff97_40c4_8d8c_85bae0fe574f
BPVOP-743888-2017 | 2294187 | 1/23/2017 2:05:43 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #T__P.png Upon the assessment of a DHW Tank with MAWP of 150 psig, was found that the Safety Relief Valve was installed in 1997 and was overdue as per CSA B51. This can contribute to the failure of the Safety Relief Valve. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | T__P.png | file://x:/photopub/docs/0000000546/c1293c2c-4582-4682-8b2a-f7f5d98595a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76a73336_4d10_4b85_8b80_c8a99c5786f2
BPVOP-743884-2017 | 2294185 | 1/23/2017 1:58:52 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #T_and_P.png Upon the assessment of a DHW Storage Tank with MAWP of 150 psig, was found that the T&P relief valve was installed in 1997 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | T_and_P.png | file://x:/photopub/docs/0000000546/8bd8371e-5f0e-407a-8cbe-491b256f73a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b5a7a19_04b7_4d40_b3eb_397196f7722e
ELIN-754829-2017 | EL-427561-2016 | 2/10/2017 10:21:15 AM | ASSESS: EL: Service Connection | png | #asFound Long barrel lugs are approved for use on copper conductors only, used on aluminum conductors | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Copper_rated_long_barrel_lugs.png Aluminum conductors are spliced with long barrel lugs that are not approved for use on aluminum | 3 | General Equipment is not approved for the specific use | Copper_rated_long_barrel_lugs.png | file://x:/photopub/docs/0000000556/0b0f76b5-4e8d-4f88-9e55-2b5717402762.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64446250_ea47_404c_8b88_644c08d290ad
GAIN-723105-2016 | GA-480483-2016 | 12/21/2016 12:05:42 PM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | 2 stage propane regulator was installed in a manner that allowed liquified propane in the supply line to drain towards the regulator. These regulators are designed to regulate vapour only. Liquid propane could damage the regulator and cause an over pressure situation feeding appliances downstream. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Frosty_propane_reg_.png | file://x:/photopub/docs/0000000534/df8458bd-8a8c-4e5d-bef4-1f1cf0ac9397.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0728e59e_4569_40ff_9414_b7529a5ee7d1
ELOP-734618-2017 | EL-468688-2016 | 1/23/2017 9:59:38 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound Sorry, did not notice until later that I did not capture the 8 inch wide by 5 inch high curb and 2 x 6 and 2 x 4 concrete forms located in the secure footing area. Have only asked for removal of forms which are contributing to unstable surface for footing in front of equipment. | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | #Main_distribution_with_large_curb_and_concrete_forms_in_secure_footing_area_in_front_of_PDC.png A 1200 amp 208 volt 3 phase service has been installed in a new commercial building. The area in front of the main service equipment has obstructions for the secure footing space in front of the equipment, including concrete forms, which provide an unstable area for persons working on or interacting with the equipment. This non compliance can lead to injury to persons. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Main_distribution_with_large_curb_and_concrete_forms_in_secure_footing_area_in_front_of_PDC.png | file://x:/photopub/docs/0000000547/55ac5c7e-ea09-49f1-9fde-88cf21724577.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__CD38281E_2C8B_4F45_853A_9B23B3F54112
ELIN-735632-2017 | EL-329973-2015 | 1/23/2017 12:07:32 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Main_service_panel_in_wet_location.png A new 200 amp 240 volt consumer service has been placed in a building housing livestock. the dry location panel board is located just inside the perimeter of the roof line and is exposed to the weather and the location is considered a wet location. Overcurrent devices can be damaged by ingress of water into the equipment. Wetted overcurrent protection may not react when required in instances where required to do so and lead to property damage or injury to persons or livestock | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Main_service_panel_in_wet_location.png | file://x:/photopub/docs/0000000547/60186662-7c5a-4013-b241-e9a81e541b49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d86f928e_435a_4153_9a67_e29ea07499f6
ELIN-738720-2017 | EL-439747-2016 | 1/13/2017 5:09:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | #Grd.png The main service neutral has not been terminated correctly and this could result in a potential voltage rise being imposed on the neutral conductor leading to an electric shock or equipment in use electrical shorting do to voltage spikes. | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Grd.png | file://x:/photopub/docs/0000000543/bc9a1bd2-89f4-4ece-8e3b-ea163b7fdb21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a99e297_16bd_4863_a8b8_a4189787b0c5
GAUP-743958-2017 | UW-493785-2017 | 1/23/2017 6:24:50 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA149 | Gas log set installed with damper not permanently secured in open position | 4 | 4 | #Propane_system1.png,Propane_system2.png The as found hazard was a gas log set which had been installed within a wood burning fireplace without having the damper secured in the open position. This is a hazard because if the damper were to be closed and the log set energized the products of combustion containing carbon monoxide would enter the home. | 4 | Gas log set installed with damper not permanently secured in open position | Propane_system2.png | file://x:/photopub/docs/0000000547/35c9c656-9c65-474a-b7bb-fee60ac7c06c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34c8533e_922a_4717_b644_244611a94fc8
GAUP-743958-2017 | UW-493785-2017 | 1/23/2017 6:24:50 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA149 | Gas log set installed with damper not permanently secured in open position | 4 | 4 | #Propane_system1.png,Propane_system2.png The as found hazard was a gas log set which had been installed within a wood burning fireplace without having the damper secured in the open position. This is a hazard because if the damper were to be closed and the log set energized the products of combustion containing carbon monoxide would enter the home. | 4 | Gas log set installed with damper not permanently secured in open position | Propane_system1.png | file://x:/photopub/docs/0000000547/ee8cdf5f-0893-48f1-85d9-8003658b54f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34c8533e_922a_4717_b644_244611a94fc8
BPVIN-711379-2016 | UW-472617-2016 | 12/7/2016 10:06:57 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided for a hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_.png | file://x:/photopub/docs/0000000527/68d5140b-c8d8-4293-8c0a-6a4a6f7187b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5abec0c4_3141_4208_9f7b_20911f2a062e
ELIN-750801-2017 | EL-480025-2016 | 2/3/2017 11:04:52 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Range_box_bonding_not_complete_in_spice.png 8 awg stranded conductor is not bonded to device box at time of rough wire. Bonding method inside box is a wire binding screw type, conductors 10 awg and smaller are allowed to be terminated in this method. 8 awg requires a compression fitting in the way of a lug. Inadequate bonding may create a failure of the wiring in the case of a fault, providing a risk of shock or fire to persons or property | 3 | Continuity Bonding; method for equipment is not adequate. | Range_box_bonding_not_complete_in_spice.png | file://x:/photopub/docs/0000000553/63f8ae66-bd56-48cd-97ad-ad043153e0cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6fdcd6e0_e748_4474_8b64_119fbf1f3d3d
ELIN-750801-2017 | EL-480025-2016 | 2/3/2017 11:04:52 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Range_box_bonding_not_complete_in_spice.png 8 awg stranded conductor is not bonded to device box at time of rough wire. Bonding method inside box is a wire binding screw type, conductors 10 awg and smaller are allowed to be terminated in this method. 8 awg requires a compression fitting in the way of a lug. Inadequate bonding may create a failure of the wiring in the case of a fault, providing a risk of shock or fire to persons or property | 3 | Continuity Bonding; method for equipment is not adequate. | Range_box_bonding_not_complete_in_spice.png | file://x:/photopub/docs/0000000553/0b8688db-a09e-46b2-88ff-29af7bf5a378.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6fdcd6e0_e748_4474_8b64_119fbf1f3d3d
ELIN-733569-2017 | EL-474832-2016 | 1/6/2017 3:03:16 PM | ASSESS: EL: Final | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | The fridge was receiving it's power from a GFCI protected kitchen counter receptacle instead of the required dedicated fridge receptacle. There wasn't a dedicated circuit in place for the fridge. This could result in overloading of the circuit and nuisance tripping. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Fridge_plugged_into_counter_receptacle.png | file://x:/photopub/docs/0000000540/f41e51a9-7c0d-47ba-a5a7-626650e6598d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bdc8f35_41bc_4898_a64c_d1dcd0975ea9
ELIN-753463-2017 | EL-469386-2016 | 2/15/2017 3:40:12 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Deck_Plugs.png A 120 volt 15 amp receptacle branch circuit for the exterior receptacles have not been Arc-fault protected, this could result in damage to electrical items using these receptacles and poses a possible shock hazard to persons. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Deck_Plugs.png | file://x:/photopub/docs/0000000557/d7b078e4-2c8e-4920-bd4e-e1db3e5ab120.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__105c8a0a_42f2_4afd_aee1_995224ebac16
BPVOP-729590-2016 | 2283655 | 12/21/2016 9:01:29 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP163 | 5.0.1 Operator non-compliance - Safety orders not followed or adhered to | 3 | 3 | All regulated equipment must be maintained and periodically inspected according to the manufacturer instructions and industry standards. I found no maintenance or inspection records available for a pressure control device on the high pressure air receiver. Records must be readily available in order to ensure that a proper maintenance program is in place, as a safeguard against incidents. | 3 | 5.0.1 Operator non-compliance - Safety orders not followed or adhered to | ASME_nameplate.png | file://x:/photopub/docs/0000000535/788100c2-f722-4259-8695-1c5281c7bf3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c53144c_7ad9_4b42_bc24_b81bcd81bbc2
BPVOP-729590-2016 | 2283655 | 12/21/2016 9:01:29 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP163 | 5.0.1 Operator non-compliance - Safety orders not followed or adhered to | 3 | 3 | All regulated equipment must be maintained and periodically inspected according to the manufacturer instructions and industry standards. I found no maintenance or inspection records available for a pressure control device on the high pressure air receiver. Records must be readily available in order to ensure that a proper maintenance program is in place, as a safeguard against incidents. | 3 | 5.0.1 Operator non-compliance - Safety orders not followed or adhered to | Air_receiver.png | file://x:/photopub/docs/0000000535/36093563-c854-4b23-ab1c-1f669dded466.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c53144c_7ad9_4b42_bc24_b81bcd81bbc2
ELIN-730750-2016 | UW-485524-2016 | 12/20/2016 12:51:56 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | This assessment found cables run on the wall surface,below 1.5m without the required protection. Cables may become damaged presenting a shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD_.png | file://x:/photopub/docs/0000000536/94eec9ca-0141-4dff-ad20-4125acffcab9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a649d618_4b1b_4d8d_aa51_9cad9394aeb8
ELIN-730750-2016 | UW-485524-2016 | 12/20/2016 12:51:56 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | This assessment found cables run on the wall surface,below 1.5m without the required protection. Cables may become damaged presenting a shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Heatpump.png | file://x:/photopub/docs/0000000536/e7a98204-7fb6-4d22-b6f7-564eb0165bae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a649d618_4b1b_4d8d_aa51_9cad9394aeb8
ELIN-758882-2017 | EL-487125-2017 | 2/20/2017 10:54:58 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Service_Conduit1.png,Service_Conduit2.png,Service_Conduit3.png The incoming 100 amp 240 volt service conduit and conductors exceed 1.5m in the home. This poses a shock hazard to persons and potential damage to the Electrical Equipment as the incoming Service Conduit and Conductors are not properly protected and must be kept as short as possible within the home. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_Conduit2.png | file://x:/photopub/docs/0000000560/ed89b18b-9f5a-4e06-ba0e-c534064b1632.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07c517a4_e504_4f6c_a1d4_82b7c24d393d
ELIN-753543-2017 | EL-485087-2016 | 2/20/2017 4:00:32 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #GFCI_Receptacle1.png,GFCI_Receptacle2.png A 15 amp 120 volt GFCI receptacle has been fed from a 20 amp breaker, this poses a hazard to persons and equipment as the breaker does not properly protect the receptacle, which is a lower ampacity rating. The receptacle could be overloaded and fail causing damage and harm before the larger ampacity rated breaker trips. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | GFCI_Receptacle1.png | file://x:/photopub/docs/0000000560/140f6b12-d6fd-4875-98ed-b7512786ac58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__150057b1_892e_4d92_9a6c_a2694de3c958
GAIN-752950-2017 | GA-493327-2017 | 2/18/2017 9:30:05 AM | ASSESS: GA: Final | png | #asFound Swing joint | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Swing_joint.png When pressure in piping exceeds 125psi then you must use the appropriate fittings and pipe rated for its intended use. Because the fittings used in this situation are not rated for their intended use this could cause premature failure of the piping system causing the release of propane vapour due to a leak in the system. | 3 | Non-compliant material/fittings installed | Swing_joint.png | file://x:/photopub/docs/0000000560/d423f5a1-904f-43d8-9557-93605e99acba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6090de1_003d_4409_a0cd_0532ab5ce3e2
ELIN-760454-2017 | EL-503004-2017 | 2/22/2017 8:16:01 AM | ASSESS: EL: Service Connection | png | #asFound Rot located at the base of pole | EL254 | Category 2 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Rot_and_split_pole1.png,Rot_and_split_pole2.png,Rot_and_split_pole3.png 6 x 6 wooden pole is rotten and split in several locations. There is a possibility that if the rot is extensive the Pole will fall over. | 4 | Category 2 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Rot_and_split_pole1.png | file://x:/photopub/docs/0000000561/413fdc28-4f2b-467d-a4c4-a69628689ecc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1046b26d_7a8c_4921_9068_1c30bf06b1aa
ELIN-760454-2017 | EL-503004-2017 | 2/22/2017 8:16:01 AM | ASSESS: EL: Service Connection | png | #asFound 6 x 6 pole splitting approximately 7 feet above grade | EL254 | Category 2 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Rot_and_split_pole1.png,Rot_and_split_pole2.png,Rot_and_split_pole3.png 6 x 6 wooden pole is rotten and split in several locations. There is a possibility that if the rot is extensive the Pole will fall over. | 4 | Category 2 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Rot_and_split_pole3.png | file://x:/photopub/docs/0000000561/35e0b49a-483f-4d09-8907-e388e356c556.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1046b26d_7a8c_4921_9068_1c30bf06b1aa
ELIN-760454-2017 | EL-503004-2017 | 2/22/2017 8:16:01 AM | ASSESS: EL: Service Connection | png | #asFound Rot at base of pole, opposite side | EL254 | Category 2 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Rot_and_split_pole1.png,Rot_and_split_pole2.png,Rot_and_split_pole3.png 6 x 6 wooden pole is rotten and split in several locations. There is a possibility that if the rot is extensive the Pole will fall over. | 4 | Category 2 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Rot_and_split_pole2.png | file://x:/photopub/docs/0000000561/f0f45e72-effb-4808-8ece-9e86c9e48dff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1046b26d_7a8c_4921_9068_1c30bf06b1aa
GAIN-716778-2016 | GA-463346-2016 | 12/15/2016 3:40:13 PM | ASSESS: GA: Rough-In | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | The as found hazard was a vent serving a hot water tank which had been oversized. This is a hazard because it creates a risk of ineffective venting in colder weather and flue gas condensation within the vent leading to premature vent failure. | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Oversized_vent.png | file://x:/photopub/docs/0000000531/795de224-ff1c-40c8-9612-bf789d83edd3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43be717e_0850_4ac7_a087_b2694462427f
GAIN-717373-2016 | GA-277784-2015 | 12/6/2016 1:47:42 PM | ASSESS: GA: Final | png | #asFound | GA003 | Provision for expansion Incorrect swing joint | 2 | 2 |  | 2 | Provision for expansion Incorrect swing joint | Swing_joint.png | file://x:/photopub/docs/0000000527/a7869d5c-33b5-4d8b-a346-8046d9bb106e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__878e44b4_d5f7_4024_98c7_01179f9b57e4
ELIN-744397-2017 | EL-336958-2016 | 1/24/2017 9:34:21 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Storage.png Storage materials in front of electrical equipment creating a lack of egress from the power shed. Without proper egress this is a trip hazard and shock hazard. | 0 | No Created Hazard Identified | Storage.png | file://x:/photopub/docs/0000000547/df3eab48-c70d-4221-906e-66b55258b082.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cad8bb66_21ff_4033_b669_d448930d2af9
ELIN-759481-2017 | EL-493449-2017 | 2/20/2017 2:39:45 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Live_Wires1.png,Live_Wires2.png,Live_Wires3.png,Live_Wires4.png,Live_Wires5.png This assessment found live wires throughout dwelling, that can cause a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Live_Wires2.png | file://x:/photopub/docs/0000000560/ed59410c-5848-4087-a20e-0d932168d1ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c56cee1_5c02_43a3_81cf_5d74a17b9b08
ELIN-759481-2017 | EL-493449-2017 | 2/20/2017 2:39:45 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Live_Wires1.png,Live_Wires2.png,Live_Wires3.png,Live_Wires4.png,Live_Wires5.png This assessment found live wires throughout dwelling, that can cause a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Live_Wires5.png | file://x:/photopub/docs/0000000560/dc3720c3-724f-49e0-ac9f-7b31da298e3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c56cee1_5c02_43a3_81cf_5d74a17b9b08
ELIN-759481-2017 | EL-493449-2017 | 2/20/2017 2:39:45 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Live_Wires1.png,Live_Wires2.png,Live_Wires3.png,Live_Wires4.png,Live_Wires5.png This assessment found live wires throughout dwelling, that can cause a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Live_wires3.png | file://x:/photopub/docs/0000000560/ecce2db7-dd45-4897-928d-e180d9999f86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c56cee1_5c02_43a3_81cf_5d74a17b9b08
ELIN-733984-2017 | EL-487310-2017 | 1/9/2017 11:58:13 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #Bushing_is_not_in_place_in_armoured_cable_termination_.png Cable bushing is not in place at armoured cable termination point. Compression that the cable clamp in the box provides, may force sharp cable sheathing into conductor insulation. A risk of shock or fire is present to persons or property if cable Insulation fails. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Bushing_is_not_in_place_in_armoured_cable_termination_.png | file://x:/photopub/docs/0000000540/006cffca-de5a-4fbd-a778-392b46ca08e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__becce82f_b2a2_476d_bee5_deb8bc1d53b2
ELIN-733036-2017 | EL-486859-2017 | 1/5/2017 12:14:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | The contractor has submitted a service connection request, the branch circuit portion of the panel board is not covered, the main breaker is not lock off. The area is not secured from unauthorized persons. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Main_service_requested_connected.png | file://x:/photopub/docs/0000000539/6b0a9eed-1b55-4d8e-881f-0b24c96a55aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5faf20f2_e75c_4791_a9a5_c2fc16c26f01
EDOP-746633-2017 | 2051302 | 1/25/2017 | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | #Wire_rope_cable_assembly.png Traction elevator wire rope cables are required to be checked for wear and breaks. The wire rope cables must maintain a certain diameter while in use. Also ropes must not exceed the maximum allowable strand breaks in 1 lay of the cable assembly. When diameter loss, strand breaks or lay breaks are found, then the ropes must be retired. On this elevator 2 of the 4 wire rope cables have exceeded the maximum allowable diameter loss. If not replaced these ropes will continue to deteriorate creating a higher chance of lay breaks. The wire rope assembly lay breaks may become unwound and entangled with rotating, moving, and or stationary equipment. | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Wire_rope_cable_assembly.png | file://x:/photopub/docs/0000000549/71d750f3-5160-4b07-a983-9e0cc778a7d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92117073_a1d2_4f42_b7da_f92cc5624677
ELIN-723945-2016 | UW-480930-2016 | 12/15/2016 1:20:33 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | The armour of the AC 90 is to be electrically and mechanically secured to ensure proper bonding of the branch circuit. Any damage to the conductors could create a shock hazard if the bonding is not completed at both ends. | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | AC90.png | file://x:/photopub/docs/0000000532/e38be000-e9fa-4d55-acd7-fa327c2bfdce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b0e369e_e6fc_41d1_bd9a_27e4329b75f3
ELIN-738357-2017 | EL-448758-2016 | 1/23/2017 4:20:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | #Missing_grounding1.png,Missing_grounding2.png The 100amp 120/240 volt secondary from the transformer creating a new systems ground was missed, this can create a voltage potential difference and create a shock hazard | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Missing_grounding2.png | file://x:/photopub/docs/0000000547/e2f8f4a6-bc51-419b-b0c6-7e582bd56424.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c011acd_bb20_42c6_abd7_23938e8c9687
ELIN-738357-2017 | EL-448758-2016 | 1/23/2017 4:20:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | #Missing_grounding1.png,Missing_grounding2.png The 100amp 120/240 volt secondary from the transformer creating a new systems ground was missed, this can create a voltage potential difference and create a shock hazard | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Missing_grounding1.png | file://x:/photopub/docs/0000000547/b827cd56-8a06-4c3e-8b02-db8f5cfc3f1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c011acd_bb20_42c6_abd7_23938e8c9687
ELHE-756374-2017 | HE-500744-2017 | 2/15/2017 2:00:55 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Overhead_pole_leaning1.png,Overhead_pole_leaning2.png,Overhead_pole_leaning3.png Overhead service intermediate pole has leaned over and is currently being supported by 2x4 timbers tied off at pole. Further failure of ground soil and movement of pole may result in energized service conductors landing on the ground or even breaking these conductors, both scenarios provide a risk of shock and fire to persons and property. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Overhead_pole_leaning3.png | file://x:/photopub/docs/0000000557/46c87bb5-1188-4a25-b670-78e1669b995e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad4ad46d_70cb_4cd9_8431_7719e90c0b09
ELHE-756374-2017 | HE-500744-2017 | 2/15/2017 2:00:55 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Overhead_pole_leaning1.png,Overhead_pole_leaning2.png,Overhead_pole_leaning3.png Overhead service intermediate pole has leaned over and is currently being supported by 2x4 timbers tied off at pole. Further failure of ground soil and movement of pole may result in energized service conductors landing on the ground or even breaking these conductors, both scenarios provide a risk of shock and fire to persons and property. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Overhead_pole_leaning1.png | file://x:/photopub/docs/0000000557/51def643-e952-40a8-abdb-243b2ba48b27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad4ad46d_70cb_4cd9_8431_7719e90c0b09
ELHE-756374-2017 | HE-500744-2017 | 2/15/2017 2:00:55 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Overhead_pole_leaning1.png,Overhead_pole_leaning2.png,Overhead_pole_leaning3.png Overhead service intermediate pole has leaned over and is currently being supported by 2x4 timbers tied off at pole. Further failure of ground soil and movement of pole may result in energized service conductors landing on the ground or even breaking these conductors, both scenarios provide a risk of shock and fire to persons and property. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Overhead_pole_leaning2.png | file://x:/photopub/docs/0000000557/cbe423d6-3439-4069-8c26-a28785789200.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad4ad46d_70cb_4cd9_8431_7719e90c0b09
ELIN-748155-2017 | EL-454189-2016 | 1/31/2017 11:56:28 AM | ASSESS: EL: Final | png | #asFound Kitchen counter receptacle located approximately 1.1 m from the kitchen sink does not have ground fault protection. | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Sink.png Final assessment on new single family dwelling. A kitchen counter receptacle has been installed within 1.5 m of the kitchen sink and is not protected by a ground fault circuit interrupter. This is a shock hazard if appliances or equipment is used in proximity to the sink. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Sink.png | file://x:/photopub/docs/0000000550/eb70a492-d06a-44ba-bb85-3e80b1aa9ccb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4762df0_b87d_4736_b2a2_18040db71b70
ELIN-748145-2017 | EL-463940-2016 | 1/31/2017 10:57:10 AM | ASSESS: EL: Final | png | #asFound Standard duplex receptacle. It is not marked as tamper proof. | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Standard_duplex.png Final assessment on new single-family dwelling. Non tamper proof receptacles have been installed throughout this dwelling for general use. Receptacles are required to be tamper proof and marked as such. It is a shock hazard for young children to be able to insert a small metallic object into a duplex receptacle. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Standard_duplex.png | file://x:/photopub/docs/0000000550/168e3999-7cba-41e6-a42a-3b2cf9304be0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39dc6a54_5c4e_4111_8595_a138545b33f0
ELIN-746817-2017 | EL-482781-2016 | 1/31/2017 10:16:24 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound unable to determine burial depth or to inspect raceways in earth as covered before date and contractor FSR did not declare if 200 amp conductors larger than 1/0 AWG buried to proper required burial depths as required by code | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #raceways_covered_before_inspection_done.png Found underground raceways were covered without an inspection request and were contractor authorized by field safety representative for service connection while conductors larger than 1/0 AWG are not confirmed and declared to be installed at proper burial depths as required by code. When conductors are not buried to proper depth the conductor is not rated for the load and may be subject to possible mechanical damage which could result in overheating or damage to electrical equipment creating a fire or shock hazard to people and property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | raceways_covered_before_inspection_done.png | file://x:/photopub/docs/0000000550/ca996911-4219-41e2-9348-5cacd22adf31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b701b8bd_cbeb_4d59_bb64_1b653efddc6d
GAIN-745389-2017 | GA-435364-2016 | 1/27/2017 3:24:15 PM | ASSESS: GA: Final | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | #Bonnet.png Second stage regulator on propane system installed that water could enter, no overhang on building bonnet not facing downwards. This is a hazard as water could enter the regulator and freeze causing rupture of the regulator diaphragm or malfunction of regulator. | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | Bonnet.png | file://x:/photopub/docs/0000000549/def5403c-7547-40b8-9869-e8f32351ecab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9a3a513_0b49_47d8_8a4d_345bef644360
ELIN-753638-2017 | EL-337459-2016 | 2/14/2017 10:30:33 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_residential_wiring1.png,Energized_residential_wiring2.png,Energized_residential_wiring3.png,Energized_residential_wiring4.png,Energized_residential_wiring5.png Energized 15/20 amp 120 volt outlet and fixture boxes throughout residence are energized with no devices, coverplates or insulation installed to prevent accidental contact by persons. This is a shock hazard. (Panelboard cover was removed by General Contractor for temp heating installation done by GC, ESO had GC disconnect heat and re-install panel cover to remove open panel hazard) | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_residential_wiring5.png | file://x:/photopub/docs/0000000557/ffd2f2b8-6a05-427c-931f-270256219197.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9296581_bfe2_4e1e_b6ff_d5eb40746eef
ELIN-753638-2017 | EL-337459-2016 | 2/14/2017 10:30:33 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_residential_wiring1.png,Energized_residential_wiring2.png,Energized_residential_wiring3.png,Energized_residential_wiring4.png,Energized_residential_wiring5.png Energized 15/20 amp 120 volt outlet and fixture boxes throughout residence are energized with no devices, coverplates or insulation installed to prevent accidental contact by persons. This is a shock hazard. (Panelboard cover was removed by General Contractor for temp heating installation done by GC, ESO had GC disconnect heat and re-install panel cover to remove open panel hazard) | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_residential_wiring1.png | file://x:/photopub/docs/0000000557/070caa9a-99fc-46b9-b1fe-dbe0642078e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9296581_bfe2_4e1e_b6ff_d5eb40746eef
ELIN-753638-2017 | EL-337459-2016 | 2/14/2017 10:30:33 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound Majority of all wiring throughout residence was energized due to Electrical Contractor terminating all branch circuits to overcurrent devices | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_residential_wiring1.png,Energized_residential_wiring2.png,Energized_residential_wiring3.png,Energized_residential_wiring4.png,Energized_residential_wiring5.png Energized 15/20 amp 120 volt outlet and fixture boxes throughout residence are energized with no devices, coverplates or insulation installed to prevent accidental contact by persons. This is a shock hazard. (Panelboard cover was removed by General Contractor for temp heating installation done by GC, ESO had GC disconnect heat and re-install panel cover to remove open panel hazard) | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_residential_wiring3.png | file://x:/photopub/docs/0000000557/49009375-20bb-4460-9a71-eeeb8c0c7415.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9296581_bfe2_4e1e_b6ff_d5eb40746eef
ELIN-753638-2017 | EL-337459-2016 | 2/14/2017 10:30:33 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_residential_wiring1.png,Energized_residential_wiring2.png,Energized_residential_wiring3.png,Energized_residential_wiring4.png,Energized_residential_wiring5.png Energized 15/20 amp 120 volt outlet and fixture boxes throughout residence are energized with no devices, coverplates or insulation installed to prevent accidental contact by persons. This is a shock hazard. (Panelboard cover was removed by General Contractor for temp heating installation done by GC, ESO had GC disconnect heat and re-install panel cover to remove open panel hazard) | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_residential_wiring4.png | file://x:/photopub/docs/0000000557/515c3b71-e478-4461-a756-54e892ba8069.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9296581_bfe2_4e1e_b6ff_d5eb40746eef
ELIN-753638-2017 | EL-337459-2016 | 2/14/2017 10:30:33 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_residential_wiring1.png,Energized_residential_wiring2.png,Energized_residential_wiring3.png,Energized_residential_wiring4.png,Energized_residential_wiring5.png Energized 15/20 amp 120 volt outlet and fixture boxes throughout residence are energized with no devices, coverplates or insulation installed to prevent accidental contact by persons. This is a shock hazard. (Panelboard cover was removed by General Contractor for temp heating installation done by GC, ESO had GC disconnect heat and re-install panel cover to remove open panel hazard) | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_residential_wiring2.png | file://x:/photopub/docs/0000000557/e912df61-b83f-43d5-95ec-4773772a9763.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9296581_bfe2_4e1e_b6ff_d5eb40746eef
ELIN-733197-2017 | EL-438436-2016 | 1/9/2017 12:24:25 PM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Meterbase_Grounding1.png,Meterbase_Grounding2.png At the 200 amp 120/240 volt, new electrical service, the grounding electrode and ground wire has been connected to the Meterbase bonding lug instead of the neutral point at the Main Panel. This could result in failure of the overcurrent devices to operate and possible shock hazard to persons. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Meterbase_Grounding1.png | file://x:/photopub/docs/0000000540/b1e773c0-b6aa-4226-ae0c-bbb74175ba61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__265c3899_958a_44aa_9b99_c78144b3ac12
ELIN-733197-2017 | EL-438436-2016 | 1/9/2017 12:24:25 PM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Meterbase_Grounding1.png,Meterbase_Grounding2.png At the 200 amp 120/240 volt, new electrical service, the grounding electrode and ground wire has been connected to the Meterbase bonding lug instead of the neutral point at the Main Panel. This could result in failure of the overcurrent devices to operate and possible shock hazard to persons. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Meterbase_Grounding2.png | file://x:/photopub/docs/0000000540/b7e3aa9a-de36-4797-b704-09932e63c453.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__265c3899_958a_44aa_9b99_c78144b3ac12
GAUP-734533-2017 | UW-487682-2017 | 1/6/2017 5:04:47 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | The as found hazard was a venting system serving a boiler and commercial hot water tank which had become dislodged. This is a hazard because with the dislodged venting the products of combustion containing carbon monoxide can escape into the occupied building. | 5 | Venting system not connected or dislodged from energized appliance | Rating_plate.png | file://x:/photopub/docs/0000000540/43b0e1e5-c22c-4bb2-8eb4-411820b9c540.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34665982_2bcc_45e0_ba9f_13a636a78717
GAUP-734533-2017 | UW-487682-2017 | 1/6/2017 5:04:47 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | The as found hazard was a venting system serving a boiler and commercial hot water tank which had become dislodged. This is a hazard because with the dislodged venting the products of combustion containing carbon monoxide can escape into the occupied building. | 5 | Venting system not connected or dislodged from energized appliance | Dislodged_venting.png | file://x:/photopub/docs/0000000540/e6698728-1a8a-4cf1-a71e-a543ba71b814.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34665982_2bcc_45e0_ba9f_13a636a78717
GAUP-734533-2017 | UW-487682-2017 | 1/6/2017 5:04:47 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | The as found hazard was a venting system serving a boiler and commercial hot water tank which had become dislodged. This is a hazard because with the dislodged venting the products of combustion containing carbon monoxide can escape into the occupied building. | 5 | Venting system not connected or dislodged from energized appliance | Unvented_reg.png | file://x:/photopub/docs/0000000540/7c15505b-1256-4da6-8fc5-e2bdb3e60c21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34665982_2bcc_45e0_ba9f_13a636a78717
GAUP-734533-2017 | UW-487682-2017 | 1/6/2017 5:04:47 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | The as found hazard was a venting system serving a boiler and commercial hot water tank which had become dislodged. This is a hazard because with the dislodged venting the products of combustion containing carbon monoxide can escape into the occupied building. | 5 | Venting system not connected or dislodged from energized appliance | Vent_gauge.png | file://x:/photopub/docs/0000000540/3fb5d066-94cd-46df-a988-2e2a2660f619.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34665982_2bcc_45e0_ba9f_13a636a78717
GAUP-734533-2017 | UW-487682-2017 | 1/6/2017 5:04:47 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | The as found hazard was a venting system serving a boiler and commercial hot water tank which had become dislodged. This is a hazard because with the dislodged venting the products of combustion containing carbon monoxide can escape into the occupied building. | 5 | Venting system not connected or dislodged from energized appliance | CRN_info.png | file://x:/photopub/docs/0000000540/d108cb21-dc7c-42e3-a374-1dd5c0f2b45c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34665982_2bcc_45e0_ba9f_13a636a78717
PROP-599979-2016 | 2224174 | 12/14/2016 1:13:32 PM | ASSESS: PR OP: RAP | png | #asFound | PR025 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 |  | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | E_stop_button_inaccessible.png | file://x:/photopub/docs/0000000532/a05ece1c-2d94-4305-86e8-66dc22e9a284.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32EDEAC7_033F_43E3_A5BC_1F0163B9FA1C
PROP-599969-2016 | 2224087 | 12/14/2016 1:46:12 PM | ASSESS: PR OP: RAP | png | #asFound | PR035 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 |  | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Growing_trees_impede_clearance.png | file://x:/photopub/docs/0000000532/e8a1e0e0-3ecc-4295-98e2-e30698af94d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__80A82F05_9D5A_4A25_B86C_12DDFE8FCBA2
ELHE-757185-2017 | HE-501163-2017 | 2/15/2017 5:18:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed energized conductors on outlet boxes | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Covers_plates_not_installed_properly_on_all_outelt_boxes1.png,Covers_plates_not_installed_properly_on_all_outelt_boxes2.png,Covers_plates_not_installed_properly_on_all_outelt_boxes3.png Found receptacle outlets with cover plates that are missing or not installed properly to cover energized conductors. When energized conductors are exposed without cover plates on the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Covers_plates_not_installed_properly_on_all_outelt_boxes1.png | file://x:/photopub/docs/0000000558/74c18f93-1dec-49a3-b774-eb0780991c64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcce87ef_5c7a_4bf6_9bb2_92e1e63bfbfd
ELIN-719203-2016 | EL-374689-2016 | 12/12/2016 11:49:20 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | The 15 amp 120 volt branch circuits feeding general 15 amp receptacles in the home have not been provided with AFCI protection, this could result in equipment damage and possible electrical fire. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Panel_Schedule.png | file://x:/photopub/docs/0000000530/cf3eaf72-5d60-46bc-992c-aa31f5fa339e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82974aa6_2818_4df4_8d18_3ec38edb0aaf
ELIN-733711-2017 | 4766552 | 1/5/2017 3:46:33 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Photo_of__Photo_of_real_estate_sign_and_sold_sticker.png | file://x:/photopub/docs/0000000539/0c468fcc-12ab-49ba-a5d2-43ecd74f476e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__443b72cf_ee4e_4ea3_af19_6c3d0d5a9e40
EDRI-734334-2017 | ED-411008-2016 | 1/6/2017 2:58:20 PM | ASSESS: ED RI: Extension | png | #asFound | ED054 | Unsecure Equipment above Sharp Edges Uneven Landing Surface Definite Slipping /Tripping Hazard Dark Unlit Space | 5 | 5 | When exiting the hoist on landing 24 there are no guard rails or other means of protection to stop people from walking off the side of the building. | 5 | Unsecure Equipment above Sharp Edges Uneven Landing Surface Definite Slipping /Tripping Hazard Dark Unlit Space | Slab_edge_2.png | file://x:/photopub/docs/0000000540/0ce7e6af-a16f-4c44-bca4-956276fdb9a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6761ae3b_b613_47c5_b3ac_cd52d0e8fd98
EDRI-734334-2017 | ED-411008-2016 | 1/6/2017 2:58:20 PM | ASSESS: ED RI: Extension | png | #asFound | ED054 | Unsecure Equipment above Sharp Edges Uneven Landing Surface Definite Slipping /Tripping Hazard Dark Unlit Space | 5 | 5 | When exiting the hoist on landing 24 there are no guard rails or other means of protection to stop people from walking off the side of the building. | 5 | Unsecure Equipment above Sharp Edges Uneven Landing Surface Definite Slipping /Tripping Hazard Dark Unlit Space | Slab_edge_exposed.png | file://x:/photopub/docs/0000000540/340f696a-e26b-43ff-b306-ef226121a442.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6761ae3b_b613_47c5_b3ac_cd52d0e8fd98
EDRI-734337-2017 | ED-411012-2016 | 1/6/2017 3:05:44 PM | ASSESS: ED RI: Extension | png | #asFound | ED054 | Unsecure Equipment above Sharp Edges Uneven Landing Surface Definite Slipping /Tripping Hazard Dark Unlit Space | 5 | 5 | When exiting the hoist on landing 24 there were no guard rails in place at the edge of the building, leaving anyone exiting the hoist with no protection from walking off the side of the building. | 5 | Unsecure Equipment above Sharp Edges Uneven Landing Surface Definite Slipping /Tripping Hazard Dark Unlit Space | Slab_edge_3.png | file://x:/photopub/docs/0000000540/3705de6e-874d-4d08-a22c-90b1fa506cd8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b871948_365b_441c_86d3_0c7b44a0db6e
EDRI-734337-2017 | ED-411012-2016 | 1/6/2017 3:05:44 PM | ASSESS: ED RI: Extension | png | #asFound | ED054 | Unsecure Equipment above Sharp Edges Uneven Landing Surface Definite Slipping /Tripping Hazard Dark Unlit Space | 5 | 5 | When exiting the hoist on landing 24 there were no guard rails in place at the edge of the building, leaving anyone exiting the hoist with no protection from walking off the side of the building. | 5 | Unsecure Equipment above Sharp Edges Uneven Landing Surface Definite Slipping /Tripping Hazard Dark Unlit Space | Slab_edge_1.png | file://x:/photopub/docs/0000000540/0db6cd1f-d26b-470a-b5e3-a2faff480e65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b871948_365b_441c_86d3_0c7b44a0db6e
ELIN-719793-2016 | EL-477130-2016 | 12/8/2016 12:12:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | The neutral lug termination at the consumer service meterbase is missing. If this service is connected as found there is a potential for overheating and fire due to a loose connection of neutral to main service. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Neutral_lug_missing.png | file://x:/photopub/docs/0000000528/ad90ab37-f4da-4302-91cf-24a778554344.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27e978b6_a9be_456f_94d6_04097b77af19
ELOP-728922-2016 | 635 | 1/24/2017 1:33:19 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Tag.png Emergency generator is nearing the end of life as indicated in testing results. Failure of the emergency generator during the loss of utility power failure could result in insufficient lighting and notification systems causing unsafe egress for the occupants of the mall. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Tag.png | file://x:/photopub/docs/0000000547/857b5d14-833f-4c44-913c-3f0fe6cd7167.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__433ef32c_d46b_49a7_a224_c16276a7afda
ELIN-742491-2017 | EL-492845-2017 | 2/1/2017 12:15:22 PM | ASSESS: EL: Service Connection | png | #asFound Ready rod used for ground | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Ready_rod_ground.png Home owner used a ready rod instead of a approved ground rod, thus creating a potential shock hazard with an ungrounded system. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ready_rod_ground.png | file://x:/photopub/docs/0000000551/c949933f-48cd-475e-b0aa-211c98cf89d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a2a1d14_b3fe_4131_8c2a_7de17ea9135c
ELIN-749388-2017 | EL-461607-2016 | 2/1/2017 12:49:19 PM | ASSESS: EL: Final | png | #asFound Service and equipment in category 1 location | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Category_1_location.png Installation of electrical service and equipment is a category 1 location. The rating of the equipment is not suitable for the area. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Category_1_location.png | file://x:/photopub/docs/0000000551/c9d9c64e-6e18-4961-aff5-6a372197ce54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10bd4998_225f_47b1_89c0_3932850f3cf6
ELHE-757185-2017 | HE-501163-2017 | 2/15/2017 5:18:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed energized conductors on outlet boxes | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Covers_plates_not_installed_properly_on_all_outelt_boxes1.png,Covers_plates_not_installed_properly_on_all_outelt_boxes2.png,Covers_plates_not_installed_properly_on_all_outelt_boxes3.png Found receptacle outlets with cover plates that are missing or not installed properly to cover energized conductors. When energized conductors are exposed without cover plates on the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Covers_plates_not_installed_properly_on_all_outelt_boxes2.png | file://x:/photopub/docs/0000000558/774b4206-92b6-473e-9d60-d452807b61d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcce87ef_5c7a_4bf6_9bb2_92e1e63bfbfd
ELHE-757185-2017 | HE-501163-2017 | 2/15/2017 5:18:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed energized conductors on outlet boxes | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Covers_plates_not_installed_properly_on_all_outelt_boxes1.png,Covers_plates_not_installed_properly_on_all_outelt_boxes2.png,Covers_plates_not_installed_properly_on_all_outelt_boxes3.png Found receptacle outlets with cover plates that are missing or not installed properly to cover energized conductors. When energized conductors are exposed without cover plates on the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Covers_plates_not_installed_properly_on_all_outelt_boxes3.png | file://x:/photopub/docs/0000000558/b4fd96f8-9c92-427c-a567-78b2475df9e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcce87ef_5c7a_4bf6_9bb2_92e1e63bfbfd
ELIN-754377-2017 | EL-467407-2016 | 2/10/2017 1:48:11 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Main_panel_without_branch_breaker_cover_panel_energize.png Main service panel found without cover on branch breaker portion. Bussing inside panel is exposed and energized, accidental contact with energized equipment can pose a risk of shock and fire to persons and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Main_panel_without_branch_breaker_cover_panel_energize.png | file://x:/photopub/docs/0000000556/7f0f8bc4-5d70-48d5-9496-29b3beca29a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44d77238_8fd9_4689_99ba_8e2cf9346a7d
ELIN-759032-2017 | EL-495752-2017 | 2/20/2017 11:07:38 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL292 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Y.png Energized panel missing cover. This is a shock hazard. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Y.png | file://x:/photopub/docs/0000000560/b1ff3680-ce9b-4a99-9c5d-59db454dcd7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc501def_c101_46ca_a1d2_e1ce5a15b3f6
ELIN-753543-2017 | EL-485087-2016 | 2/20/2017 4:00:32 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #GFCI_Receptacle1.png,GFCI_Receptacle2.png A 15 amp 120 volt GFCI receptacle has been fed from a 20 amp breaker, this poses a hazard to persons and equipment as the breaker does not properly protect the receptacle, which is a lower ampacity rating. The receptacle could be overloaded and fail causing damage and harm before the larger ampacity rated breaker trips. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | GFCI_Receptacle2.png | file://x:/photopub/docs/0000000560/71965f0b-5470-4dfc-a3cd-87deaf680fc7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__150057b1_892e_4d92_9a6c_a2694de3c958
ELIN-758882-2017 | EL-487125-2017 | 2/20/2017 10:54:58 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Service_Conduit1.png,Service_Conduit2.png,Service_Conduit3.png The incoming 100 amp 240 volt service conduit and conductors exceed 1.5m in the home. This poses a shock hazard to persons and potential damage to the Electrical Equipment as the incoming Service Conduit and Conductors are not properly protected and must be kept as short as possible within the home. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_Conduit1.png | file://x:/photopub/docs/0000000560/f624343b-9aad-4dbf-9799-1f4b9701ffdb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07c517a4_e504_4f6c_a1d4_82b7c24d393d
GAIN-760062-2017 | GA-466371-2016 | 2/21/2017 3:39:27 PM | ASSESS: GA: Final | png | #asFound | GA134 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | 2 | 2 | #Electrical_receptical_mounted_to_supply_air_plenum.png Electrical connections must be made in compliance with canadian electrical code. There is a risk of fire or damage to equipment when electrical work is not compliant with code requirements. | 2 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | Electrical_receptical_mounted_to_supply_air_plenum.png | file://x:/photopub/docs/0000000560/ab19d5ec-9bf0-4578-90df-89b672b3c392.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a5228184_2a10_4f5a_92cd_f988420da00a
GAUP-760898-2017 | UW-503236-2017 | 2/21/2017 3:54:21 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | #Regulator_mounted_in_the_vertical_position.png Regulator not installed in accordance with installation instructions. Regulator will not operate as designed when not installed as per manufacturers installation instructions. | 2 | Not installed according to certified installation instructions | Regulator_mounted_in_the_vertical_position.png | file://x:/photopub/docs/0000000560/d0de4c07-c40f-484d-a8f2-91f465331940.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc8b29e5_ac1e_4cbb_babe_4c4adef3ad17
ELIN-723991-2016 | EL-469452-2016 | 12/15/2016 11:29:01 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Cable enters the wall space flush with baseboard. A nail could pierce armour of cable. Cable is not protected by any immediate fusing or breaker. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | No_mech_protect_cable.png | file://x:/photopub/docs/0000000531/c409bd9d-090e-4c23-8887-1878e5073c9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b878619_b48a_4db6_b457_2a6d72103deb
ELIN-745004-2017 | EL-480629-2016 | 1/25/2017 11:39:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | #No_roof_over_temp_conn_perm_panel_basement_only_constructed.png A new residence with a 200 amp 240 volt service has been authorized for connection. The building is under construction and has not been provided a sealed roof or roof structure at the time of connection. Specific construction of temporary weatherproof enclosures are required to protect the electrical equipment from being adversely affected. When equipment is affected by the entry of water it can lead to property damage or injury to persons. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | No_roof_over_temp_conn_perm_panel_basement_only_constructed.png | file://x:/photopub/docs/0000000548/0ace8502-8802-4ac0-b663-41f7266f2d24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb357d3b_3c5b_4e88_8a9f_2b37d54ca6c8
ELIN-743111-2017 | EL-464404-2016 | 1/25/2017 1:59:39 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #4_meter_wall_no_receptacles.png Anew residence under construction does not have receptacles installed in walls where drywall was found installed floor to ceiling. The minimum number of receptacles were not installed prior to installing the drywall. This will not provide the necessary spacing to ensure owners do not resort to using extension cords.. Use of extension cords increases the risk of arc fault fires and can lead to property damage or injury to persons | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 4_meter_wall_no_receptacles.png | file://x:/photopub/docs/0000000548/7c4d72d8-7197-4fd4-bb97-947dcc67794c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9d52a3c_378a_4523_976b_b45a9a88bbca
ELIN-734482-2017 | UW-464696-2016 | 1/6/2017 6:42:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound Range receptacle | EL157 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 4 | 4 | #Suite_range_receptacle.png An electrical permit is required for the installation of electrical equipment. This requirement is to help ensure that the equipment is installed correctly and is safe to use. During an electrical safety assessment for unpermitted work in a non-conforming secondary suite inside a dwelling, the electrical safety officer found the 40 amp range receptacle mounted on the floor instead of on the wall behind the range. The receptacle and range cord where damaged by the sliding drawer under the range. This damage to the receptacle could create a shock hazard to persons in contact with the range or create a potential fire hazard if an electrical arc was to occur. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | Suite_range_receptacle.png | file://x:/photopub/docs/0000000540/c7baa4d4-4836-4b3d-8f8b-a76eba21e814.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc7e3cce_3e23_4f2e_9cd0_bbf9744fdcfb
ELIN-723991-2016 | EL-469452-2016 | 12/15/2016 11:29:01 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Cable enters the wall space flush with baseboard. A nail could pierce armour of cable. Cable is not protected by any immediate fusing or breaker. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Suite_cable_at_floor.png | file://x:/photopub/docs/0000000531/3ec3c8af-d644-44fb-8437-c35d753a0d64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b878619_b48a_4db6_b457_2a6d72103deb
ELIN-723998-2016 | EL-423104-2016 | 12/15/2016 1:04:58 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Non- fused portion of consumer service cable enter the wall without mechanical protection. A nail or screw could easily be driven into conductors. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Cable_at_floor.png | file://x:/photopub/docs/0000000531/b28d3f07-9722-4a95-903f-5ab17630770c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e1419e4_39bf_43cd_bf05_c2bf8d5eac97
GAIN-641558-2016 | GA-400964-2016 | 12/19/2016 11:01:02 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | Vent_term.png | file://x:/photopub/docs/0000000533/5e44887d-08a2-459a-bbbd-9163e00df228.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b93a4eda_bb04_4070_a89f_d4801c7d949b
EDIN-761420-2017 | ED-462288-2016 | 2/22/2017 7:28:35 AM | ASSESS: ED IN: Acceptance | png | #asFound | ED033 | Operating control installed contrary to the manufacturer instructions and/ or applicable Standards Contractor is not aware Risk Reg ED-02 | 3 | 3 | #Top_landing_exposed_hall_door_11.png,Top_landing_exposed_hall_door_12.png The hoistway is supposed to be kept dry and protected from the elements. During an inspection it was found that the top landing hall door that is exposed to the outside has no means to prevent any water/rain from entering the hoistway. The possibility of rain/water entering the hoistway would possibly pose an electrical hazard as well as possible failure of electrical/electronic components used for safe operation of the elevator. It was found the elevator contractor recognized the issue and brought it up to the general contractor but the general contractor did not rectify the problem. This 4 stop front and back MRL traction is newly installed in a commercial building. | 3 | Operating control installed contrary to the manufacturer instructions and/ or applicable Standards Contractor is not aware Risk Reg ED-02 | Top_landing_exposed_hall_door_11.png | file://x:/photopub/docs/0000000561/fb0ee83c-aa2e-4f57-9168-668054243711.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c9a75ff_0b73_4106_b1b4_53357b1c0b5a
EDIN-761420-2017 | ED-462288-2016 | 2/22/2017 7:28:35 AM | ASSESS: ED IN: Acceptance | png | #asFound | ED033 | Operating control installed contrary to the manufacturer instructions and/ or applicable Standards Contractor is not aware Risk Reg ED-02 | 3 | 3 | #Top_landing_exposed_hall_door_11.png,Top_landing_exposed_hall_door_12.png The hoistway is supposed to be kept dry and protected from the elements. During an inspection it was found that the top landing hall door that is exposed to the outside has no means to prevent any water/rain from entering the hoistway. The possibility of rain/water entering the hoistway would possibly pose an electrical hazard as well as possible failure of electrical/electronic components used for safe operation of the elevator. It was found the elevator contractor recognized the issue and brought it up to the general contractor but the general contractor did not rectify the problem. This 4 stop front and back MRL traction is newly installed in a commercial building. | 3 | Operating control installed contrary to the manufacturer instructions and/ or applicable Standards Contractor is not aware Risk Reg ED-02 | Top_landing_exposed_hall_door_12.png | file://x:/photopub/docs/0000000561/2414c865-c6b0-471f-b7f8-2e288b3b4203.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c9a75ff_0b73_4106_b1b4_53357b1c0b5a
PROP-598684-2016 | PR-312465-2015 | 12/7/2016 11:25:13 AM | ASSESS: PR OP: RAP | png | #asFound | PR044 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | 3 | 3 | Carriage travel safety switch is used to to monitor the correct position of the haul rope tensioning system carriage. During a RAP inspection it was noted that the wand on this switch was bent and would have missed the switch activating devices for uphill or downhill movement of the carriage. If the carriage moved from it normal operating position this could cause under or over tension of the haul rope that could result in damage to ropeway equipment or a potential injury hazard to passengers riding the ropeway. | 3 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | Carriage_Travel_Switch_Bent_Wand_1.png | file://x:/photopub/docs/0000000528/d6807081-a045-48c3-a612-34e64059c4c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__D093E1F5_4561_47CC_93E6_3EA033AC8B7A
ELIN-715059-2016 | EL-320504-2015 | 12/6/2016 4:35:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Grounding conductor terminations are required to be tightened to the specifications of the equipment manufacturer. This is required to ensure a solid and effective connection to the service equipment. This installation for a new 400A 120/240V service for a townhouse complex has a #2 copper ground conductor that has been installed from the ground electrode to the service switch termination point. The ground conductor has not been tightened at the service switch termination point. Left uncorrected this is a potential shock hazard if a lightning strike occurs or if a fault occurs on the electrical system and the grounding connection at the service box fails to keep the electrical equipment and the surrounding ground at the same equipotential. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Exterior_of_new_building_under_construction.png | file://x:/photopub/docs/0000000527/9a425bb3-e455-4a80-82aa-eff6f13df871.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae784ef1_0a27_4794_b805_396f25ae6ad1
ELIN-716019-2016 | EL-352988-2016 | 12/6/2016 11:49:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service cables are required to be located on the outside of buildings except where they enter the building to terminate at the service equipment. When they enter the building they are required to be as short as practicable and not more than 1.5M in length. Where this is not possible and the cables exceed 1.5M in length the cables are required to be encased in 50mm of concrete to protect them. This is required because service cables run directly from meter bases to panels lack effective over-current protection and the requirement is intended to prevent the service cable from getting damaged after the initial installation. This installation for a new triplex residential building has three 3c#1/0 armoured service cables that run through the basement and interior walls for lengths greater than 1.5M. The service cables are partially concrete encasement but the encasement is not 50mm around the cables as required. Left uncorrected this is a potential shock and fire hazard if the service cable gets damaged after the | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Less_than_50mm_of_concrete_encasement.png | file://x:/photopub/docs/0000000527/fa2e43a7-7dae-4d15-ae0b-f3bce5bcbae6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5fda52f_7cdf_417a_89e6_d23130d3871f
ELIN-713532-2016 | EL-352988-2016 | 12/6/2016 12:33:38 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | Boxes larger than 100mm in dimension are required to be supported on two sides of the box. This is required to support the box and the devices connected to them to prevent the box from moving or becoming detached from the structure. This installation for a new triplex residential building under construction has range and dryer outlet boxes that are not supported on two sides of the box. Left uncorrected this is a potential fire and shock hazard if boxes become detached from their supports and wiring is damaged from strain where it is connected to the box and the devices. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Dryer_box_supported_on_one_side_only.png | file://x:/photopub/docs/0000000527/7e553296-f0ee-4c32-bbcd-baea238bc062.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9a3cefc_1726_47fe_adc7_92f51215fb1d
ELIN-716019-2016 | EL-352988-2016 | 12/6/2016 11:49:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service cables are required to be located on the outside of buildings except where they enter the building to terminate at the service equipment. When they enter the building they are required to be as short as practicable and not more than 1.5M in length. Where this is not possible and the cables exceed 1.5M in length the cables are required to be encased in 50mm of concrete to protect them. This is required because service cables run directly from meter bases to panels lack effective over-current protection and the requirement is intended to prevent the service cable from getting damaged after the initial installation. This installation for a new triplex residential building has three 3c#1/0 armoured service cables that run through the basement and interior walls for lengths greater than 1.5M. The service cables are partially concrete encasement but the encasement is not 50mm around the cables as required. Left uncorrected this is a potential shock and fire hazard if the service cable gets damaged after the | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_cables_inside_wall_for_lengths_greater_than_1500mm.png | file://x:/photopub/docs/0000000527/b6a8e367-e1d6-4dab-bac0-f5dd4958fb90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5fda52f_7cdf_417a_89e6_d23130d3871f
ELIN-753737-2017 | EL-492679-2017 | 2/9/2017 2:00:59 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | #H1.png,H2.png,H3.png,H4.png 3c #2awg aluminium on a 100A breaker. This is a fire hazard as the conductor is only rated for 90A at 75 degrees. | 3 | Protection and control Loading of distribution equipment exceeded | H4.png | file://x:/photopub/docs/0000000556/b752400f-e505-4da3-96a8-817dca37c85a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e918fdf3_8b04_4bc9_9441_db9efe308a31
ELIN-753737-2017 | EL-492679-2017 | 2/9/2017 2:00:59 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | #H1.png,H2.png,H3.png,H4.png 3c #2awg aluminium on a 100A breaker. This is a fire hazard as the conductor is only rated for 90A at 75 degrees. | 3 | Protection and control Loading of distribution equipment exceeded | H2.png | file://x:/photopub/docs/0000000556/321bcae3-9081-486a-bb43-2fe790de55df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e918fdf3_8b04_4bc9_9441_db9efe308a31
ELIN-753737-2017 | EL-492679-2017 | 2/9/2017 2:00:59 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | #H1.png,H2.png,H3.png,H4.png 3c #2awg aluminium on a 100A breaker. This is a fire hazard as the conductor is only rated for 90A at 75 degrees. | 3 | Protection and control Loading of distribution equipment exceeded | H1.png | file://x:/photopub/docs/0000000556/a36f7bda-e6cb-4814-84ba-b356f81306eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e918fdf3_8b04_4bc9_9441_db9efe308a31
ELIN-753737-2017 | EL-492679-2017 | 2/9/2017 2:00:59 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | #H1.png,H2.png,H3.png,H4.png 3c #2awg aluminium on a 100A breaker. This is a fire hazard as the conductor is only rated for 90A at 75 degrees. | 3 | Protection and control Loading of distribution equipment exceeded | H3.png | file://x:/photopub/docs/0000000556/64dfdfed-bd31-4666-a072-fa4268f11afc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e918fdf3_8b04_4bc9_9441_db9efe308a31
ELIN-752860-2017 | EL-498023-2017 | 2/14/2017 8:31:15 AM | ASSESS: EL: Service Connection | png | #asFound Interior cover missing from paddleboard, busbars are exposed to contact | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Interior_cover.png Interior cover missing on panelboard, unenergized exposed bus bar was observed. A high likelihood of someone receiving a shock or burn if the condition remains. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Interior_cover.png | file://x:/photopub/docs/0000000557/aff1449a-b1b1-4055-86ef-c620b95de06e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10a538c6_2bf5_4b35_993c_071dc0b5852b
ELIN-724108-2016 | UW-481044-2016 | 12/15/2016 9:00:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL040 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 3 | 3 | Unlabelled electrical cabinets with 600 volt energized conductors. This is an arc flash and shock hazard for individuals. | 3 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 1.png | file://x:/photopub/docs/0000000532/b2c3b3b3-5bac-4e2b-b99b-86d701c536eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e1971d1_c1c4_4c7c_9fa6_8d4adf3b39ce
ELIN-724094-2016 | UW-481038-2016 | 12/14/2016 5:28:37 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeders not properly supported. This is a hazard as the cables can become damaged. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000532/36c14954-1e5a-45de-8ad7-8712518c339b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eff337d5_f560_4738_8dc1_07f00445db4b
ELIN-724108-2016 | UW-481044-2016 | 12/15/2016 9:00:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL040 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 3 | 3 | Unlabelled electrical cabinets with 600 volt energized conductors. This is an arc flash and shock hazard for individuals. | 3 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 6.png | file://x:/photopub/docs/0000000532/d70477b8-9ea3-419e-b30f-ef7266e3ee2b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e1971d1_c1c4_4c7c_9fa6_8d4adf3b39ce
ELIN-724094-2016 | UW-481038-2016 | 12/14/2016 5:28:37 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeders not properly supported. This is a hazard as the cables can become damaged. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | C.png | file://x:/photopub/docs/0000000532/6b957c9b-1821-471a-9beb-a54a92b0c69f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eff337d5_f560_4738_8dc1_07f00445db4b
ELIN-724108-2016 | UW-481044-2016 | 12/15/2016 9:00:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL040 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 3 | 3 | Unlabelled electrical cabinets with 600 volt energized conductors. This is an arc flash and shock hazard for individuals. | 3 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 2.png | file://x:/photopub/docs/0000000532/d0f8e884-503f-4613-8a41-63e134eed61d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e1971d1_c1c4_4c7c_9fa6_8d4adf3b39ce
ELIN-724094-2016 | UW-481038-2016 | 12/14/2016 5:28:37 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeders not properly supported. This is a hazard as the cables can become damaged. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | E.png | file://x:/photopub/docs/0000000532/79204e04-1edc-4919-9eb2-d1fa128bff97.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eff337d5_f560_4738_8dc1_07f00445db4b
ELIN-724108-2016 | UW-481044-2016 | 12/15/2016 9:00:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL040 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 3 | 3 | Unlabelled electrical cabinets with 600 volt energized conductors. This is an arc flash and shock hazard for individuals. | 3 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 4.png | file://x:/photopub/docs/0000000532/0de3ab8d-96f1-48d3-ba78-86882415ea9e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e1971d1_c1c4_4c7c_9fa6_8d4adf3b39ce
ELIN-724094-2016 | UW-481038-2016 | 12/14/2016 5:28:37 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeders not properly supported. This is a hazard as the cables can become damaged. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | B.png | file://x:/photopub/docs/0000000532/d5ed2ef9-589e-41ed-b558-acf64712beab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eff337d5_f560_4738_8dc1_07f00445db4b
ELIN-724108-2016 | UW-481044-2016 | 12/15/2016 9:00:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL040 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 3 | 3 | Unlabelled electrical cabinets with 600 volt energized conductors. This is an arc flash and shock hazard for individuals. | 3 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 3.png | file://x:/photopub/docs/0000000532/033a87bd-eda1-45d3-a439-4fd0a4f6f0df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e1971d1_c1c4_4c7c_9fa6_8d4adf3b39ce
ELIN-724094-2016 | UW-481038-2016 | 12/14/2016 5:28:37 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeders not properly supported. This is a hazard as the cables can become damaged. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | D.png | file://x:/photopub/docs/0000000532/0685a160-9f1a-43d6-86da-3b421d553ad1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eff337d5_f560_4738_8dc1_07f00445db4b
ELIN-724108-2016 | UW-481044-2016 | 12/15/2016 9:00:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL040 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 3 | 3 | Unlabelled electrical cabinets with 600 volt energized conductors. This is an arc flash and shock hazard for individuals. | 3 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 5.png | file://x:/photopub/docs/0000000532/5774fdd6-8ee2-4d21-919f-64a2cee4ed42.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e1971d1_c1c4_4c7c_9fa6_8d4adf3b39ce
ELIN-716019-2016 | EL-352988-2016 | 12/6/2016 11:49:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service cables are required to be located on the outside of buildings except where they enter the building to terminate at the service equipment. When they enter the building they are required to be as short as practicable and not more than 1.5M in length. Where this is not possible and the cables exceed 1.5M in length the cables are required to be encased in 50mm of concrete to protect them. This is required because service cables run directly from meter bases to panels lack effective over-current protection and the requirement is intended to prevent the service cable from getting damaged after the initial installation. This installation for a new triplex residential building has three 3c#1/0 armoured service cables that run through the basement and interior walls for lengths greater than 1.5M. The service cables are partially concrete encasement but the encasement is not 50mm around the cables as required. Left uncorrected this is a potential shock and fire hazard if the service cable gets damaged after the | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Less_than_50mm_of_concrete_encasement_.png | file://x:/photopub/docs/0000000527/08bc7cbf-5460-4028-ae88-70a6c66ff2a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5fda52f_7cdf_417a_89e6_d23130d3871f
ELIN-715059-2016 | EL-320504-2015 | 12/6/2016 4:35:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Grounding conductor terminations are required to be tightened to the specifications of the equipment manufacturer. This is required to ensure a solid and effective connection to the service equipment. This installation for a new 400A 120/240V service for a townhouse complex has a #2 copper ground conductor that has been installed from the ground electrode to the service switch termination point. The ground conductor has not been tightened at the service switch termination point. Left uncorrected this is a potential shock hazard if a lightning strike occurs or if a fault occurs on the electrical system and the grounding connection at the service box fails to keep the electrical equipment and the surrounding ground at the same equipotential. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Service_switch.png | file://x:/photopub/docs/0000000527/4f8f19c5-6413-4c69-9d66-d32635a63e32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae784ef1_0a27_4794_b805_396f25ae6ad1
ELIN-715059-2016 | EL-320504-2015 | 12/6/2016 4:35:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Grounding conductor terminations are required to be tightened to the specifications of the equipment manufacturer. This is required to ensure a solid and effective connection to the service equipment. This installation for a new 400A 120/240V service for a townhouse complex has a #2 copper ground conductor that has been installed from the ground electrode to the service switch termination point. The ground conductor has not been tightened at the service switch termination point. Left uncorrected this is a potential shock hazard if a lightning strike occurs or if a fault occurs on the electrical system and the grounding connection at the service box fails to keep the electrical equipment and the surrounding ground at the same equipotential. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Terminations_in_service_switch.png | file://x:/photopub/docs/0000000527/49685be6-568f-47c9-b845-67e51b77031f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae784ef1_0a27_4794_b805_396f25ae6ad1
ELIN-715059-2016 | EL-320504-2015 | 12/6/2016 4:35:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Grounding conductor terminations are required to be tightened to the specifications of the equipment manufacturer. This is required to ensure a solid and effective connection to the service equipment. This installation for a new 400A 120/240V service for a townhouse complex has a #2 copper ground conductor that has been installed from the ground electrode to the service switch termination point. The ground conductor has not been tightened at the service switch termination point. Left uncorrected this is a potential shock hazard if a lightning strike occurs or if a fault occurs on the electrical system and the grounding connection at the service box fails to keep the electrical equipment and the surrounding ground at the same equipotential. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_conductor_termination_not_tightened.png | file://x:/photopub/docs/0000000527/14f26c15-16a4-41ac-85f0-26a89737ce52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae784ef1_0a27_4794_b805_396f25ae6ad1
ELIN-713532-2016 | EL-352988-2016 | 12/6/2016 12:33:38 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | Boxes larger than 100mm in dimension are required to be supported on two sides of the box. This is required to support the box and the devices connected to them to prevent the box from moving or becoming detached from the structure. This installation for a new triplex residential building under construction has range and dryer outlet boxes that are not supported on two sides of the box. Left uncorrected this is a potential fire and shock hazard if boxes become detached from their supports and wiring is damaged from strain where it is connected to the box and the devices. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Dryer_box_supported_on_one_side.png | file://x:/photopub/docs/0000000527/506f464e-6e63-41ed-b7bc-efb283f6d6dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9a3cefc_1726_47fe_adc7_92f51215fb1d
ELIN-716019-2016 | EL-352988-2016 | 12/6/2016 11:49:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service cables are required to be located on the outside of buildings except where they enter the building to terminate at the service equipment. When they enter the building they are required to be as short as practicable and not more than 1.5M in length. Where this is not possible and the cables exceed 1.5M in length the cables are required to be encased in 50mm of concrete to protect them. This is required because service cables run directly from meter bases to panels lack effective over-current protection and the requirement is intended to prevent the service cable from getting damaged after the initial installation. This installation for a new triplex residential building has three 3c#1/0 armoured service cables that run through the basement and interior walls for lengths greater than 1.5M. The service cables are partially concrete encasement but the encasement is not 50mm around the cables as required. Left uncorrected this is a potential shock and fire hazard if the service cable gets damaged after the | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Exterior_of_building_.png | file://x:/photopub/docs/0000000527/de10085a-dd3c-44da-90dd-c4d4c5c3a6ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5fda52f_7cdf_417a_89e6_d23130d3871f
ELIN-716019-2016 | EL-352988-2016 | 12/6/2016 11:49:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service cables are required to be located on the outside of buildings except where they enter the building to terminate at the service equipment. When they enter the building they are required to be as short as practicable and not more than 1.5M in length. Where this is not possible and the cables exceed 1.5M in length the cables are required to be encased in 50mm of concrete to protect them. This is required because service cables run directly from meter bases to panels lack effective over-current protection and the requirement is intended to prevent the service cable from getting damaged after the initial installation. This installation for a new triplex residential building has three 3c#1/0 armoured service cables that run through the basement and interior walls for lengths greater than 1.5M. The service cables are partially concrete encasement but the encasement is not 50mm around the cables as required. Left uncorrected this is a potential shock and fire hazard if the service cable gets damaged after the | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Typical_unit_panel.png | file://x:/photopub/docs/0000000527/ded7be26-e6c3-485f-a17e-55b46418e6ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5fda52f_7cdf_417a_89e6_d23130d3871f
BPVIN-705752-2016 | BPV-450800-2016 | 2/15/2017 9:40:27 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | #Boiler_shut_off_switches_1.png,Boiler_shut_off_switches_2.png A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected when required. I found that there was no remote boiler shutdown switch provided. Potential exists for an incident due to lack of remote emergency control. | 0 | No Created Hazard Identified | Boiler_shut_off_switches_1.png | file://x:/photopub/docs/0000000557/e4a1d2d3-863f-4053-8967-8f31a7d685eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8d309ea_f2e6_47d4_a081_22e8e0f73da5
BPVIN-705752-2016 | BPV-450800-2016 | 2/15/2017 9:40:27 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | #Boiler_shut_off_switches_1.png,Boiler_shut_off_switches_2.png A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected when required. I found that there was no remote boiler shutdown switch provided. Potential exists for an incident due to lack of remote emergency control. | 0 | No Created Hazard Identified | Boiler_shut_off_switches_2.png | file://x:/photopub/docs/0000000557/b1f04db1-289a-4683-b887-cdcd49cdc430.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8d309ea_f2e6_47d4_a081_22e8e0f73da5
ELIN-719977-2016 | EL-395684-2016 | 12/7/2016 1:18:54 PM | ASSESS: EL: Final | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Electrical service conductors are required to be mechanically protected by raceways. Provisions must be made for underground raceways that are subject to movement by ground settlement or frost, to prevent damage to the conductors or the electrical equipment. At a new single family dwelling, adequate provisions where not made for ground settlement for the underground service raceway. The service raceway separated at a coupling just above grade and the energized service conductors where exposed for the 200A, 120/240V service. The exposed service conductors could be mechanically damaged which could create a shock hazard to persons or equipment damage to the service. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Front_of_house.png | file://x:/photopub/docs/0000000529/3c3d1126-b4f6-4296-affa-d33d12736887.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__451c5bdc_2b90_49d9_98ec_306e2094ea38
ELIN-719977-2016 | EL-395684-2016 | 12/7/2016 1:18:54 PM | ASSESS: EL: Final | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Electrical service conductors are required to be mechanically protected by raceways. Provisions must be made for underground raceways that are subject to movement by ground settlement or frost, to prevent damage to the conductors or the electrical equipment. At a new single family dwelling, adequate provisions where not made for ground settlement for the underground service raceway. The service raceway separated at a coupling just above grade and the energized service conductors where exposed for the 200A, 120/240V service. The exposed service conductors could be mechanically damaged which could create a shock hazard to persons or equipment damage to the service. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Service_Conduit_.png | file://x:/photopub/docs/0000000529/2c113285-89c1-4a49-bd34-5674fa82e0fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__451c5bdc_2b90_49d9_98ec_306e2094ea38
ELIN-719977-2016 | EL-395684-2016 | 12/7/2016 1:18:54 PM | ASSESS: EL: Final | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Electrical service conductors are required to be mechanically protected by raceways. Provisions must be made for underground raceways that are subject to movement by ground settlement or frost, to prevent damage to the conductors or the electrical equipment. At a new single family dwelling, adequate provisions where not made for ground settlement for the underground service raceway. The service raceway separated at a coupling just above grade and the energized service conductors where exposed for the 200A, 120/240V service. The exposed service conductors could be mechanically damaged which could create a shock hazard to persons or equipment damage to the service. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Side_of_House_.png | file://x:/photopub/docs/0000000529/86cd4eac-dc64-491d-abdf-346b61a36a95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__451c5bdc_2b90_49d9_98ec_306e2094ea38
ELIN-759119-2017 | EL-498065-2017 | 2/20/2017 9:53:50 AM | ASSESS: EL: Service Connection | png | #asFound Load calculation required. | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 3 | #200_Amp_panel.png Service conductors are under sized to table # 4 with out a load calculation. If overloaded may cause a thermal hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 200_Amp_panel.png | file://x:/photopub/docs/0000000560/3b2d23fc-d1c6-4855-9d8e-d9e2fe3a7f82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82bea40c_69a1_439c_b690_91fa3bd2ae23
ELIN-758882-2017 | EL-487125-2017 | 2/20/2017 10:54:58 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Service_Conduit1.png,Service_Conduit2.png,Service_Conduit3.png The incoming 100 amp 240 volt service conduit and conductors exceed 1.5m in the home. This poses a shock hazard to persons and potential damage to the Electrical Equipment as the incoming Service Conduit and Conductors are not properly protected and must be kept as short as possible within the home. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_Conduit3.png | file://x:/photopub/docs/0000000560/733b72b4-728b-46fe-ad91-79b0b17c19f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07c517a4_e504_4f6c_a1d4_82b7c24d393d
PROP-760746-2017 | 2224096 | 2/21/2017 7:55:18 PM | ASSESS: PR OP: Operational | png | #asFound | PR025 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Vertical_clearance.png Clearance not maintenance at unload station, between carriers and skiable area. Skiing public could be clipped by a loaded chair if a person were to fail to unload | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Vertical_clearance.png | file://x:/photopub/docs/0000000560/71343f17-81f2-4c15-9871-087a4d4c2890.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0456858_39fe_49b5_af26_e4409eab3a90
AMIN-714469-2016 | AM-470134-2016 | 12/19/2016 4:24:23 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | No anchoring being used on the Inflatable, device could move while in operation. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Anchoring_rings_.png | file://x:/photopub/docs/0000000533/4de47c45-56f2-4bc2-8865-693c591acbb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5ce6817_5285_4bf1_80c7_dec9618c9156
ELIN-704327-2016 | EL-449212-2016 | 1/12/2017 11:16:54 AM | ASSESS: EL: Final | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | #Aerhnu.png Openings in panel required installation of knock-out fillers as all unused opening are required to be filled | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Aerhnu.png | file://x:/photopub/docs/0000000542/80e95897-f627-4956-9c2b-1cc0ba8b8fad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b21235a2_1348_4e0d_afd4_744811a62835
GAWP-745909-2017 | GA-476550-2016 | 1/25/2017 7:52:51 PM | ASSESS: GA Work In Progress | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Reg.png 2 psi to inches line reg installed inches away from mechanical air intake. If regulator relieved raw gas will be introduced to heater causing explosion or fire . | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Reg.png | file://x:/photopub/docs/0000000548/4ff07ad2-44ce-45ee-832e-dfd9942b620e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97d2aa25_d5cb_4cc8_b5b0_25a5e218c354
BPVIN-749909-2017 | BPV-497336-2017 | 2/1/2017 12:44:40 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | #Clearances_.png | 0 | No Created Hazard Identified | Clearances_.png | file://x:/photopub/docs/0000000552/e0541e1e-094d-4b33-be96-ac58c55b0ab0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4f0941b_c3eb_498e_9ab3_27536b71b6b0
GAIN-721407-2016 | GA-473066-2016 | 12/13/2016 12:29:30 PM | ASSESS: GA: Rough-In | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | Appliance air intake located underneath dryer exhaust duct. This could allow lint and dryer exhaust to enter the air inlet of the appliance leading to incomplete combustion and production of carbon monoxide. | 2 | Side wall vent termination not compliant with installation instructions | Appliance_air_intake.png | file://x:/photopub/docs/0000000530/88d7f373-2240-4162-8060-6722b425919d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__335be99d_d332_4a3c_b65b_dccff4cf1079
GAIN-721408-2016 | GA-473065-2016 | 12/13/2016 12:42:16 PM | ASSESS: GA: Rough-In | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | Furnace air intake pipe located next to gas regulator relief vent. If the regulator reliefs gas through the vent it could be sucked into the furnace air intake possibly resulting in an explosion or fire. | 2 | Side wall vent termination not compliant with installation instructions | Furnace_air_intake.png | file://x:/photopub/docs/0000000530/42b9dd7c-ed9b-4f8b-90c9-a0165521c13f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__041e54f3_d8d6_42e7_bac8_748993843db6
BPVOP-726523-2016 | 3984116 | 6/8/2016 3:14:55 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Relief_valve_installation1.png | file://x:/photopub/docs/0000000533/fe77eccb-1942-473c-8726-4df4679d741d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ce8ce01_70bc_404d_8296_5c3e42bbb1e9
BPVOP-726513-2016 | 3983891 | 6/8/2016 2:54:47 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 | Safety relief valves may not function properly due to code non-compliant installation. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Relief_valve_installation.png | file://x:/photopub/docs/0000000533/f00d8442-ea6c-47a2-a0c5-6b2ca2f168b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ff5ff9a_d31c_4083_a8fc_e203d4b989f0
ELIN-735411-2017 | EL-427990-2016 | 1/9/2017 1:40:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather1.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather2.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather3.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather4.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather5.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather6.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather7.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather8.png Found temporary construction distribution panelboards and its feeder electrical equipment to be damaged due to not being made weatherproof and protected from being damaged. When electrical equipment is not weatherproof and protecte | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather6.png | file://x:/photopub/docs/0000000543/29ef484e-2ec4-4382-a364-74452f99b37e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c56a2be_d0fb_4dc1_b463_c24d444cc9e7
ELIN-735411-2017 | EL-427990-2016 | 1/9/2017 1:40:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather1.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather2.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather3.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather4.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather5.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather6.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather7.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather8.png Found temporary construction distribution panelboards and its feeder electrical equipment to be damaged due to not being made weatherproof and protected from being damaged. When electrical equipment is not weatherproof and protecte | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather2.png | file://x:/photopub/docs/0000000543/d01ecdc3-2743-4c11-a9dc-c6a85ade2566.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c56a2be_d0fb_4dc1_b463_c24d444cc9e7
ELIN-713532-2016 | EL-352988-2016 | 12/6/2016 12:33:38 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | Boxes larger than 100mm in dimension are required to be supported on two sides of the box. This is required to support the box and the devices connected to them to prevent the box from moving or becoming detached from the structure. This installation for a new triplex residential building under construction has range and dryer outlet boxes that are not supported on two sides of the box. Left uncorrected this is a potential fire and shock hazard if boxes become detached from their supports and wiring is damaged from strain where it is connected to the box and the devices. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Improperly_supported_range_box.png | file://x:/photopub/docs/0000000527/6580fc6b-d5dc-485e-8803-9f72aea95064.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9a3cefc_1726_47fe_adc7_92f51215fb1d
ELIN-716019-2016 | EL-352988-2016 | 12/6/2016 11:49:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service cables are required to be located on the outside of buildings except where they enter the building to terminate at the service equipment. When they enter the building they are required to be as short as practicable and not more than 1.5M in length. Where this is not possible and the cables exceed 1.5M in length the cables are required to be encased in 50mm of concrete to protect them. This is required because service cables run directly from meter bases to panels lack effective over-current protection and the requirement is intended to prevent the service cable from getting damaged after the initial installation. This installation for a new triplex residential building has three 3c#1/0 armoured service cables that run through the basement and interior walls for lengths greater than 1.5M. The service cables are partially concrete encasement but the encasement is not 50mm around the cables as required. Left uncorrected this is a potential shock and fire hazard if the service cable gets damaged after the | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Meter_base.png | file://x:/photopub/docs/0000000527/59f13046-3113-4f1a-9737-2dd02ae064d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5fda52f_7cdf_417a_89e6_d23130d3871f
ELIN-732770-2017 | EL-470509-2016 | 1/10/2017 3:08:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Leaning_unsupported_service_pole1.png,Leaning_unsupported_service_pole2.png Poles that support over head wiring are required to be supported to prevent them from being pulled over when under strain from the weight of supporting over head cables. This installation for a new 200A 120/240V service to a detached garage has the service conduit and meter base installed on a pole. The pole is already leaning over at a substantial angle and will have additional weight added to support the new service supply conductors that will be installed by the utility. Left uncorrected this is a shock and fire hazard if the pole leans over enough to lower the height of the service supply cables crossing the road and a vehicle hits it. Also the pole may fall over onto the ground and leave energized conductors exposed to contact from persons or vehicles. Poles that support over head wiring are required to be supported to prevent them from being pulled over when under strain from the weight of supporting over head cables. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Leaning_unsupported_service_pole1.png | file://x:/photopub/docs/0000000541/21cb4055-4a66-4c7e-8e4c-7ca97f5223bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e913411f_85fe_4023_8a21_e60ad421c4e0
ELIN-757731-2017 | UW-501477-2017 | 2/16/2017 10:24:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png Marijuana grow operation has overloaded the main service. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A5.png | file://x:/photopub/docs/0000000558/7ef14e4b-b2d6-433d-bde7-6b9c11b2b28c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b145f20_c0a0_40d3_99e2_d209611038ec
ELIN-757731-2017 | UW-501477-2017 | 2/16/2017 10:24:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png Marijuana grow operation has overloaded the main service. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A7.png | file://x:/photopub/docs/0000000558/c0890ade-7218-4e0c-ae0a-5efe458ad669.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b145f20_c0a0_40d3_99e2_d209611038ec
ELIN-757731-2017 | UW-501477-2017 | 2/16/2017 10:24:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png Marijuana grow operation has overloaded the main service. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A3.png | file://x:/photopub/docs/0000000558/c48a2435-9e65-4e95-8c12-2242e09052c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b145f20_c0a0_40d3_99e2_d209611038ec
ELIN-757731-2017 | UW-501477-2017 | 2/16/2017 10:24:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png Marijuana grow operation has overloaded the main service. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A4.png | file://x:/photopub/docs/0000000558/64182a90-b735-4401-91dd-73feff3d274a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b145f20_c0a0_40d3_99e2_d209611038ec
ELIN-757731-2017 | UW-501477-2017 | 2/16/2017 10:24:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png Marijuana grow operation has overloaded the main service. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A1.png | file://x:/photopub/docs/0000000558/52b84452-40d9-48ba-b397-34f1973e64ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b145f20_c0a0_40d3_99e2_d209611038ec
ELIN-757731-2017 | UW-501477-2017 | 2/16/2017 10:24:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png Marijuana grow operation has overloaded the main service. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A6.png | file://x:/photopub/docs/0000000558/ca70dfb9-fccd-48f0-b8dd-a01f5836603e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b145f20_c0a0_40d3_99e2_d209611038ec
ELIN-757731-2017 | UW-501477-2017 | 2/16/2017 10:24:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png Marijuana grow operation has overloaded the main service. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A2.png | file://x:/photopub/docs/0000000558/a3a23fc3-9db9-49f1-b13d-c31b782f4bb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b145f20_c0a0_40d3_99e2_d209611038ec
PROP-701317-2016 | 2224162 | 2/8/2017 5:28:04 PM | ASSESS: PR OP: Annual | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | #Oil_leaking_onto_drive_belt.png The main drive gearbox was leaking oil onto a set of drive belts. Oil was being allowed to collect onto these drive belts which are utilized by both the auxiliary and evacuation drive to provide rotation to the main drive gearbox. There is a risk that in the event of the operator needing to utilize the auxiliary or evacuation drive that the belts would slip and not provide the friction required to move the lift with the auxiliary or evacuation drive. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Oil_leaking_onto_drive_belt.png | file://x:/photopub/docs/0000000558/1695976f-73b9-477f-ac8b-902134ddf6e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14de7030_c2fc_46bd_9c46_ab492d87d4f8
ELIN-718600-2016 | EL-468830-2016 | 12/7/2016 7:21:20 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found 60 amp 120/240 volt 1 phase panelboards with exposed energized conductors and bus bars in two separate residential occupancies units. When electrical equipment such as panelboards have covers missing leaving bus bars and conductors exposed and energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Switching is not done in an ungrounded conductor | b.png | file://x:/photopub/docs/0000000527/4c9bdcca-d1e7-4906-be9e-e893890ae92f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3008b5c0_91d8_4317_a6a6_d443cd4e3bfa
ELIN-718600-2016 | EL-468830-2016 | 12/7/2016 7:21:20 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found 60 amp 120/240 volt 1 phase panelboards with exposed energized conductors and bus bars in two separate residential occupancies units. When electrical equipment such as panelboards have covers missing leaving bus bars and conductors exposed and energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Switching is not done in an ungrounded conductor | d.png | file://x:/photopub/docs/0000000527/6c246f18-0a4b-40a3-8b7c-c0a0b74c81dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3008b5c0_91d8_4317_a6a6_d443cd4e3bfa
ELIN-718600-2016 | EL-468830-2016 | 12/7/2016 7:21:20 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found 60 amp 120/240 volt 1 phase panelboards with exposed energized conductors and bus bars in two separate residential occupancies units. When electrical equipment such as panelboards have covers missing leaving bus bars and conductors exposed and energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Switching is not done in an ungrounded conductor | f.png | file://x:/photopub/docs/0000000527/5010f155-1d64-49e7-9ea1-9b3fbd6f6669.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3008b5c0_91d8_4317_a6a6_d443cd4e3bfa
ELIN-732684-2017 | EL-484215-2016 | 1/17/2017 4:48:30 PM | ASSESS: EL: Service Connection | png | #asFound damaged rusted inoperable existing consumer's service switch and equipment is damaged unapproved and not in weatherproof enclosure | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | #damaged_hazardous_unapproved_electrical_equipment_for_existing_service1.png,damaged_hazardous_unapproved_electrical_equipment_for_existing_service2.png Found damaged, hazardous and inoperable electrical equipment for 200 amp 120/240 volt single phase consumer's service switch which is fully exposed and not weatherproofed and is not approved for the use. When electrical equipment is not installed and protected properly, the electrical equipment can become damaged and hazardous and will not operate as intended for its use. The damaged electrical equipment can create an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | damaged_hazardous_unapproved_electrical_equipment_for_existing_service2.png | file://x:/photopub/docs/0000000544/6647b9a6-1459-4e36-8af8-a688909f68e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acd4fbed_40db_49b8_a10b_dc99467a1b78
ELIN-732684-2017 | EL-484215-2016 | 1/17/2017 4:48:30 PM | ASSESS: EL: Service Connection | png | #asFound damaged rusted inoperable existing consumer's service switch and equipment is damaged unapproved and not in weatherproof enclosure | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | #damaged_hazardous_unapproved_electrical_equipment_for_existing_service1.png,damaged_hazardous_unapproved_electrical_equipment_for_existing_service2.png Found damaged, hazardous and inoperable electrical equipment for 200 amp 120/240 volt single phase consumer's service switch which is fully exposed and not weatherproofed and is not approved for the use. When electrical equipment is not installed and protected properly, the electrical equipment can become damaged and hazardous and will not operate as intended for its use. The damaged electrical equipment can create an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | damaged_hazardous_unapproved_electrical_equipment_for_existing_service1.png | file://x:/photopub/docs/0000000544/a368b742-60cb-4133-bec2-98ec7b6722f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acd4fbed_40db_49b8_a10b_dc99467a1b78
ELIN-735411-2017 | EL-427990-2016 | 1/9/2017 1:40:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather1.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather2.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather3.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather4.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather5.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather6.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather7.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather8.png Found temporary construction distribution panelboards and its feeder electrical equipment to be damaged due to not being made weatherproof and protected from being damaged. When electrical equipment is not weatherproof and protecte | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather4.png | file://x:/photopub/docs/0000000543/ea67de2b-51ef-4d6e-af8c-a556d7140bca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c56a2be_d0fb_4dc1_b463_c24d444cc9e7
ELIN-735411-2017 | EL-427990-2016 | 1/9/2017 1:40:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather1.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather2.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather3.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather4.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather5.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather6.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather7.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather8.png Found temporary construction distribution panelboards and its feeder electrical equipment to be damaged due to not being made weatherproof and protected from being damaged. When electrical equipment is not weatherproof and protecte | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather3.png | file://x:/photopub/docs/0000000543/c33c110b-a70c-4e2f-b14f-9b184f71307d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c56a2be_d0fb_4dc1_b463_c24d444cc9e7
ELIN-735411-2017 | EL-427990-2016 | 1/9/2017 1:40:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather1.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather2.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather3.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather4.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather5.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather6.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather7.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather8.png Found temporary construction distribution panelboards and its feeder electrical equipment to be damaged due to not being made weatherproof and protected from being damaged. When electrical equipment is not weatherproof and protecte | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather5.png | file://x:/photopub/docs/0000000543/4bcb1adc-3bf3-48f0-b202-a4cce4f4f063.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c56a2be_d0fb_4dc1_b463_c24d444cc9e7
ELIN-735411-2017 | EL-427990-2016 | 1/9/2017 1:40:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather1.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather2.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather3.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather4.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather5.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather6.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather7.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather8.png Found temporary construction distribution panelboards and its feeder electrical equipment to be damaged due to not being made weatherproof and protected from being damaged. When electrical equipment is not weatherproof and protecte | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather1.png | file://x:/photopub/docs/0000000543/335bd8d7-a4e5-4165-b87e-ba77cb4425b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c56a2be_d0fb_4dc1_b463_c24d444cc9e7
ELIN-732770-2017 | EL-470509-2016 | 1/10/2017 3:08:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Leaning_unsupported_service_pole1.png,Leaning_unsupported_service_pole2.png Poles that support over head wiring are required to be supported to prevent them from being pulled over when under strain from the weight of supporting over head cables. This installation for a new 200A 120/240V service to a detached garage has the service conduit and meter base installed on a pole. The pole is already leaning over at a substantial angle and will have additional weight added to support the new service supply conductors that will be installed by the utility. Left uncorrected this is a shock and fire hazard if the pole leans over enough to lower the height of the service supply cables crossing the road and a vehicle hits it. Also the pole may fall over onto the ground and leave energized conductors exposed to contact from persons or vehicles. Poles that support over head wiring are required to be supported to prevent them from being pulled over when under strain from the weight of supporting over head cables. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Leaning_unsupported_service_pole2.png | file://x:/photopub/docs/0000000541/8beaa38e-5588-4fde-af44-70ec364b4469.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e913411f_85fe_4023_8a21_e60ad421c4e0
GAIN-726200-2016 | GA-425774-2016 | 12/20/2016 1:20:24 PM | ASSESS: GA: Final | png | #asFound | GA134 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | 2 | 2 | A piece of extension wire cord was used to wire the unit heater to a plug. This incorrect wiring could lead to a shock or fire hazard. | 2 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | Unit_heater_wiring.png | file://x:/photopub/docs/0000000534/1788dfb0-6b8e-4638-a8ea-4fff287689b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad7bc10e_e050_4145_b53a_410e9a09e1d4
GAUP-740564-2017 | UW-492072-2017 | 1/17/2017 6:33:55 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Cellular_core_vent.png Furnace venting installed to existing Cellular Core ABS plastic piping. Cellular Core ABS plastic piping is no longer accepted and should always be replaced with S636. Cellular Core ABS can melt causing leakage for flue gases into building leading to possible CO poisoning of occupants of building | 3 | Unapproved venting material | Cellular_core_vent.png | file://x:/photopub/docs/0000000544/1056f528-18bc-40d0-a372-4c0224109ee5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0487b7ae_f5ab_4585_b50b_40e1799f24b4
BPVIN-748373-2017 | BPV-488313-2017 | 1/30/2017 1:56:39 PM | ASSESS: BPV IN: Final (First Certification) Boiler | pdf | #asFound DHW Heaters | BP001 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | 5 | 5 | #Photo.pdf During the inspection of 2 DHW Heaters with MAWP of 100 psig I found that the T&P's had the set point at 150 psig. In case of an overpressure the T&P's would not protect the vessels and rupture could occur. | 5 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | Photo.pdf | file://x:/photopub/docs/0000000550/a9747fe2-e349-4c3f-9777-b980b06ef70a.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62648701_7961_423f_b4cb_1ed300aeb399
BPVIN-748373-2017 | BPV-488313-2017 | 1/30/2017 1:56:39 PM | ASSESS: BPV IN: Final (First Certification) Boiler | pdf | #asFound | BP001 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | 5 | 5 | #Photo.pdf During the inspection of 2 DHW Heaters with MAWP of 100 psig I found that the T&P's had the set point at 150 psig. In case of an overpressure the T&P's would not protect the vessels and rupture could occur. | 5 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | Photo.pdf | file://x:/photopub/docs/0000000550/41e9150a-080b-4760-aaee-3e4555099717.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62648701_7961_423f_b4cb_1ed300aeb399
BPVIN-748373-2017 | BPV-488313-2017 | 1/30/2017 1:56:39 PM | ASSESS: BPV IN: Final (First Certification) Boiler | pdf | #asFound | BP001 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | 5 | 5 | #Photo.pdf During the inspection of 2 DHW Heaters with MAWP of 100 psig I found that the T&P's had the set point at 150 psig. In case of an overpressure the T&P's would not protect the vessels and rupture could occur. | 5 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | Photo.pdf | file://x:/photopub/docs/0000000550/b0ad2be5-da1f-48f6-a339-ecbe98ab3975.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62648701_7961_423f_b4cb_1ed300aeb399
ELIN-718600-2016 | EL-468830-2016 | 12/7/2016 7:21:20 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found 60 amp 120/240 volt 1 phase panelboards with exposed energized conductors and bus bars in two separate residential occupancies units. When electrical equipment such as panelboards have covers missing leaving bus bars and conductors exposed and energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Switching is not done in an ungrounded conductor | a.png | file://x:/photopub/docs/0000000527/dd3a3a9a-a5fc-4511-8d96-8fddbda527b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3008b5c0_91d8_4317_a6a6_d443cd4e3bfa
GAUP-719257-2016 | UW-477466-2016 | 12/7/2016 1:40:53 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | While assessing an unpermitted installation of a hot water tank I found a small gas leak on the gas connector serving the appliance, which i was able to valve off an isolate. Should this have been left unchecked, over time raw gas could accumulate in the living space until it finds a source of ignition which could lead to a fire or explosion. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Leak_location.png | file://x:/photopub/docs/0000000527/e5882e9e-1be4-4ef1-8a58-8608ff62c037.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__536f0460_ca85_473f_a308_3742332817fb
ELHE-755498-2017 | HE-500464-2017 | 2/14/2017 9:35:57 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #B1.png,B2.png,B3.png Pigtail lights in crawl space have conductors entered into outlet box without a proper connector. This is a fire hazard and shock hazard. The conductors are exposed to injury and the terminations are exposed to strain. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | B1.png | file://x:/photopub/docs/0000000557/c0963c05-c3cd-411f-aee8-f4ce312610ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__552e9312_d40b_48e5_996e_ef81643aea1d
ELHE-755498-2017 | HE-500464-2017 | 2/14/2017 9:35:57 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #B1.png,B2.png,B3.png Pigtail lights in crawl space have conductors entered into outlet box without a proper connector. This is a fire hazard and shock hazard. The conductors are exposed to injury and the terminations are exposed to strain. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | B3.png | file://x:/photopub/docs/0000000557/be02197e-1213-45b1-b5d5-e1b16024d67b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__552e9312_d40b_48e5_996e_ef81643aea1d
ELHE-755498-2017 | HE-500464-2017 | 2/14/2017 9:35:57 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #B1.png,B2.png,B3.png Pigtail lights in crawl space have conductors entered into outlet box without a proper connector. This is a fire hazard and shock hazard. The conductors are exposed to injury and the terminations are exposed to strain. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | B2.png | file://x:/photopub/docs/0000000557/3e0268ea-61dc-4bbe-b0b6-745738c8cd16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__552e9312_d40b_48e5_996e_ef81643aea1d
ELIN-735411-2017 | EL-427990-2016 | 1/9/2017 1:40:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather1.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather2.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather3.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather4.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather5.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather6.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather7.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather8.png Found temporary construction distribution panelboards and its feeder electrical equipment to be damaged due to not being made weatherproof and protected from being damaged. When electrical equipment is not weatherproof and protecte | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather7.png | file://x:/photopub/docs/0000000543/79860006-ce43-4803-9a40-dc5d7b3241dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c56a2be_d0fb_4dc1_b463_c24d444cc9e7
ELIN-735411-2017 | EL-427990-2016 | 1/9/2017 1:40:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather1.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather2.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather3.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather4.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather5.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather6.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather7.png,temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather8.png Found temporary construction distribution panelboards and its feeder electrical equipment to be damaged due to not being made weatherproof and protected from being damaged. When electrical equipment is not weatherproof and protecte | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | temporary_construction_distribution_panelboards_not_protected_from_being_damaged_from_weather8.png | file://x:/photopub/docs/0000000543/6218345f-749c-48ec-99cc-de1c90e4afce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c56a2be_d0fb_4dc1_b463_c24d444cc9e7
BPVOP-727013-2016 | UW-449010-2016 | 10/5/2016 | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP092 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | 3 | 3 | No evidence of Hi-temperature limit control with manual reset switch installed on this boiler. This may contribute to temperature overrun and result in an incident. | 3 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | Nameplate_1.png | file://x:/photopub/docs/0000000533/8ab929a8-fc1b-4e5d-a378-20ade91343a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea81e948_4db0_4ede_b2db_89ff1ccd1f5b
BPVOP-727013-2016 | UW-449010-2016 | 10/5/2016 | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP092 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | 3 | 3 | No evidence of Hi-temperature limit control with manual reset switch installed on this boiler. This may contribute to temperature overrun and result in an incident. | 3 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | boiler_front_panel_removed.png | file://x:/photopub/docs/0000000533/f50e846b-613f-4d18-9c7b-a24adaa2841c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea81e948_4db0_4ede_b2db_89ff1ccd1f5b
BPVOP-727013-2016 | UW-449010-2016 | 10/5/2016 | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP092 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | 3 | 3 | No evidence of Hi-temperature limit control with manual reset switch installed on this boiler. This may contribute to temperature overrun and result in an incident. | 3 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | Nameplate_view_2.png | file://x:/photopub/docs/0000000533/108163ee-bc06-48b7-9e20-60395eeff5aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea81e948_4db0_4ede_b2db_89ff1ccd1f5b
BPVOP-727013-2016 | UW-449010-2016 | 10/5/2016 | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP092 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | 3 | 3 | No evidence of Hi-temperature limit control with manual reset switch installed on this boiler. This may contribute to temperature overrun and result in an incident. | 3 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | Boiler_additional_information_sticker.png | file://x:/photopub/docs/0000000533/7cc337da-abb8-46d4-81a5-7332bb5a738a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea81e948_4db0_4ede_b2db_89ff1ccd1f5b
BPVOP-727013-2016 | UW-449010-2016 | 10/5/2016 | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP092 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | 3 | 3 | No evidence of Hi-temperature limit control with manual reset switch installed on this boiler. This may contribute to temperature overrun and result in an incident. | 3 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | Prestige_boiler_overview_photo.png | file://x:/photopub/docs/0000000533/415e897c-fe90-4fb7-a561-f37331290f4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea81e948_4db0_4ede_b2db_89ff1ccd1f5b
GAIN-757032-2017 | GA-501090-2017 | 2/22/2017 12:14:28 PM | ASSESS: GA: Final | png | #asFound Second stage regulator vent to close to source of ignition. | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | #Regulator_vent.png If a overpressure situation occurs in the propane system a relief style regulator is installed to protect the system from over-pressuring. There are clearances to be met from sources ignition. In this case the clearances are not met and could lead to a potential for explosion or fire. | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | Regulator_vent.png | file://x:/photopub/docs/0000000561/5a79674e-4b7b-48f2-8079-ec754ce1b5f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83ec1a9e_7d18_4e81_b3be_11770609a089
ELIN-759773-2017 | EL-496000-2017 | 2/21/2017 3:45:58 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #No_access_and_not_weatherproof1.png,No_access_and_not_weatherproof2.png,No_access_and_not_weatherproof3.png,No_access_and_not_weatherproof4.png Service equipment is not accessible as one door is screwed shut and the other is not able to open past the roofing. Panel sides are also still exposed to weather. Roofing and sides do not cover panel. Possibility for damage to equipment or fault on system without access to circuit breakers. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | No_access_and_not_weatherproof4.png | file://x:/photopub/docs/0000000561/30e808c5-af2c-48ad-936d-dd0f59927154.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1599ac12_dc3c_4ff2_8657_3276f742b051
ELIN-759773-2017 | EL-496000-2017 | 2/21/2017 3:45:58 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #No_access_and_not_weatherproof1.png,No_access_and_not_weatherproof2.png,No_access_and_not_weatherproof3.png,No_access_and_not_weatherproof4.png Service equipment is not accessible as one door is screwed shut and the other is not able to open past the roofing. Panel sides are also still exposed to weather. Roofing and sides do not cover panel. Possibility for damage to equipment or fault on system without access to circuit breakers. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | No_access_and_not_weatherproof2.png | file://x:/photopub/docs/0000000561/ea030109-0174-4e71-8f40-f9bceed5c6e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1599ac12_dc3c_4ff2_8657_3276f742b051
ELIN-760343-2017 | EL-501082-2017 | 2/21/2017 3:51:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Exposed_panel.png Panel is exposed to weather and can possibly be damaged and not function correctly. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Exposed_panel.png | file://x:/photopub/docs/0000000561/d958f551-4dc1-498b-8747-e41a8e0d6477.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef024989_83a1_4419_8c1e_a0fe13004833
ELIN-714739-2016 | EL-461355-2016 | 12/12/2016 1:24:23 PM | ASSESS: EL: Service Connection | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 2 | A 100 amp 240 volt feeder from a permanent residential service to a new sub panel in a newly constructed dwelling had the neutral conductor connected using a lug that was not approved for the purpose. This can lead to loose connection of the neutral conductor and be a risk to property and persons. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Jury_rigged_lug_in_seimens_panel.png | file://x:/photopub/docs/0000000530/cef5323a-1119-4e9a-bce2-d341c85de5f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7658738e_40f1_48a0_af36_8b17993b5b3a
ELIN-719442-2016 | EL-466635-2016 | 12/12/2016 11:17:12 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | A house under construction was found to have 2 construction heaters operating on a 30 and a 40 amp 240 volt supply. the heaters had the cord caps removed, hazardous extension of the cables for the heaters installed, and were hard wired to permanent wiring to the future range and dryer locations. At both locations the cables were connected to the range and dryer wiring lacking adequate support and strain relief. This can lead to injury of workers and potential for fire for the dwelling. | 4 | Conductors, Misuse of flexible cords. | Unit_heater_connection_to_dryer_and_range_receptacles_identical.png | file://x:/photopub/docs/0000000530/dd06c375-2f23-4332-ab9f-a04d794dfc77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__adaa2715_5c54_4fd2_b022_140efe15eb03
GAIN-751398-2017 | GA-483514-2016 | 2/6/2017 1:24:41 PM | ASSESS: GA: Final | png | #asFound | GA075 | Required clearances not met | 2 | 2 | #ReliefDevice.png Relief device installed to close to air intake. If relief device were to vent, the gas would enter the air intake and create an unsafe gas/air mixture in the combustion chamber. | 2 | Required clearances not met | ReliefDevice.png | file://x:/photopub/docs/0000000554/5362b038-4947-43bd-b449-dc45231e4649.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c96a7b14_ed73_4dac_8c08_0ee93d3f211b
GAIN-747835-2017 | GA-496123-2017 | 2/6/2017 4:17:08 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | #Regulator_in_the_vertical_position.png Regulator not installed in accordance with certified manufacturers installation instructions. Regulator must be installed with the vent limiter in the vertical position. | 2 | Not installed according to certified installation instructions | Regulator_in_the_vertical_position.png | file://x:/photopub/docs/0000000554/40f97bda-70ac-41bf-9bc4-4a2d8c181195.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8989755_910d_4228_ab6a_3c1de31e069b
ELHE-757655-2017 | HE-444247-2016 | 1/31/2017 3:52:33 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #No_bed_of_sand_installed1.png,No_bed_of_sand_installed2.png When ESO attended site the non-metallic sheathed cable was in trench and not provided with a bed of sand to protect the cable from mechanical injury. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | No_bed_of_sand_installed1.png | file://x:/photopub/docs/0000000557/777c39e2-9c23-4056-852c-0ac89d0c0d20.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dddd76b4_4742_4e35_9119_be55068b0740
ELHE-757655-2017 | HE-444247-2016 | 1/31/2017 3:52:33 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #No_bed_of_sand_installed1.png,No_bed_of_sand_installed2.png When ESO attended site the non-metallic sheathed cable was in trench and not provided with a bed of sand to protect the cable from mechanical injury. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | No_bed_of_sand_installed2.png | file://x:/photopub/docs/0000000557/697b0059-c330-444c-9470-30163021268a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dddd76b4_4742_4e35_9119_be55068b0740
ELIN-749109-2017 | EL-427081-2016 | 2/6/2017 9:18:59 AM | ASSESS: EL: Final | png | #asFound Extension cord not properly fastened or seated within cord end | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Noticed_condition__noticed_condition_of_extension_cord.png 15 amp temporary construction receptacle is not GFCI protected. There's a possibility that an electric shock could occur due to improper use of extension cords or equipment. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Noticed_condition__noticed_condition_of_extension_cord.png | file://x:/photopub/docs/0000000554/029d43ef-edfe-44b3-b8a9-4cf32dfef4cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68196bfd_0b4e_46a3_85b6_c4b07fa6b026
GAIN-758659-2017 | GA-443524-2016 | 2/22/2017 4:30:59 PM | ASSESS: GA: Final | png | #asFound Combustion air intake not goosenecked nor is the exhaust terminated correctly | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Venting.png The Air intake and the exhaust for the boiler shall terminate according to the manufacturer instructions and the gas code B149.1 -2015. In this case the arrangement of the venting and air intake may cause the boiler to operate incorrectly causing exhaust gases to enter the combustion air pipe, causing pre-mature failure of the boiler. | 3 | Appliance not installed according to installation instructions | Venting.png | file://x:/photopub/docs/0000000561/aeb135dc-1319-432a-8c27-bede11d47dd2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6c41e4a_7fd4_40fc_b652_87d459626094
ELIN-740962-2017 | EL-452336-2016 | 1/19/2017 11:34:31 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #F21.png,F22.png,F23.png,F24.png,F25.png,F26.png Circuits and outlets are energized without covers and contractor is calling for a FINAL inspection. No request was submitted to BCSA to energize permanent wiring circuits during construction. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | F26.png | file://x:/photopub/docs/0000000545/43287b17-3c91-460e-9d99-679b5d38fc06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0315eaaa_8904_4358_bdbf_32cc0a647496
ELIN-740962-2017 | EL-452336-2016 | 1/19/2017 11:34:31 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #F21.png,F22.png,F23.png,F24.png,F25.png,F26.png Circuits and outlets are energized without covers and contractor is calling for a FINAL inspection. No request was submitted to BCSA to energize permanent wiring circuits during construction. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | F22.png | file://x:/photopub/docs/0000000545/556f9edd-d949-4525-87d9-ca10bb2fa6d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0315eaaa_8904_4358_bdbf_32cc0a647496
ELIN-740962-2017 | EL-452336-2016 | 1/19/2017 11:34:31 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #F21.png,F22.png,F23.png,F24.png,F25.png,F26.png Circuits and outlets are energized without covers and contractor is calling for a FINAL inspection. No request was submitted to BCSA to energize permanent wiring circuits during construction. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | F24.png | file://x:/photopub/docs/0000000545/bf21b8f2-2012-4eb8-9f48-d2a96466842c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0315eaaa_8904_4358_bdbf_32cc0a647496
ELIN-740962-2017 | EL-452336-2016 | 1/19/2017 11:34:31 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #F21.png,F22.png,F23.png,F24.png,F25.png,F26.png Circuits and outlets are energized without covers and contractor is calling for a FINAL inspection. No request was submitted to BCSA to energize permanent wiring circuits during construction. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | F25.png | file://x:/photopub/docs/0000000545/8e79c59a-ccbf-4208-9a15-7a67dc74273f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0315eaaa_8904_4358_bdbf_32cc0a647496
ELIN-740962-2017 | EL-452336-2016 | 1/19/2017 11:34:31 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #F21.png,F22.png,F23.png,F24.png,F25.png,F26.png Circuits and outlets are energized without covers and contractor is calling for a FINAL inspection. No request was submitted to BCSA to energize permanent wiring circuits during construction. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | F23.png | file://x:/photopub/docs/0000000545/2962662b-2a68-4920-a57b-a8bde6df7efa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0315eaaa_8904_4358_bdbf_32cc0a647496
ELIN-740962-2017 | EL-452336-2016 | 1/19/2017 11:34:31 AM | ASSESS: EL: Final | png | #asFound Final inspection is called. Work is not completed. Outlets are without covers. | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #F21.png,F22.png,F23.png,F24.png,F25.png,F26.png Circuits and outlets are energized without covers and contractor is calling for a FINAL inspection. No request was submitted to BCSA to energize permanent wiring circuits during construction. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | F21.png | file://x:/photopub/docs/0000000545/c247cd8c-915a-46c9-a7c0-29ec23a524fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0315eaaa_8904_4358_bdbf_32cc0a647496
ELIN-730266-2016 | EL-346283-2016 | 12/29/2016 3:46:49 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cable | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable-2.png | file://x:/photopub/docs/0000000536/fca37685-1618-4819-ab78-5564c929afd7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__50ff526b_7c09_401c_918b_75d938c4b90f
GAIN-747577-2017 | GA-493048-2017 | 1/31/2017 11:24:18 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | #Vent_termination.png Horizontal vent termination too close to an electrical meter. The condensate from the vent may drip onto the electrical meter possibly leading to an electrical short and fire. | 2 | Side wall vent termination not compliant with installation instructions | Vent_termination.png | file://x:/photopub/docs/0000000550/0c7fd335-2739-4056-8b36-8dc78b6d7807.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c73c99ca_3cbc_401c_a457_ab1410e2a802
GAIN-747577-2017 | GA-493048-2017 | 1/31/2017 11:24:18 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | #Vent_termination.png Horizontal vent termination too close to an electrical meter. The condensate from the vent may drip onto the electrical meter possibly leading to an electrical short and fire. | 2 | Side wall vent termination not compliant with installation instructions | Vent_termination.png | file://x:/photopub/docs/0000000550/5589a40b-c88e-492b-a27a-9bc6a34b55f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c73c99ca_3cbc_401c_a457_ab1410e2a802
GAIN-747577-2017 | GA-493048-2017 | 1/31/2017 11:24:18 AM | ASSESS: GA: Final | png | #asFound Horizontal clearance to electrical meter. | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | #Vent_termination.png Horizontal vent termination too close to an electrical meter. The condensate from the vent may drip onto the electrical meter possibly leading to an electrical short and fire. | 2 | Side wall vent termination not compliant with installation instructions | Vent_termination.png | file://x:/photopub/docs/0000000550/58d043c5-5aca-4472-9002-1ec0d16a3a2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c73c99ca_3cbc_401c_a457_ab1410e2a802
GAIN-707572-2016 | GA-418584-2016 | 12/13/2016 11:11:31 AM | ASSESS: GA: Final | png | #asFound | GA003 | Provision for expansion Incorrect swing joint | 2 | 2 | Provisions shall be made for the settling of ground and frost heaving, this is made by providing a proper 3 or 5 elbow swing joint at meter set and for example, a separate riser take off on the system, if these provisions are not made this could cause undue stress on the piping system and cause a gas leak to happen. | 2 | Provision for expansion Incorrect swing joint | No_swing_joint.png | file://x:/photopub/docs/0000000530/96501f88-68a1-484b-8ba7-0f973b7f26cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__829d9455_a3eb_498f_bb5a_65143f2421bb
GAIN-697091-2016 | GA-458935-2016 | 12/13/2016 12:28:01 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | A return air grill takes in air from the house and this is circulated by a blower fan located in the furnace. One of these grills is installed on the furnace return duct in the same room as the furnace this is not to manufacturers instructions and should be placed in a safer location as natural gas appliances have the potential of creating a hazardous condition such as carbon monoxide. | 3 | Appliance not installed according to installation instructions | Return_air_grill_installed_in_furnace_room.png | file://x:/photopub/docs/0000000530/a3807791-af0c-4166-b3fd-a2ddb321ff2c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15385d53_04e5_412f_9237_dc9a7531b0ca
ELIN-722396-2016 | EL-461876-2016 | 12/14/2016 12:37:47 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | NMD-90 cable is installed to close to the edge of a 2x4 stud without mechanical protection. Cable should be 32mm from edge of 2x4 stud. This is a shock hazard condition. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD-90_cable_installed_to_close_to_the_edge_of_stud_wall.png | file://x:/photopub/docs/0000000531/bb99cc96-cd04-44c0-82b9-635c003a1f32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd89e516_2425_4d53_b8a8_87d108f1cc6c
ELIN-739853-2017 | EL-491471-2017 | 1/18/2017 1:01:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Meter_and_mast_installation1.png,Meter_and_mast_installation2.png Service mast is attached to siding boards with mast mounted clevis. Supply conductors exceed 30m. Meter is mounted with unapproved mounting device. Service can be pulled from building resulting in fire and shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Meter_and_mast_installation1.png | file://x:/photopub/docs/0000000545/0bb96200-e421-40b0-aaaa-d30b70121a25.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6188bb8e_c948_4f4f_95d0_d00c10994deb
ELIN-739853-2017 | EL-491471-2017 | 1/18/2017 1:01:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Meter_and_mast_installation1.png,Meter_and_mast_installation2.png Service mast is attached to siding boards with mast mounted clevis. Supply conductors exceed 30m. Meter is mounted with unapproved mounting device. Service can be pulled from building resulting in fire and shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Meter_and_mast_installation2.png | file://x:/photopub/docs/0000000545/e5443855-5a1c-457b-8eca-865a0651c89d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6188bb8e_c948_4f4f_95d0_d00c10994deb
ELHE-730805-2016 | HE-485615-2016 | 12/30/2016 8:07:57 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Overhead conductors mounted on rotten poles. This is a fire and shock hazard. These poles were swaying the breeze. If they fall over they can rip the conductors off of the house. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 1.png | file://x:/photopub/docs/0000000537/86624212-99f0-4bae-a3a8-0f352fd16de7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c00d0eb_69bc_4be0_8519_de1b8a78cda2
ELHE-730805-2016 | HE-485615-2016 | 12/30/2016 8:07:57 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Overhead conductors mounted on rotten poles. This is a fire and shock hazard. These poles were swaying the breeze. If they fall over they can rip the conductors off of the house. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4.png | file://x:/photopub/docs/0000000537/8ad3b896-1465-4367-a5bd-5d58e75b4e6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c00d0eb_69bc_4be0_8519_de1b8a78cda2
ELIN-730835-2016 | EL-470962-2016 | 12/30/2016 10:19:05 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | Minimum working clearances around electrical equipment not provided. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | A.png | file://x:/photopub/docs/0000000537/ddbba3dc-7aa0-4c61-a6b2-cf520f953307.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9786ae4e_0e12_43ee_a223_e6ae15cb5b21
ELHE-759777-2017 | HE-502633-2017 | 2/20/2017 12:36:02 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #El_room_clearance.png electrical equipment located in room with very little clearances for safe work or access. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | El_room_clearance.png | file://x:/photopub/docs/0000000560/a28e79ef-9c01-495b-88ae-f64eaa7e3dce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8cf84037_758c_47e6_a7ba_835ddd15394b
GAIN-728057-2016 | GA-483472-2016 | 12/22/2016 2:32:06 PM | ASSESS: GA: Final | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | Two gas branch lines were open on the ends inside of a home under renovation. The lines were connected to a live gas manifold in the basement with only a single shutoff valve each stopping gas flow through the tubing. If the shut off valves were opened gas would flow through the tubing into the house potentially causing a fire or explosion. | 5 | Open gas line connected to fuel supply (no cap/plug) | Open_CSST.png | file://x:/photopub/docs/0000000534/a7a06a4d-879b-494d-b163-fb4e30b3cb00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7961c69a_e20a_4c65_a332_ea073fe03083
ELIN-757971-2017 | EL-414364-2016 | 2/22/2017 11:01:27 AM | ASSESS: EL: Service Connection | png | #asFound Structural support for mast has not been provided. | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #Mast_supports_secured_only_in_to_plywood_.png Service mast has not been adequately supported to structure. When using OSB plywood is used as support the OSB may deteriorate over time and the weight of the service conductors pulling on the mast could cause the mast to fall over. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Mast_supports_secured_only_in_to_plywood_.png | file://x:/photopub/docs/0000000561/0b663dc0-8d92-4b54-bd71-022957b06598.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc195ea5_ba56_427a_83d5_0cd1f0d97a15
ELIN-760232-2017 | EL-502923-2017 | 2/21/2017 1:34:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | #Temporary_pole1.png,Temporary_pole2.png Distribution is exposed to weather and temporary pole not braced. Possibility for damage to equipment. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Temporary_pole2.png | file://x:/photopub/docs/0000000561/614cea78-7111-4a9d-a2c9-d564e9a9b9f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ec8da10_2d07_4861_be1c_228d7fe08d5f
ELIN-759773-2017 | EL-496000-2017 | 2/21/2017 3:45:58 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #No_access_and_not_weatherproof1.png,No_access_and_not_weatherproof2.png,No_access_and_not_weatherproof3.png,No_access_and_not_weatherproof4.png Service equipment is not accessible as one door is screwed shut and the other is not able to open past the roofing. Panel sides are also still exposed to weather. Roofing and sides do not cover panel. Possibility for damage to equipment or fault on system without access to circuit breakers. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | No_access_and_not_weatherproof3.png | file://x:/photopub/docs/0000000561/b2e24543-4965-410a-a394-b97aeb4e2079.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1599ac12_dc3c_4ff2_8657_3276f742b051
ELIN-759773-2017 | EL-496000-2017 | 2/21/2017 3:45:58 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #No_access_and_not_weatherproof1.png,No_access_and_not_weatherproof2.png,No_access_and_not_weatherproof3.png,No_access_and_not_weatherproof4.png Service equipment is not accessible as one door is screwed shut and the other is not able to open past the roofing. Panel sides are also still exposed to weather. Roofing and sides do not cover panel. Possibility for damage to equipment or fault on system without access to circuit breakers. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | No_access_and_not_weatherproof1.png | file://x:/photopub/docs/0000000561/018a7271-a6f1-4299-9c01-5d6b6c90714d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1599ac12_dc3c_4ff2_8657_3276f742b051
ELIN-760232-2017 | EL-502923-2017 | 2/21/2017 1:34:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | #Temporary_pole1.png,Temporary_pole2.png Distribution is exposed to weather and temporary pole not braced. Possibility for damage to equipment. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Temporary_pole1.png | file://x:/photopub/docs/0000000561/f6be4047-e2af-4a63-9c7c-b3c5b714f2e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ec8da10_2d07_4861_be1c_228d7fe08d5f
GAHE-724899-2016 | HE-481887-2016 | 12/14/2016 12:54:54 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 |  | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | First_stage_reg.png | file://x:/photopub/docs/0000000533/6189e944-28c4-4b9b-b89f-1dff4ba9fdc7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3f72949_705f_4785_8e4d_2fd2e776edf0
ELIN-725900-2016 | EL-482474-2016 | 12/20/2016 8:44:32 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Hot water tank was removed with NMD90 cable left hanging and not installed in a box or removed from panel. Conductors could become energized and accessed by the public. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | HWT_cable.png | file://x:/photopub/docs/0000000534/d1623111-3202-4e63-a2ff-84f9b162b9e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1e9144a_3113_4543_852b_9c8bbe213ada
ELIN-723824-2016 | EL-462930-2016 | 12/21/2016 8:28:40 AM | ASSESS: EL: Final | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | Electrical sub panel located in kitchen. Cupboard. -Panel subject to mechanical damage -Panel does not have safe work clearances for maintenance | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Cupboard_panel.png | file://x:/photopub/docs/0000000534/6e1c36a3-9ce0-4217-ad1a-d7afcd7fba00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a277a47e_3632_42a0_b0f7_e3e98f85cbdb
ELIN-737339-2017 | EL-455627-2016 | 1/12/2017 11:29:43 AM | ASSESS: EL: Final | png | #asFound | EL191 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | 3 | 3 | #Dishwasher_feed_enrgized.png Dishwasher feed is not terminated in dishwasher or device box with a cover if dishwasher is not being installed. Non metallic sheathed cable feeding dishwasher was found in an energized state. Accidental contact with energized conductors poses a risk of shock or fire to persons or property. | 3 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | Dishwasher_feed_enrgized.png | file://x:/photopub/docs/0000000542/fa640eae-d431-4576-af1f-45b8fe415b8e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12d41db4_cd0c_4fc0_8205_691826d5f638
ELHE-730805-2016 | HE-485615-2016 | 12/30/2016 8:07:57 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Overhead conductors mounted on rotten poles. This is a fire and shock hazard. These poles were swaying the breeze. If they fall over they can rip the conductors off of the house. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 2.png | file://x:/photopub/docs/0000000537/2ae11037-14e2-4c90-87b2-6b260eda1ba1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c00d0eb_69bc_4be0_8519_de1b8a78cda2
ELHE-730805-2016 | HE-485615-2016 | 12/30/2016 8:07:57 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Overhead conductors mounted on rotten poles. This is a fire and shock hazard. These poles were swaying the breeze. If they fall over they can rip the conductors off of the house. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 5.png | file://x:/photopub/docs/0000000537/c5dc1852-b569-4b60-9bbc-65df6ef5cbf7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c00d0eb_69bc_4be0_8519_de1b8a78cda2
ELHE-730805-2016 | HE-485615-2016 | 12/30/2016 8:07:57 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Overhead conductors mounted on rotten poles. This is a fire and shock hazard. These poles were swaying the breeze. If they fall over they can rip the conductors off of the house. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 3.png | file://x:/photopub/docs/0000000537/4dc64925-117d-42a6-b9c8-a8b02147571e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c00d0eb_69bc_4be0_8519_de1b8a78cda2
ELIN-730835-2016 | EL-470962-2016 | 12/30/2016 10:19:05 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | Minimum working clearances around electrical equipment not provided. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | H.png | file://x:/photopub/docs/0000000537/e808911a-57bf-4fa1-9c25-fc6cb6e794f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9786ae4e_0e12_43ee_a223_e6ae15cb5b21
GAIN-715450-2016 | GA-443754-2016 | 1/3/2017 2:07:07 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | Vent_limiter.png | file://x:/photopub/docs/0000000538/1cc46c99-030f-4067-b0c8-72954f4cc7cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32a5eec4_5069_49e6_b550_343b089702f7
GAIN-726386-2016 | GA-479697-2016 | 1/3/2017 9:49:26 AM | ASSESS: GA: Final | png | #asFound | GA039 | Painting of exterior piping | 1 | 1 | Exterior black iron pipe must be painted with a rust coat paint, if exterior piping is not protected against the elements the piping could eventually develop a leak from pre-mature deterioration. | 1 | Painting of exterior piping | Exterior_piping.png | file://x:/photopub/docs/0000000537/134af868-f91c-431a-bd04-2b4b189c93a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__205842fe_5f78_4301_bded_5fc7620fc95e
ELHE-754296-2017 | HE-495675-2017 | 2/9/2017 10:33:38 AM | ASSESS: EL HE: Hazard Elimination | jpg | #asFound Service room. Service is overloaded and has open energized panel | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #9e10d57e-e2ac-416e-8ca6-dcafd5501b68.jpg Assessment in response to Ministry of Lands, Water & Natural Resources with RCMP. BC Hydro load readings have determined that the electrical service on this industrial property is overloaded. The metal door of the service entrance fused switch was also hot to the touch. It is a fire hazard if a connection comes loose or a safety device such as one of the main fuses fails to operate. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 9e10d57e-e2ac-416e-8ca6-dcafd5501b68.jpg | file://x:/photopub/docs/0000000555/bde6d22d-0a00-4a33-9eae-e1473d9227d5.jpg | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6cb3e49_6031_43ce_986d_a7812d35247d
ELHE-754296-2017 | HE-495675-2017 | 2/9/2017 10:33:38 AM | ASSESS: EL HE: Hazard Elimination | jpg | #asFound Service room. BC Hydro on site indicating that load readings are in excess of the allowable. Metal door on service entrance fused switch is hot to the touch. | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #9e10d57e-e2ac-416e-8ca6-dcafd5501b68.jpg Assessment in response to Ministry of Lands, Water & Natural Resources with RCMP. BC Hydro load readings have determined that the electrical service on this industrial property is overloaded. The metal door of the service entrance fused switch was also hot to the touch. It is a fire hazard if a connection comes loose or a safety device such as one of the main fuses fails to operate. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 9e10d57e-e2ac-416e-8ca6-dcafd5501b68.jpg | file://x:/photopub/docs/0000000555/8f00918d-b97e-42ef-b1ca-68249fde50b6.jpg | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6cb3e49_6031_43ce_986d_a7812d35247d
ELHE-754296-2017 | HE-495675-2017 | 2/9/2017 10:33:38 AM | ASSESS: EL HE: Hazard Elimination | jpg | #asFound Un-secured service room. Service was overloaded | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #9e10d57e-e2ac-416e-8ca6-dcafd5501b68.jpg Assessment in response to Ministry of Lands, Water & Natural Resources with RCMP. BC Hydro load readings have determined that the electrical service on this industrial property is overloaded. The metal door of the service entrance fused switch was also hot to the touch. It is a fire hazard if a connection comes loose or a safety device such as one of the main fuses fails to operate. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 9e10d57e-e2ac-416e-8ca6-dcafd5501b68.jpg | file://x:/photopub/docs/0000000555/f1c27afd-df36-48ed-9876-cbed4f5dd017.jpg | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6cb3e49_6031_43ce_986d_a7812d35247d
ELIN-760234-2017 | EL-352256-2016 | 2/21/2017 10:05:05 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Found non-metallic sheathed cables located in roof attic space that measures more than one meter between ceiling joists and top roof rafter and these cables have no mechanical protection or running boards to protect cables from possible mechanical damages. When electrical equipment is not mechanically protected from possible mechanical damage the electrical equipment could get damaged and could cause an electrical fire or shock hazard to people and property. | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #Non-metallic_sheathed_cable_in_roof_attic_non-compliances1.png,Non-metallic_sheathed_cable_in_roof_attic_non-compliances2.png Found non-metallic sheathed cables located in roof attic space that measures more than one meter between ceiling joists and top roof rafter and these cables have no mechanical protection or running boards to protect cables from possible mechanical damages. When electrical equipment is not mechanically protected from possible mechanical damage the electrical equipment could get damaged and could cause an electrical fire or shock hazard to people and property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Non-metallic_sheathed_cable_in_roof_attic_non-compliances2.png | file://x:/photopub/docs/0000000561/3b71e33c-c75b-4c42-ae71-8e21714aa405.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__231bcbd4_c0eb_45b8_adfd_92cce5da8982
ELIN-760234-2017 | EL-352256-2016 | 2/21/2017 10:05:05 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Found non-metallic sheathed cables located in roof attic space that measures more than one meter between ceiling joists and top roof rafter and these cables have no mechanical protection or running boards to protect cables from possible mechanical damages. When electrical equipment is not mechanically protected from possible mechanical damage the electrical equipment could get damaged and could cause an electrical fire or shock hazard to people and property. | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #Non-metallic_sheathed_cable_in_roof_attic_non-compliances1.png,Non-metallic_sheathed_cable_in_roof_attic_non-compliances2.png Found non-metallic sheathed cables located in roof attic space that measures more than one meter between ceiling joists and top roof rafter and these cables have no mechanical protection or running boards to protect cables from possible mechanical damages. When electrical equipment is not mechanically protected from possible mechanical damage the electrical equipment could get damaged and could cause an electrical fire or shock hazard to people and property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Non-metallic_sheathed_cable_in_roof_attic_non-compliances1.png | file://x:/photopub/docs/0000000561/a7818fec-a48b-4246-ba16-eba0c2ef8632.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__231bcbd4_c0eb_45b8_adfd_92cce5da8982
PROP-744303-2017 | 2224061 | 1/23/2017 8:27:30 AM | ASSESS: PR OP: Operational | png | #asFound Mobile grooming machine (snowcat) hit anchor bolt of tower. | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | #Anchor_bolt_hit_by_groomer.png | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Anchor_bolt_hit_by_groomer.png | file://x:/photopub/docs/0000000548/51288884-7e50-4236-9f74-c21e3c7b25a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b45a3527_c9f3_484a_b5fa_bb3216320392
GAIN-728084-2016 | GA-441717-2016 | 1/25/2017 7:34:37 AM | ASSESS: GA: Final | png | #asFound | GA116 | Supports/termination present, but not in compliance with mfg instructions | 1 | 2 | #Tim.png Combustion and exhaust termination not compliant to meet snow load or elbows. Water could be introduced into combustion chamber of water heater causing component failure | 1 | Supports/termination present, but not in compliance with mfg instructions | Tim.png | file://x:/photopub/docs/0000000548/82747091-6181-4157-9c84-33b31a5c0d5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4b421b1_bc95_4ef5_bc9e_4498f105847c
ELIN-759974-2017 | EL-490336-2017 | 2/20/2017 1:42:06 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Image_7-81.png,Image_7-82.png Energized service conductors in conduit not approved for surface use. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Image_7-81.png | file://x:/photopub/docs/0000000559/015cb15f-4bb4-4222-a2f6-70c64dcdcbc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e282b67e_1b29_40f4_87ec_e0bae84979a6
ELIN-737339-2017 | EL-455627-2016 | 1/12/2017 11:29:43 AM | ASSESS: EL: Final | png | #asFound | EL191 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | 3 | 3 | #Dishwasher_feed_enrgized.png Dishwasher feed is not terminated in dishwasher or device box with a cover if dishwasher is not being installed. Non metallic sheathed cable feeding dishwasher was found in an energized state. Accidental contact with energized conductors poses a risk of shock or fire to persons or property. | 3 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | Dishwasher_feed_enrgized.png | file://x:/photopub/docs/0000000542/12f5a58d-abba-4b7f-9f60-d325cd9dfd64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12d41db4_cd0c_4fc0_8205_691826d5f638
ELIN-737339-2017 | EL-455627-2016 | 1/12/2017 11:29:43 AM | ASSESS: EL: Final | png | #asFound | EL191 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | 3 | 3 | #Dishwasher_feed_enrgized.png Dishwasher feed is not terminated in dishwasher or device box with a cover if dishwasher is not being installed. Non metallic sheathed cable feeding dishwasher was found in an energized state. Accidental contact with energized conductors poses a risk of shock or fire to persons or property. | 3 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | Dishwasher_feed_enrgized.png | file://x:/photopub/docs/0000000542/e0ec0898-4b81-4413-8ddf-c21c42f2df8e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12d41db4_cd0c_4fc0_8205_691826d5f638
GAIN-747172-2017 | GA-495837-2017 | 1/30/2017 11:44:30 AM | ASSESS: GA: Final | png | #asFound | GA069 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | 3 | 3 | #Cowichan_lake.png Gas line undersized for connected load. If all appliances are in use,pressure could drop below the required minimum required for proper operation. Possible delayed ignition and or improper combustion resulting in the production of carbon monoxide. | 3 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | Cowichan_lake.png | file://x:/photopub/docs/0000000550/15ee1590-5fa5-4ab4-ab68-1ee5cb66c327.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c4d862b_6416_439b_8870_cc0d5c5e1999
GAIN-743982-2017 | GA-488890-2017 | 1/27/2017 1:45:13 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #King_George_4.png,King_george.png Appliance sidewall vented, not listed as an approved method by manufacturer. Possibly of spillage of exhaust products due to improper draft. Possible risk of carbon oxide . | 3 | Appliance not installed according to installation instructions | King_george.png | file://x:/photopub/docs/0000000550/05fa281e-6a74-4881-9d7c-78b9f40f6754.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__100c1e1b_62f2_4a40_9012_ff1719ad90a2
ELOP-651564-2016 | 1302 | 1/31/2017 7:30:29 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL159 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | 3 | 3 | #20amp_breaker_protecting_15amp_receptacle1.png,20amp_breaker_protecting_15amp_receptacle2.png In an existing commercial school, a 15amp dedicated refrigerator receptacle was observed to have a 20amp breaker protecting the circuit. This can lead to a "Power supply/System interrupt" condition. Pic is attached. | 3 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | 20amp_breaker_protecting_15amp_receptacle1.png | file://x:/photopub/docs/0000000550/12950a88-871d-4503-a307-0e2f63b3f4a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65903D66_7BDB_4524_B222_7A83D29F7495
ELOP-651564-2016 | 1302 | 1/31/2017 7:30:29 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL159 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | 3 | 3 | #20amp_breaker_protecting_15amp_receptacle1.png,20amp_breaker_protecting_15amp_receptacle2.png In an existing commercial school, a 15amp dedicated refrigerator receptacle was observed to have a 20amp breaker protecting the circuit. This can lead to a "Power supply/System interrupt" condition. Pic is attached. | 3 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | 20amp_breaker_protecting_15amp_receptacle2.png | file://x:/photopub/docs/0000000550/1e04a96f-3623-4b00-ac68-7d16fa82613b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65903D66_7BDB_4524_B222_7A83D29F7495
ELIN-758862-2017 | EL-394954-2016 | 2/17/2017 11:43:22 AM | ASSESS: EL: Service Connection | png | #asFound Panel fillers missing and live exposed bus bar are present | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Panel_fillers.png Description of hazards are too numerous to document, panel fillers missing from panelboard that results in the likelihood and possibility of someone making contact with live expose busbars and being electrocuted or injured | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Panel_fillers.png | file://x:/photopub/docs/0000000558/1feaf66e-c615-4816-a68b-4b0ea3ee5536.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f3978458_5465_41f2_af6a_cebde9ffbf4c
EDMA-730880-2016 | ED-430566-2016 | 12/29/2016 9:27:43 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | Engineered documentation required for counterweight guide fastening method | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | CWT_guide.png | file://x:/photopub/docs/0000000536/e8532eb7-e716-4ae2-a9c0-718292979eb7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78f0c50f_698f_4a1e_ad34_615c96ebfdf1
BPVIN-575606-2016 | UW-356804-2016 | 2/20/2017 10:44:22 AM | ASSESS: BPV IN: Final (First Certification) Boiler | jpg | #asFound SV | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | #IMG_20170216_205028.jpg During the inspection of a HP Electric Steam Boiler with MAWP of 100 psig was found that the capacity of the Safety Valve was smaller than the minimum required by the boiler manufacturer. In case of a steam release by the Safety Relief over-pressure can occur. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | IMG_20170216_205028.jpg | file://x:/photopub/docs/0000000560/90a76606-f44e-4169-9e83-e3ccdd5cb511.jpg | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee4b8ed0_2068_4674_9587_e7d170de6b8b
BPVIN-575606-2016 | UW-356804-2016 | 2/20/2017 10:44:22 AM | ASSESS: BPV IN: Final (First Certification) Boiler | jpg | #asFound SV | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | #IMG_20170216_205028.jpg During the inspection of a HP Electric Steam Boiler with MAWP of 100 psig was found that the capacity of the Safety Valve was smaller than the minimum required by the boiler manufacturer. In case of a steam release by the Safety Relief over-pressure can occur. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | IMG_20170216_205028.jpg | file://x:/photopub/docs/0000000560/57942331-ce83-4257-987a-2020d83bfbab.jpg | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee4b8ed0_2068_4674_9587_e7d170de6b8b
ELIN-731913-2017 | EL-332490-2016 | 1/16/2017 11:58:44 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Image_11.png,Image_12.png,Image_13.png,Image_14.png,Image_15.png Wiring exposed to mechanical damage and open to environment. | 3 | Conductors Equipment is not approved for the specific use. | Image_15.png | file://x:/photopub/docs/0000000543/c40ae58c-69d1-4602-b4a1-0cc29fc1c18b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1844ded5_991e_4ea9_ad69_f5cce70516d3
ELIN-731913-2017 | EL-332490-2016 | 1/16/2017 11:58:44 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Image_11.png,Image_12.png,Image_13.png,Image_14.png,Image_15.png Wiring exposed to mechanical damage and open to environment. | 3 | Conductors Equipment is not approved for the specific use. | Image_11.png | file://x:/photopub/docs/0000000543/8a11e8ff-831e-4dbe-9ac3-e8db01aa16b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1844ded5_991e_4ea9_ad69_f5cce70516d3
ELIN-731913-2017 | EL-332490-2016 | 1/16/2017 11:58:44 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Image_11.png,Image_12.png,Image_13.png,Image_14.png,Image_15.png Wiring exposed to mechanical damage and open to environment. | 3 | Conductors Equipment is not approved for the specific use. | Image_12.png | file://x:/photopub/docs/0000000543/dcdd0220-d331-429d-8401-1f5fa55e9df0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1844ded5_991e_4ea9_ad69_f5cce70516d3
ELIN-731913-2017 | EL-332490-2016 | 1/16/2017 11:58:44 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Image_11.png,Image_12.png,Image_13.png,Image_14.png,Image_15.png Wiring exposed to mechanical damage and open to environment. | 3 | Conductors Equipment is not approved for the specific use. | Image_13.png | file://x:/photopub/docs/0000000543/a15ffbb0-3bac-4aab-9939-f05c952812f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1844ded5_991e_4ea9_ad69_f5cce70516d3
ELIN-731913-2017 | EL-332490-2016 | 1/16/2017 11:58:44 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Image_11.png,Image_12.png,Image_13.png,Image_14.png,Image_15.png Wiring exposed to mechanical damage and open to environment. | 3 | Conductors Equipment is not approved for the specific use. | Image_14.png | file://x:/photopub/docs/0000000543/88df04d1-e974-4d9b-978b-7ef400087d82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1844ded5_991e_4ea9_ad69_f5cce70516d3
PROP-599968-2016 | 2224086 | 12/7/2016 9:50:28 AM | ASSESS: PR OP: RAP | png | #asFound | PR035 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Using incorrect components (bicycle brake pad) to hold a handle on the rope tow. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Incorrect_component.png | file://x:/photopub/docs/0000000528/647d818b-d0f1-4583-8807-1aaf08d20935.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__F7EBE931_1022_4737_819C_A275C7375CDE
PROP-599967-2016 | 2224085 | 12/7/2016 10:34:15 AM | ASSESS: PR OP: RAP | png | #asFound | PR044 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | 3 | 3 | Function of button not identified. | 3 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | Button_not_identified.png | file://x:/photopub/docs/0000000528/190206c0-0aa8-46c6-ad68-f5bc1310a4e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DBD2EB0D_B4DA_4069_97E4_1E4B7B90E68D
ELIN-725306-2016 | 3957949 | 12/21/2016 9:37:44 AM | ASSESS: EL: Final | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | The 200 amp 120/240 volt combination panelboard is missing a breaker filler and is accessible by persons within the residence, this is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Missing_panel_filler.png | file://x:/photopub/docs/0000000535/26243d11-5a58-40f6-899b-cd06fd82a8c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3560996e_060e_4774_a9a5_39ffb08b5534
ELIN-724466-2016 | EL-398768-2016 | 12/19/2016 12:25:00 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | A final assessment on a new industrial building found live energized conductors hanging from a wall within 450mm of where a plumber was working. Shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Open_energized_cnductors.png | file://x:/photopub/docs/0000000533/fdaee8cb-ab1e-4b7f-9180-395324438ada.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7f28887_9011_44db_823c_26b6c276ff8e
ELIN-699656-2016 | EL-443494-2016 | 12/1/2016 12:10:10 PM | ASSESS: EL: Final | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | A new 100 amp 240 volt service has been installed in a secondary dwelling /shop. The new panel is obstructed by a hot water tank and plumbing pipe which severely restricts safe access to the equipment for operators or workers . This hazard can lead to injury of persons or inability to access equipment in an emergency. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Obstructed_panel.png | file://x:/photopub/docs/0000000525/de72d7c0-fb5d-443c-ba3e-0a38dc42e5f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e033900_6256_4426_aaf8_8218f82591e7
ELIN-726228-2016 | EL-455605-2016 | 12/20/2016 9:34:53 AM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Panel_fillers__panel_fillers_missing_electrical_panel.png | file://x:/photopub/docs/0000000533/0eebf0cb-6980-4033-81b7-25b9d67c4293.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df409905_4bda_4e11_aba2_7b8bbbb49709
ELIN-722860-2016 | EL-474089-2016 | 12/15/2016 12:42:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Outdoor panel enclosure | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Temp_enclosure.png | file://x:/photopub/docs/0000000531/605536b2-5645-4081-aac1-4e7f459887a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12d48864_4381_4bb0_b64e_34e87125e777
BPOP-711027-2016 | BPV-435898-2016 | 12/19/2016 9:58:33 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA011 | Cylinder/valve expired | 3 | 3 | Expired relief valve, relief valves must be replaced every 25 years to maintain their effectiveness. | 3 | Cylinder/valve expired | Relief_valve_1379_.png | file://x:/photopub/docs/0000000534/88a1242f-a8c2-4065-8e89-542b435bcd0d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d758d959_2c48_4a40_91ec_3439033b5864
ELIN-743770-2017 | UW-483705-2016 | 1/24/2017 12:22:48 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL088 | Continuity Metal boxes, cabinets, or covers required to be bonded are not bonded to ground | 4 | 3 | #Connections_not_secured1.png,Connections_not_secured2.png Bonding conductor in not secured and cable is not protected against mechanical damage. | 4 | Continuity Metal boxes, cabinets, or covers required to be bonded are not bonded to ground | Connections_not_secured1.png | file://x:/photopub/docs/0000000547/cf1b1870-1b73-4f99-87fd-b512ec249326.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2e7e250_68d2_41e1_b89b_40205139f007
ELIN-743770-2017 | UW-483705-2016 | 1/24/2017 12:22:48 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL088 | Continuity Metal boxes, cabinets, or covers required to be bonded are not bonded to ground | 4 | 3 | #Connections_not_secured1.png,Connections_not_secured2.png Bonding conductor in not secured and cable is not protected against mechanical damage. | 4 | Continuity Metal boxes, cabinets, or covers required to be bonded are not bonded to ground | Connections_not_secured2.png | file://x:/photopub/docs/0000000547/209fecae-e1b7-4f32-b005-0bff80cbc108.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2e7e250_68d2_41e1_b89b_40205139f007
ELIN-720435-2016 | EL-477162-2016 | 12/12/2016 2:52:23 PM | ASSESS: EL: Service Connection | png | #asFound | EL014 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate. | 2 | 2 |  | 2 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate. | Protection_of_a__protection_of_a_CW_you_required_because_it_is_less_than_32_mm_from_the_face_of_a_joist.png | file://x:/photopub/docs/0000000529/d83c43e7-4e2e-4940-9eb2-70844d86b8c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3670371_0c08_401d_842f_7e1f391061af
ELIN-720435-2016 | EL-477162-2016 | 12/12/2016 2:52:23 PM | ASSESS: EL: Service Connection | png | #asFound | EL014 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate. | 2 | 2 |  | 2 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate. | Bonding_of__bonding_of_telephone_and_cable_vision_is_not_accessible_after_drywall_has_been_installed.png | file://x:/photopub/docs/0000000529/c08d0d2a-c0bb-4bc3-916c-6e73e2f843df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3670371_0c08_401d_842f_7e1f391061af
ELIN-720436-2016 | EL-477162-2016 | 12/12/2016 3:18:02 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL156 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | 3 | 3 | Device boxes require support from two sides according to rule 12â€“3010. Support is required to ensure the box is flush to the exterior surface of the finish. This will prevent the likelihood of any arcing to burn behind the wall and cause a fire. | 3 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | Support_required__support_required_for_any_box_greater_than_4_inches.png | file://x:/photopub/docs/0000000529/72078f1b-1e6c-46f7-ad37-0e9d55a4d4c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b379239f_622a_417f_8eac_de44f7507cb6
ELIN-720436-2016 | EL-477162-2016 | 12/12/2016 3:18:02 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL156 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | 3 | 3 | Device boxes require support from two sides according to rule 12â€“3010. Support is required to ensure the box is flush to the exterior surface of the finish. This will prevent the likelihood of any arcing to burn behind the wall and cause a fire. | 3 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | Support_required_.png | file://x:/photopub/docs/0000000529/bcf82428-4a6b-4c43-b4fe-84234bff6b3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b379239f_622a_417f_8eac_de44f7507cb6
ELIN-750625-2017 | EL-465149-2016 | 2/7/2017 9:19:33 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #No_Outlet_Location.png Usable wall space locations in the residential home have not been provided with receptacle locations as required by code, this could poses a risk to persons and equipment if extension cords are used because of the lack of receptacle locations. Possible overload conditions could occur to the outlets which have been provided. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | No_Outlet_Location.png | file://x:/photopub/docs/0000000555/9ae53d15-3642-4e1c-af22-713d32020f75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ed72148_adc8_40a5_b304_db4195588437
ELIN-745753-2017 | EL-492354-2017 | 2/9/2017 12:00:32 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Dual_lugging_on_two_breakers.png 4 branch circuits in a dwelling operating at 120 volts and 15 amps were found connected in a panel board with 2 conductors under each breaker. This can lead to overheating or loose conductors and result in property damage or injury to persons | 3 | Conductors Equipment is not approved for the specific use. | Dual_lugging_on_two_breakers.png | file://x:/photopub/docs/0000000557/3e575cd9-0bba-42c0-9a7d-3a51294dd893.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3155ad10_6e79_43e9_b6a0_f0c3d048a4f4
ELIN-714026-2016 | EL-330229-2015 | 12/2/2016 7:08:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | Fused disconnect not installed as per manufacture specifications. Supply conductors are terminated to load side of fuse leaving fuse energized for disconnection and maintenance. Potential for shock. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Supply_on_load_side_of_fuse.png | file://x:/photopub/docs/0000000525/347c1a0a-4fe7-4240-ad08-adceb956ecd0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9ec8239_484b_4119_badc_59984460ab79
ELIN-714026-2016 | EL-330229-2015 | 12/2/2016 7:08:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | Fused disconnect not installed as per manufacture specifications. Supply conductors are terminated to load side of fuse leaving fuse energized for disconnection and maintenance. Potential for shock. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Dry_connector_service_conduit_to_meter_hub.png | file://x:/photopub/docs/0000000525/9c51f337-7f28-4e4c-8313-9f1a45dbd1fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9ec8239_484b_4119_badc_59984460ab79
GAIN-715930-2016 | GA-464900-2016 | 12/2/2016 3:42:32 PM | ASSESS: GA: Final | png | #asFound | GA075 | Required clearances not met | 2 | 2 | Clearance to combustible material not maintained. Clearances outlined by manufacturer must be maintained to avoid fire hazard. | 2 | Required clearances not met | Clearance_to_combustibles_not_maintained.png | file://x:/photopub/docs/0000000526/6ea77f95-6976-40b6-a470-9c9482944fc9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dbc4c596_94dd_463c_87d4_a979fadd67fd
GAIN-697638-2016 | GA-438614-2016 | 12/5/2016 10:37:37 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | Venting material does not meet manufacturers installation instructions. Venting material exposed to sunlight must be UV stabilized or deterioration could occur. | 2 | Side wall vent termination not compliant with installation instructions | Exposed_venting_not_protected_from_UV.png | file://x:/photopub/docs/0000000526/8ceeb64f-4375-42c3-ab3a-98b610bd3ffe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2231a0fe_6643_4c35_8c62_3c9f89e33d15
ELIN-748353-2017 | EL-419632-2016 | 1/31/2017 12:21:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | #Conductors_in_service_box_area.png Conductors are running through service box area. This could be a potential hazard if these conductors were to be removed in the future. The service box area has service conductors that are protected by the supply authority. The supply authority over fuses their protection of these conductors which could lead to shock/fire hazard when removing conductors through the service box area. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Conductors_in_service_box_area.png | file://x:/photopub/docs/0000000551/2125f615-21ee-40e5-aefc-4538ed179631.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc79ca7c_e231_49ba_9295_7de0c5068c03
ELIN-746171-2017 | EL-419632-2016 | 1/30/2017 8:40:23 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Floor_heat.png Floor heating branch circuit is improperly installed. This could be a hazard if the heating conductor where to get damaged, this could cause a fire/shock hazard to person(s) or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Floor_heat.png | file://x:/photopub/docs/0000000551/6d948a2c-eb2a-4e87-9989-c0efaddff53c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92a1040d_7e11_4af5_81a9_b7fc9709378f
GAIN-732738-2017 | GA-431309-2016 | 1/10/2017 11:21:41 AM | ASSESS: GA: Final | png | #asFound 3/8" gas connector 48" long | GA070 | Undersized hose or appliance connector | 3 | 3 | #Gas_connector1.png,Gas_connector2.png Rooftop unit installed and operating with an undersized flexible gas connector. An undersized connector con result incomplete combustion and the production of carbon monoxide. | 3 | Undersized hose or appliance connector | Gas_connector1.png | file://x:/photopub/docs/0000000541/a47d64dd-5ada-4acb-9dd4-a02e1de96fbe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8b054a2_8f5c_42b6_a789_12551f2197a7
GAIN-732738-2017 | GA-431309-2016 | 1/10/2017 11:21:41 AM | ASSESS: GA: Final | png | #asFound 125 MBTU input | GA070 | Undersized hose or appliance connector | 3 | 3 | #Gas_connector1.png,Gas_connector2.png Rooftop unit installed and operating with an undersized flexible gas connector. An undersized connector con result incomplete combustion and the production of carbon monoxide. | 3 | Undersized hose or appliance connector | Gas_connector2.png | file://x:/photopub/docs/0000000541/1fd5c159-f66f-49e7-84fb-cece1990eb61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8b054a2_8f5c_42b6_a789_12551f2197a7
ELIN-746697-2017 | EL-453068-2016 | 2/2/2017 11:40:32 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_gfci.png The 15 amp 120 volt receptacle located in the ensuite washroom does not include GFCI protection, this is both a thermal and shock hazard for individuals using electrical equipment inserted into the outlet | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | No_gfci.png | file://x:/photopub/docs/0000000553/1e549f65-0ec0-4e95-a758-997a428d773c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9303348_b96b_4b83_8112_0f2da80561c0
ELIN-747419-2017 | EL-274429-2015 | 2/2/2017 12:56:54 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 4 | #Low_unprotected_light_fixture.png The existing incandescent light fixture located under the stairwell does not provide mechanical protection or is guarded from accidental contact from persons/ children and this is a shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Low_unprotected_light_fixture.png | file://x:/photopub/docs/0000000553/0da0a2ee-02e0-458c-b546-f7e7c09c6019.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2a99e78_3166_40bc_9ebb_5366ee31e64e
ELIN-749677-2017 | EL-449483-2016 | 2/2/2017 12:55:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL298 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #safety_switched_wired_line_on_load_side.png Safety switches must be wired so moving parts and fuse holders are de-energized when the switch is in the open position so that fuses may be changed without undue shock hazard. This switch is wired so the fuses themselves would remain energized when the switch was in the open position, creating a serious shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | safety_switched_wired_line_on_load_side.png | file://x:/photopub/docs/0000000553/463e9540-38f8-491b-861b-13a3e84a1c42.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e9bc1334_195e_4aad_9540_daa39e449242
ELIN-742725-2017 | EL-492788-2017 | 1/24/2017 2:55:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Dayton_Dr_6-208__1.png Consumer service conductors installed improperly. Length of unprotected conductors exceeds the maximum 1.5 M allowable | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Dayton_Dr_6-208__1.png | file://x:/photopub/docs/0000000547/9f331ec5-c899-4fa1-af6c-1344c5a20176.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec38c57f_a874_44c8_8423_12c36b8d8e86
GAUP-744166-2017 | UW-493947-2017 | 1/24/2017 4:30:11 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Grhugwvd1.png,Grhugwvd2.png Multiple combustion and exhaust terminations from boilers were installed 8-10" above roof. Snow could block the terminations causing appliances to lockout | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Grhugwvd1.png | file://x:/photopub/docs/0000000547/aa5e14a3-ad4b-4571-84b5-042351266c53.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71a26ffa_0c33_40d3_8c4b_bd477d805784
GAUP-744166-2017 | UW-493947-2017 | 1/24/2017 4:30:11 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Grhugwvd1.png,Grhugwvd2.png Multiple combustion and exhaust terminations from boilers were installed 8-10" above roof. Snow could block the terminations causing appliances to lockout | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Grhugwvd2.png | file://x:/photopub/docs/0000000547/0dc876d3-ca5d-4327-b01a-8b21a4d1ff29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71a26ffa_0c33_40d3_8c4b_bd477d805784
BPOP-670538-2016 | BPV-404715-2015 | 12/12/2016 5:29:06 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Vegetation must be removed for proper inspection and in case of Fire | 3 | Clearance to combustible not met | Pic2.png | file://x:/photopub/docs/0000000530/745f5db6-236b-4bab-b27a-572995a0aeb1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__619905b4_09ff_494c_b7c8_e4605558bd3d
BPOP-711010-2016 | BPV-434058-2016 | 12/12/2016 5:19:16 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | Tank is buried under snow without markers , tank could be hit by snowplow or other causing damage to tank. | 3 | Code prohibited practices or materials | Snowtank.png | file://x:/photopub/docs/0000000530/319b7adc-6b5f-42b9-bee3-edec6b18224a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5eaf2d33_954e_44c5_8393_6e9fe51c1feb
BPOP-670538-2016 | BPV-404715-2015 | 12/12/2016 5:29:06 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Vegetation must be removed for proper inspection and in case of Fire | 3 | Clearance to combustible not met | Pic1.png | file://x:/photopub/docs/0000000530/c2135ff2-ff61-476e-acb2-05cb99e491b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__619905b4_09ff_494c_b7c8_e4605558bd3d
BPVOP-208995-2014 | 2288564 | 12/14/2016 10:34:17 AM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Low Pressure Steam Heating Boiler with Heating surface area of 32 square meters, Maximum Allowable Working Pressure (MAWP) of 15psig, it was determined that safety valve has exceeded the required yearly interval for testing and 5 years interval of servicing/replacement.Failure to have safety valve tested and serviced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water/steam and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve.png | file://x:/photopub/docs/0000000531/a18b5447-e5aa-46ef-aa9e-89457b5f0d93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06A540C8_FEE8_4598_AE51_CBA77808F97E
ELIN-727241-2016 | EL-463247-2016 | 12/21/2016 7:59:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | The ampacity of a service conductor should be equal to or greater than the calculated load of the service. This protects the conductor from overheating and the conductor insulation from breaking down. At rural property where a service upgrade was taking place, a cable with a 250 amp rating was installed for a 400 amp service. If the cable was energized and the load on the cable was greater than 250 amps, the insulation around the conductors could breakdown which would result in equipment damage and a potential fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 400A_Fused_Switch.png | file://x:/photopub/docs/0000000534/4bac3b02-90b0-4dab-af4b-ac6134fcf806.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2c668b2_4136_47ba_b565_99410e61898d
ELIN-727241-2016 | EL-463247-2016 | 12/21/2016 7:59:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | The ampacity of a service conductor should be equal to or greater than the calculated load of the service. This protects the conductor from overheating and the conductor insulation from breaking down. At rural property where a service upgrade was taking place, a cable with a 250 amp rating was installed for a 400 amp service. If the cable was energized and the load on the cable was greater than 250 amps, the insulation around the conductors could breakdown which would result in equipment damage and a potential fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Pole.png | file://x:/photopub/docs/0000000534/87bcf9dd-a90f-4eb6-b830-54c73bf2211d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2c668b2_4136_47ba_b565_99410e61898d
ELIN-637988-2016 | EL-327133-2015 | 12/14/2016 9:40:39 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | The 15 amp 120 volt flexible cord is directly terminated into main panel and concealed in wall (temporary) and coiled on floor below panel. Materials are stored in area and if stored on cord can create a thermal hazard. Hazard is located in remote Temporary service shed from residence. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord.png | file://x:/photopub/docs/0000000531/1b0eb7a6-df46-4554-a32a-0574c5e9149c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd2bf0ad_9159_474b_b992_e2c68338ae96
ELOP-753470-2017 | EL-498983-2017 | 2/8/2017 9:45:55 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL276 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | 2 | 2 | #Emergency.png No evidence of periodic maintenance and testing of emergency lighting unit. Lack of emergency lighting in an outage situation may impede safe egress from the building. | 2 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | Emergency.png | file://x:/photopub/docs/0000000555/dc515f54-d393-4f3c-8156-c9f47b998aa0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C8C450B4_57C6_4D28_8724_F2183FDC60C4
GAIN-733314-2017 | GA-431510-2016 | 1/13/2017 11:43:07 AM | ASSESS: GA: Final | png | #asFound | GA124 | Blocked combustion air supply | 4 | 4 | #Combustion_airvent.png The as found condition is a vent supplying combustion air to a boiler mechanical room is equipped with a locking cover that was closed at the time of inspection. The as found hazard is the cover prevents ambient outside air from reaching the appliance, resulting in the combustion process potentially depressurizing the area and drawing harmful products of combustion into the building envelope. | 4 | Blocked combustion air supply | Combustion_airvent.png | file://x:/photopub/docs/0000000543/1c18e5c7-7339-4594-b1ce-90436c44fb86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__501dc941_65fe_4a87_a5d9_3ec9b893cdf2
ELIN-719986-2016 | EL-406657-2016 | 12/28/2016 4:11:23 PM | ASSESS: EL: Final | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Isolated receptacles defeat the purpose of creating an equipotential ground plane within the patient care areas. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Isolated_gorunding_type_receptacles.png | file://x:/photopub/docs/0000000536/57e7ec7b-23ee-4f63-a80d-d44ba043287c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a37ac001_fccf_430b_ae4d_1c8c6cba6321
ELIN-719986-2016 | EL-406657-2016 | 12/28/2016 4:11:23 PM | ASSESS: EL: Final | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Isolated receptacles defeat the purpose of creating an equipotential ground plane within the patient care areas. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Incompleted_circuits.png | file://x:/photopub/docs/0000000536/dfba382c-3644-43cb-9885-fcb15149c1f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a37ac001_fccf_430b_ae4d_1c8c6cba6321
ELIN-719986-2016 | EL-406657-2016 | 12/28/2016 4:11:23 PM | ASSESS: EL: Final | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Isolated receptacles defeat the purpose of creating an equipotential ground plane within the patient care areas. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Isolated_grounding_type_receptacles_2.png | file://x:/photopub/docs/0000000536/2774e4bb-cfe1-4a4d-9d15-ca1877050dd2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a37ac001_fccf_430b_ae4d_1c8c6cba6321
GAHE-753991-2017 | HE-499429-2017 | 2/8/2017 2:25:11 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #Burner.png The homeowner manufactured a custom decorative burner from parts purchased at a local home hardware store. The appliance consisted of a ball valve that was connected to a piece of 3/4" black iron with holes drilled in it that was used as a burner. It contained no pilots, safeties or controls. It was lite with a BBQ lighter as the gas valve was turned on. Potential hazards are uncontrolled gas leak if ball valve was accidentally turned on, and potential injury as the burners were on the edge of a slippery pool deck with a walkway immediately adjacent. | 3 | Uncertified appliance connected to gas supply but not in service | Burner.png | file://x:/photopub/docs/0000000555/4210c028-66db-481f-bb97-2576301130d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc0484fc_25f4_4a9b_8249_a9807b63632d
ELIN-752603-2017 | EL-495992-2017 | 2/8/2017 3:15:36 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #armoured_cable_not_terminated_in_device_box.png Armoured cable used for lighting is not terminated in approved device box or termination junction for light fixture. Exposed conductors in this situation would pose a risk of fire or shock to property or persons | 3 | Installation of electrical equipment Equipment is not approved for the specific use | armoured_cable_not_terminated_in_device_box.png | file://x:/photopub/docs/0000000555/27f904de-8a8c-49ca-b241-0edd95421f06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3d3c00b_fdcf_4d10_844c_83fcf8c8bb17
ELIN-750730-2017 | EL-492732-2017 | 2/2/2017 1:56:39 PM | ASSESS: EL: Service Connection | png | #asFound Split stranded conductor | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #Parking_lot_service1.png,Parking_lot_service2.png The system neutral conductor is a stranded cable, it has been split into two and terminated under separate barrels in the provided lug. The service also requires mechanical protection from vehicular traffic | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Parking_lot_service2.png | file://x:/photopub/docs/0000000552/f91957c1-0a8b-480d-817c-9b3a23523226.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ca4a514_868f_43a0_b570_2b499f84500b
ELIN-750730-2017 | EL-492732-2017 | 2/2/2017 1:56:39 PM | ASSESS: EL: Service Connection | png | #asFound Lack of vehicular protection | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #Parking_lot_service1.png,Parking_lot_service2.png The system neutral conductor is a stranded cable, it has been split into two and terminated under separate barrels in the provided lug. The service also requires mechanical protection from vehicular traffic | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Parking_lot_service1.png | file://x:/photopub/docs/0000000552/80529ed5-cfd1-4cb4-98b1-f92e39955667.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ca4a514_868f_43a0_b570_2b499f84500b
ELHE-751178-2017 | HE-498055-2017 | 2/3/2017 11:38:33 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Bundled cable is used for stage lighting. | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Bundling.png Hazard Elimination of unsafe wiring in building used for plays and performances. Flexible cord has been bundled and used in the facility as permanent wiring. This has been used for stage lighting. Bundling of these multi conductor cable's has caused some to be brittle because they cannot dissipate the heat. They are undersized and can be a fire hazard. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Bundling.png | file://x:/photopub/docs/0000000553/5ab4e3fa-cc4f-4cb5-90db-184302c893ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ea3b766_7f0c_4ad2_80cc_7cc6319c1595
ELIN-732131-2017 | EL-440221-2016 | 1/4/2017 12:28:21 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | The 15 amp 120 volt wire, that is to connect to the hoodfan, is energized and hanging out of the wall and not protected from accidental contact from persons, this poses a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Hoodfan.png | file://x:/photopub/docs/0000000538/18506b34-e8cf-4d75-8824-b4f44d1dfab5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29d2e99c_0bed_4270_9b22_5c5d0b019592
ELIN-746282-2017 | EL-482390-2016 | 2/2/2017 3:36:17 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound Road base used for underground cable. No inspection requested for underground installation, covered and cable energized at time of inspection. | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #Service_cable.png Private pole and meter installed by unknown individual, no certification and gain mark visible on pole, road base material used around cable, no inspection requested before cover of underground installation, service energized at time of inspection. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Service_cable.png | file://x:/photopub/docs/0000000552/317abd6f-b5f3-4e07-9d7d-0e1d447ec64d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58d58179_15f3_41a5_afb4_0ee1b70459bc
ELIN-747014-2017 | EL-462459-2016 | 1/30/2017 5:36:49 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_400A_Pnl1.png,Energized_400A_Pnl2.png,Energized_400A_Pnl3.png,Energized_400A_Pnl4.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. During an assessment of a commercial building undergoing a renovation, an energized 400 amp 120/240 volt electrical panel was found with the no panel cover installed. Armoured cable for temporary power was entered through the face of the panel and was connected to breakers inside the panel. There is a potential shock hazard for any persons that make accidental contact with with the energized bus bars or exposed energized conductors inside the panel. There is also a potential for an arc fault hazard if the metal armour of the cable was to come in contact with the energized bus bars or conductors inside the panel. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_400A_Pnl2.png | file://x:/photopub/docs/0000000550/8fa397d8-cd90-4d3a-8854-5cbe958ca608.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2baa30f0_1b4c_4cf6_a896_e8faf21f8272
ELIN-747014-2017 | EL-462459-2016 | 1/30/2017 5:36:49 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_400A_Pnl1.png,Energized_400A_Pnl2.png,Energized_400A_Pnl3.png,Energized_400A_Pnl4.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. During an assessment of a commercial building undergoing a renovation, an energized 400 amp 120/240 volt electrical panel was found with the no panel cover installed. Armoured cable for temporary power was entered through the face of the panel and was connected to breakers inside the panel. There is a potential shock hazard for any persons that make accidental contact with with the energized bus bars or exposed energized conductors inside the panel. There is also a potential for an arc fault hazard if the metal armour of the cable was to come in contact with the energized bus bars or conductors inside the panel. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_400A_Pnl1.png | file://x:/photopub/docs/0000000550/c9289fad-3a8f-433f-9635-2ca5fa45f899.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2baa30f0_1b4c_4cf6_a896_e8faf21f8272
ELIN-747014-2017 | EL-462459-2016 | 1/30/2017 5:36:49 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_400A_Pnl1.png,Energized_400A_Pnl2.png,Energized_400A_Pnl3.png,Energized_400A_Pnl4.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. During an assessment of a commercial building undergoing a renovation, an energized 400 amp 120/240 volt electrical panel was found with the no panel cover installed. Armoured cable for temporary power was entered through the face of the panel and was connected to breakers inside the panel. There is a potential shock hazard for any persons that make accidental contact with with the energized bus bars or exposed energized conductors inside the panel. There is also a potential for an arc fault hazard if the metal armour of the cable was to come in contact with the energized bus bars or conductors inside the panel. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_400A_Pnl3.png | file://x:/photopub/docs/0000000550/6309aec6-9138-4309-afd4-0d5ef1e2730c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2baa30f0_1b4c_4cf6_a896_e8faf21f8272
ELIN-747014-2017 | EL-462459-2016 | 1/30/2017 5:36:49 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_400A_Pnl1.png,Energized_400A_Pnl2.png,Energized_400A_Pnl3.png,Energized_400A_Pnl4.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. During an assessment of a commercial building undergoing a renovation, an energized 400 amp 120/240 volt electrical panel was found with the no panel cover installed. Armoured cable for temporary power was entered through the face of the panel and was connected to breakers inside the panel. There is a potential shock hazard for any persons that make accidental contact with with the energized bus bars or exposed energized conductors inside the panel. There is also a potential for an arc fault hazard if the metal armour of the cable was to come in contact with the energized bus bars or conductors inside the panel. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_400A_Pnl4.png | file://x:/photopub/docs/0000000550/3c2b8764-3571-4892-bef5-c525ceb71727.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2baa30f0_1b4c_4cf6_a896_e8faf21f8272
BPVOP-719579-2016 | 2258661 | 12/7/2016 4:48:06 PM | ASSESS: BPV OP: Incident REF/PV | png | #asFound | BP118 | 3.0.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Ammonia Pressure Relief Device discharge location does not meet CSA B-52 code requirements and is likely to cause risk to personnel if overpressure and discharge occurs. | 4 | 4 | Found the openings of 2 Safety Relief Valves installed on the Ammonia Accumulator Pressure Vessel to be at a height of 8 feet, which is below the minimum of 15 feet above accessible roof level as required by code. If the Safety Relief Valves were to discharge, there is a potential for personnel to be harmed. | 4 | 3.0.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Ammonia Pressure Relief Device discharge location does not meet CSA B-52 code requirements and is likely to cause risk to personnel if overpressure and discharge occurs. | Rooftop_accumulator_reliefs.png | file://x:/photopub/docs/0000000538/bb84036a-2265-465f-be19-bf02724d724d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0fcff740_afd8_41e6_b908_b9e3ccefd292
BPVOP-719579-2016 | 2258661 | 12/7/2016 4:48:06 PM | ASSESS: BPV OP: Incident REF/PV | png | #asFound | BP118 | 3.0.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Ammonia Pressure Relief Device discharge location does not meet CSA B-52 code requirements and is likely to cause risk to personnel if overpressure and discharge occurs. | 4 | 4 | Found the openings of 2 Safety Relief Valves installed on the Ammonia Accumulator Pressure Vessel to be at a height of 8 feet, which is below the minimum of 15 feet above accessible roof level as required by code. If the Safety Relief Valves were to discharge, there is a potential for personnel to be harmed. | 4 | 3.0.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Ammonia Pressure Relief Device discharge location does not meet CSA B-52 code requirements and is likely to cause risk to personnel if overpressure and discharge occurs. | Rooftop.png | file://x:/photopub/docs/0000000538/7f6ab95f-6e3b-4978-811b-5effa9063378.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0fcff740_afd8_41e6_b908_b9e3ccefd292
GAIN-710887-2016 | GA-471804-2016 | 1/16/2017 12:03:55 PM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Alkali1.png Piping and fittings installed on propane tank manifold is tank pressure and fittings and pipe is schedule 40 Threaded schedule 40 fittings not rated for the excess pressure and could leak | 3 | Non-compliant material/fittings installed | Alkali1.png | file://x:/photopub/docs/0000000543/9832a9e3-b6a4-443e-98ca-d9fd803dd5c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f8553f4_30e4_47c6_b999_5af4ad59a262
GAUP-739524-2017 | UW-491160-2017 | 1/16/2017 1:26:55 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Combustible_floor2.png The as found condition is a steam boiler installed on a combustible floor against the manufacturer requirement to have the appliance installed on a non-combustible floor. The as found hazard is the boiler installation could lead to a possible fire resulting from excessive heat being transferred to the floor. | 3 | Clearance to combustible not met | Combustible_floor2.png | file://x:/photopub/docs/0000000543/345e81fa-aa9b-44ad-ba82-450f6533cceb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5fc08fe8_d1b0_44da_9177_a46f43422071
BPVOP-722060-2016 | 2271551 | 12/12/2016 3:19:21 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 3 | Upon assessment of domestic hot water storage tank (length-2.2m, diameter-0.90) it is determined that vessel's pressure relief device set pressure is higher than Maximum Allowable Working Pressure (MAWP) of vessel. In the event of fire or failure of control, vessel will be subjected to pressure above MAWP resulting in failure of pressure boundary with likelihood of severe incident. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | T_and_P_relief_valve.png | file://x:/photopub/docs/0000000532/2482fbc2-69b6-46e1-ac2d-4fed40788cdc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__60b9bc92_66ab_4313_8b37_918de4bdb81f
ELOP-721098-2016 | 1973 | 12/8/2016 11:20:35 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | The outlet near the sink is not GFCI protected. In the event there is contact between an appliance plugged into this outlet, the user and water, a shock hazard could result. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Non_gfci_protected_outlet_near_sink.png | file://x:/photopub/docs/0000000531/b5993550-e041-49b2-9e4b-ab27e0476354.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__573875bf_27a8_48ac_ab6a_4dc539cb85ce
ELOP-697588-2016 | EL-428792-2016 | 12/8/2016 11:42:35 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | A privately owned 14400 volt gang operated switch has been found to be inadequately grounded to protect operators of the switch. This can lead to injury or fatality of operators of the switch | 3 | Continuity Bonding; method for equipment is not adequate. | No_redundant_ground_to_mat_high_voltage_system.png | file://x:/photopub/docs/0000000528/d1062ee1-ce2f-4f20-ac14-819cafed04f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C490F23D_A3B1_4E07_8BCB_9AA26CC75F16
BPVOP-719556-2016 | 2258656 | 12/7/2016 12:21:00 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP118 | 3.0.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Ammonia Pressure Relief Device discharge location does not meet CSA B-52 code requirements and is likely to cause risk to personnel if overpressure and discharge occurs. | 4 | 4 | Found the openings of 2 Safety Relief Valves installed on the Ammonia Accumulator Pressure Vessel to be at a height of 8 feet, which is below the minimum of 15 feet above accessible roof level required by code. If the Safety Relief Valves were to discharge, there is a potential for personnel to be harmed. | 4 | 3.0.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Ammonia Pressure Relief Device discharge location does not meet CSA B-52 code requirements and is likely to cause risk to personnel if overpressure and discharge occurs. | Rooftop_Accumulator_relief_discharge.png | file://x:/photopub/docs/0000000537/1bc559ae-dd93-4892-b5c1-c88089ff24d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__100d48a9_e4ba_437f_9847_554063ae4f53
BPVOP-723854-2016 | 5147182 | 12/7/2016 12:17:50 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | Relief discharge below the minimum requirement. | 0 | No Created Hazard Identified | Relief_discharge.png | file://x:/photopub/docs/0000000537/2bfe33de-ef7f-48f8-bd38-4098a6e061bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ee7c7f8_70ff_4cf4_bdf1_bfd1bb99e2b4
GAIN-735103-2017 | GA-487864-2017 | 1/10/2017 3:08:29 PM | ASSESS: GA: Final | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | #9214_McBride1.png,9214_McBride2.png Occupied home is under renovations and a shut off valve has been cut into the existing gas piping system for a future gas range but has not been capped closed. If for any reason the shut off valve was to get knocked open an uncontrolled gas leak would occur and could fill up the basement with natural gas and when either the furnace or water heater were too cycle on this would ignite the natural gas causing an explosion and fire causing property damage and possible death or injuries too occupants of this home | 5 | Open gas line connected to fuel supply (no cap/plug) | 9214_McBride2.png | file://x:/photopub/docs/0000000541/173ce2a8-800f-45a1-948c-72c4c233ac4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__757d0e9f_e88f_4e4a_9fb3_a96ef592255c
GAIN-735103-2017 | GA-487864-2017 | 1/10/2017 3:08:29 PM | ASSESS: GA: Final | png | #asFound Gas line in basement furnace room | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | #9214_McBride1.png,9214_McBride2.png Occupied home is under renovations and a shut off valve has been cut into the existing gas piping system for a future gas range but has not been capped closed. If for any reason the shut off valve was to get knocked open an uncontrolled gas leak would occur and could fill up the basement with natural gas and when either the furnace or water heater were too cycle on this would ignite the natural gas causing an explosion and fire causing property damage and possible death or injuries too occupants of this home | 5 | Open gas line connected to fuel supply (no cap/plug) | 9214_McBride1.png | file://x:/photopub/docs/0000000541/3042862a-5e33-4b10-a36a-e33ebf08630c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__757d0e9f_e88f_4e4a_9fb3_a96ef592255c
ELIN-734111-2017 | UW-487419-2017 | 1/6/2017 10:16:56 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | B.png | file://x:/photopub/docs/0000000540/b11f7699-8478-494f-9ed0-9df57c79824b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9312507_a792_421f_8733_997673130eb4
ELIN-734111-2017 | UW-487419-2017 | 1/6/2017 10:16:56 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | A.png | file://x:/photopub/docs/0000000540/0b2e9598-c979-4013-ab1d-274b22e65a5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9312507_a792_421f_8733_997673130eb4
ELIN-717155-2016 | EL-473988-2016 | 12/15/2016 11:31:18 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | A new home under construction with a 200 amp 240 volt service panel was found accessible to the general public or unauthorized operation. This can lead to tampering or other interference that can endanger persons or property | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_open_to_unauthorized_access.png | file://x:/photopub/docs/0000000532/ae67d1a1-a0d1-483b-ae0f-99a5fecf7ebf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2711f8a3_7061_460b_954d_14ba6999c80c
BPVOP-725737-2016 | 4972358 | 12/16/2016 10:31:35 PM | ASSESS: BPV OP: Re-Inspection REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 4 | Safety devices protect equipment from dangerous conditions and damage. Devices must be installed according to all applicable standards. I found a safety device (pressure relief valve on a hot water storage tank) not installed. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | Relief_valve_not_installed.png | file://x:/photopub/docs/0000000532/87c4e3d7-1a85-4b54-b733-1363675b13e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81b64c3d_345d_4ba6_8eab_c341dbbe8019
BPVOP-725735-2016 | 4972357 | 12/16/2016 10:00:50 PM | ASSESS: BPV OP: RAP (for recert insp) REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 4 | Safety devices protect equipment from dangerous conditions and damage. Devices must be installed according to all applicable standards. I found a safety device (pressure relief valve on a hot water storage tank) not installed. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | Relief_valve_missing.png | file://x:/photopub/docs/0000000532/85ce6b63-5e37-4561-9111-28787938da21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14e74989_4a6c_4ef0_b3ff_1cc01b1c93a4
ELIN-759974-2017 | EL-490336-2017 | 2/20/2017 1:42:06 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Image_7-81.png,Image_7-82.png Energized service conductors in conduit not approved for surface use. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Image_7-82.png | file://x:/photopub/docs/0000000559/c55a5720-95ab-4649-b8ee-69b2bbb972cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e282b67e_1b29_40f4_87ec_e0bae84979a6
GAIN-741490-2017 | GA-485791-2016 | 1/19/2017 10:44:45 AM | ASSESS: GA: Rough-In | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | #Keating_X_rd1.png Certified appliance connector hose not approved for application. Connector hose could be damaged by movement of the appliance causing a leak. | 2 | Certified appliance connector installed but not approved for application | Keating_X_rd1.png | file://x:/photopub/docs/0000000545/fa0da44f-4f7a-48e3-a593-cc721a153c17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__697e658b_9ee3_4adb_83fe_98f62e90f5d8
BPVOP-721897-2016 | 2295187 | 12/12/2016 12:18:15 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP077 | 1.2.3 Boiler construction - Indications of overheating caused by scale or deposits on heat exchange surfaces. | 3 | 3 | During the inspection of a DHW Boiler with MAWP of 160 psig, signs of overheating were observed on the casing. | 3 | 1.2.3 Boiler construction - Indications of overheating caused by scale or deposits on heat exchange surfaces. | Overheating_.png | file://x:/photopub/docs/0000000530/4bc0a17a-d1f8-439e-b396-a5b14b12c24b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bef9d59_dad4_4947_b77c_ed1a02cec921
BPVIN-722399-2016 | UW-479965-2016 | 12/12/2016 3:51:35 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | horizontal_Safety_Relief_Valve.png | file://x:/photopub/docs/0000000530/11ee381b-65b1-442b-aff9-be4d67c02330.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ec4a103_92b9_49c6_8c8c_5b932cf7fe89
ELIN-738948-2017 | EL-490420-2017 | 1/16/2017 9:35:53 AM | ASSESS: EL: Final | png | #asFound White conductor requires re-identification to red black or blue at all locations | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 | #Photos_of__Photos_of_missing_knockout_filler_and_re-identification_of_the_white_conductor_required1.png,Photos_of__Photos_of_missing_knockout_filler_and_re-identification_of_the_white_conductor_required2.png,Photos_of__Photos_of_missing_knockout_filler_and_re-identification_of_the_white_conductor_required3.png | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Photos_of__Photos_of_missing_knockout_filler_and_re-identification_of_the_white_conductor_required1.png | file://x:/photopub/docs/0000000543/22ead580-303b-40ba-b3d7-2e6b41c60424.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9229a1ce_b694_48c6_a0c6_f9eb252c13fe
ELIN-738948-2017 | EL-490420-2017 | 1/16/2017 9:35:53 AM | ASSESS: EL: Final | png | #asFound Knockout fillers need to be installed in panelboards | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 | #Photos_of__Photos_of_missing_knockout_filler_and_re-identification_of_the_white_conductor_required1.png,Photos_of__Photos_of_missing_knockout_filler_and_re-identification_of_the_white_conductor_required2.png,Photos_of__Photos_of_missing_knockout_filler_and_re-identification_of_the_white_conductor_required3.png | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Photos_of__Photos_of_missing_knockout_filler_and_re-identification_of_the_white_conductor_required3.png | file://x:/photopub/docs/0000000543/91dbe569-535f-41bd-b182-311b76e3ce51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9229a1ce_b694_48c6_a0c6_f9eb252c13fe
ELIN-738948-2017 | EL-490420-2017 | 1/16/2017 9:35:53 AM | ASSESS: EL: Final | png | #asFound Knockouts trailer needs to be installed | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 | #Photos_of__Photos_of_missing_knockout_filler_and_re-identification_of_the_white_conductor_required1.png,Photos_of__Photos_of_missing_knockout_filler_and_re-identification_of_the_white_conductor_required2.png,Photos_of__Photos_of_missing_knockout_filler_and_re-identification_of_the_white_conductor_required3.png | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Photos_of__Photos_of_missing_knockout_filler_and_re-identification_of_the_white_conductor_required2.png | file://x:/photopub/docs/0000000543/378b7bc9-016a-413d-891a-bde56ba17303.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9229a1ce_b694_48c6_a0c6_f9eb252c13fe
ELOP-651497-2016 | 1284 | 1/23/2017 9:53:35 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #No_cover.png In an existing commercial space, a 15amp 120volt outlet was found in an energized state with no cover installed. This can lead to a shock hazard. Pic attached. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | no_cover.png | file://x:/photopub/docs/0000000549/f4c648e9-e851-407c-b7da-c8a839deabab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__B2958047_2ED4_4B17_978E_7D3432C81B0D
ELOP-651497-2016 | 1284 | 1/23/2017 9:53:35 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #No_cover.png In an existing commercial space, a 15amp 120volt outlet was found in an energized state with no cover installed. This can lead to a shock hazard. Pic attached. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | No_Cover.png | file://x:/photopub/docs/0000000549/7926388a-a7a0-4e19-8e49-2077a340b088.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__B2958047_2ED4_4B17_978E_7D3432C81B0D
EDRI-748291-2017 | ED-426307-2016 | 1/25/2017 3:16:00 PM | ASSESS: ED RI: Initial | png | #asFound At the bottom level of the hoist, a carriage gate that is not used on the bottom level (but will be used on higher levels) can be opened. When opened there is a missing wall that would normally prevent passengers from being able to exit the hoist where they are not supposed to. This provides a 5'-6' fall hazard into the restricted 'pit' area of the hoist. | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 3 | #Bottom_landing_unused_gate_with_missing_fascia.png At the bottom level of the hoist, a carriage gate that is not used on the bottom level (but will be used on higher levels) can be opened. When opened there is a missing wall that would normally prevent passengers from being able to exit the hoist where they are not supposed to. This provides a 5'-6' fall hazard into the restricted 'pit' area of the hoist. | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Bottom_landing_unused_gate_with_missing_fascia.png | file://x:/photopub/docs/0000000550/5453dfe4-673b-4b32-ab8a-170e04f4c66e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a64c6f6_284a_4583_9e54_d609ec16a02c
ELIN-749304-2017 | EL-465253-2016 | 2/1/2017 12:06:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Main_distribution_installed_near_the_window_opening_Window_not_installed.png 100 amp, 120/240 volt main distribution panel rated for indoor use only is subject to outdoor elements. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_distribution_installed_near_the_window_opening_Window_not_installed.png | file://x:/photopub/docs/0000000552/b2e72ddb-e814-4af8-8802-b472e41faf4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb995b26_a464_49c6_a320_87397208705a
ELIN-718600-2016 | EL-468830-2016 | 12/7/2016 7:21:20 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found 60 amp 120/240 volt 1 phase panelboards with exposed energized conductors and bus bars in two separate residential occupancies units. When electrical equipment such as panelboards have covers missing leaving bus bars and conductors exposed and energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Switching is not done in an ungrounded conductor | g.png | file://x:/photopub/docs/0000000527/2c89c113-8938-469b-96f1-268d0c353904.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3008b5c0_91d8_4317_a6a6_d443cd4e3bfa
ELIN-718600-2016 | EL-468830-2016 | 12/7/2016 7:21:20 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found 60 amp 120/240 volt 1 phase panelboards with exposed energized conductors and bus bars in two separate residential occupancies units. When electrical equipment such as panelboards have covers missing leaving bus bars and conductors exposed and energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Switching is not done in an ungrounded conductor | c.png | file://x:/photopub/docs/0000000527/d7edfd1e-d7a5-4fe9-b9ca-d1c2d6df17e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3008b5c0_91d8_4317_a6a6_d443cd4e3bfa
ELIN-718600-2016 | EL-468830-2016 | 12/7/2016 7:21:20 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found 60 amp 120/240 volt 1 phase panelboards with exposed energized conductors and bus bars in two separate residential occupancies units. When electrical equipment such as panelboards have covers missing leaving bus bars and conductors exposed and energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Switching is not done in an ungrounded conductor | e.png | file://x:/photopub/docs/0000000527/2ead8da9-8f17-4b18-9ab0-09de76e6cf45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3008b5c0_91d8_4317_a6a6_d443cd4e3bfa
ELIN-751984-2017 | EL-497473-2017 | 2/16/2017 9:35:51 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Cables_not_supported_to_ensure_they_cannot_be_struck_by_nails_screws.png Cables installed too close to drywall surfaces are subject to damage if struck by drywall nails or screws. This presents a potential fire hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cables_not_supported_to_ensure_they_cannot_be_struck_by_nails_screws.png | file://x:/photopub/docs/0000000558/65d6318a-1816-4b32-89b9-627ce673a350.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b30fd4d_5f00_45ad_8f95_e809c174eff3
BPVOP-726528-2016 | 3983907 | 6/8/2016 3:32:49 PM | ASSESS: BPV OP: Re-Inspection Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Relief_valve_installation2.png | file://x:/photopub/docs/0000000533/6edab8c3-9663-4357-b0a3-19453872bd6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6864a41e_f636_49c2_bee2_6a209773d2c9
ELIN-741117-2017 | EL-420604-2016 | 1/19/2017 8:24:20 AM | ASSESS: EL: Final | png | #asFound | EL128 | Installation of electrical equipment Residential: branch circuit for kitchen counter receptacles is not split 15 A, or 20 A. | 3 | 3 | #15_amp_GFCI.png Receptacles rated at 15 amps were protected by a breaker rated at 20 amps. This condition could cause overheating of the receptacle and a potential fire hazard. | 3 | Installation of electrical equipment Residential: branch circuit for kitchen counter receptacles is not split 15 A, or 20 A. | 15_amp_GFCI.png | file://x:/photopub/docs/0000000545/6eb1e591-f9f6-4bf2-8007-99f082394d07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28a618fd_0505_444c_9bac_01bc8ab3bed6
ELHE-752638-2017 | HE-498789-2017 | 2/6/2017 2:49:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Conductors_and_cables_not_supported_properly_while_energized1.png,Conductors_and_cables_not_supported_properly_while_energized2.png,Conductors_and_cables_not_supported_properly_while_energized3.png,Conductors_and_cables_not_supported_properly_while_energized4.png,Conductors_and_cables_not_supported_properly_while_energized5.png,Conductors_and_cables_not_supported_properly_while_energized6.png Found branch circuit insulated conductors and cables to be not supported properly and is energized and not safe or authorized for connection to power supply system. When electrical equipment is not supported properly while being energized the electrical equipment conductors are subject to possible mechanical damage and could pose an electrical fire or shock hazard to people and property. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Conductors_and_cables_not_supported_properly_while_energized5.png | file://x:/photopub/docs/0000000554/5198510e-39c0-49e8-855c-38b577be7974.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93a36f4d_f6a0_49fa_a3d9_acfa68a37fa0
ELHE-752638-2017 | HE-498789-2017 | 2/6/2017 2:49:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Conductors_and_cables_not_supported_properly_while_energized1.png,Conductors_and_cables_not_supported_properly_while_energized2.png,Conductors_and_cables_not_supported_properly_while_energized3.png,Conductors_and_cables_not_supported_properly_while_energized4.png,Conductors_and_cables_not_supported_properly_while_energized5.png,Conductors_and_cables_not_supported_properly_while_energized6.png Found branch circuit insulated conductors and cables to be not supported properly and is energized and not safe or authorized for connection to power supply system. When electrical equipment is not supported properly while being energized the electrical equipment conductors are subject to possible mechanical damage and could pose an electrical fire or shock hazard to people and property. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Conductors_and_cables_not_supported_properly_while_energized3.png | file://x:/photopub/docs/0000000554/b7a41c4c-bae6-4336-a04f-0670ac715521.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93a36f4d_f6a0_49fa_a3d9_acfa68a37fa0
ELHE-752638-2017 | HE-498789-2017 | 2/6/2017 2:49:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Conductors_and_cables_not_supported_properly_while_energized1.png,Conductors_and_cables_not_supported_properly_while_energized2.png,Conductors_and_cables_not_supported_properly_while_energized3.png,Conductors_and_cables_not_supported_properly_while_energized4.png,Conductors_and_cables_not_supported_properly_while_energized5.png,Conductors_and_cables_not_supported_properly_while_energized6.png Found branch circuit insulated conductors and cables to be not supported properly and is energized and not safe or authorized for connection to power supply system. When electrical equipment is not supported properly while being energized the electrical equipment conductors are subject to possible mechanical damage and could pose an electrical fire or shock hazard to people and property. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Conductors_and_cables_not_supported_properly_while_energized1.png | file://x:/photopub/docs/0000000554/bc31a46e-0931-4767-ba96-03cb2ba5706a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93a36f4d_f6a0_49fa_a3d9_acfa68a37fa0
ELHE-752638-2017 | HE-498789-2017 | 2/6/2017 2:49:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Conductors_and_cables_not_supported_properly_while_energized1.png,Conductors_and_cables_not_supported_properly_while_energized2.png,Conductors_and_cables_not_supported_properly_while_energized3.png,Conductors_and_cables_not_supported_properly_while_energized4.png,Conductors_and_cables_not_supported_properly_while_energized5.png,Conductors_and_cables_not_supported_properly_while_energized6.png Found branch circuit insulated conductors and cables to be not supported properly and is energized and not safe or authorized for connection to power supply system. When electrical equipment is not supported properly while being energized the electrical equipment conductors are subject to possible mechanical damage and could pose an electrical fire or shock hazard to people and property. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Conductors_and_cables_not_supported_properly_while_energized4.png | file://x:/photopub/docs/0000000554/9c597f47-3568-4282-a198-72143c3eba88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93a36f4d_f6a0_49fa_a3d9_acfa68a37fa0
GAUP-737459-2017 | UW-489273-2017 | 1/12/2017 9:40:41 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Incorrect_venting_material.png Incorrect venting material for type of appliance. Incorrect venting material and method of venting can cause fire hazard and spillage of venting products into occupied space. | 3 | Unapproved venting material | Incorrect_venting_material.png | file://x:/photopub/docs/0000000542/1abc8c49-102c-4031-a3ee-a80056e9b7ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31110b06_fdf6_45f1_92a0_ad2d021a6e52
BPVOP-722895-2016 | 2268005 | 12/13/2016 12:32:34 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Hot Water Boiler with Heating surface area of 33 square meters, Maximum Allowable Working Pressure (MAWP) of 100psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that safety relief valve has exceeded the required 2year interval for testing. Failure to have safety valve tested as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_relief_valve.png | file://x:/photopub/docs/0000000531/bc65e6b7-2ae6-414b-89b6-2e6329601ecd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f05cceda_1315_493d_8353_e875ee880812
BPVIN-722910-2016 | UW-077836-2013 | 12/13/2016 1:39:27 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Hot Water Supply Boiler with Heating Surface (HS) of 6 square meters, Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 240*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_room_door_without_emergency_shutdown_switch.png | file://x:/photopub/docs/0000000531/8dfe49c1-3e50-44e6-8356-fe9b74e5d10d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a96fffc8_2fc4_4827_95a2_c8071817eb08
ELIN-739031-2017 | EL-413153-2016 | 1/16/2017 10:25:20 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Missing_plates1.png,Missing_plates2.png The 100 amp 120/240volt combination sub-distribution panel has a missing breaker filler plate and a missing knock out filler, this can expose a person(s) to an accidental contact issue and this is a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Missing_plates2.png | file://x:/photopub/docs/0000000544/4c477450-cc5f-4350-95c0-0e02bc2995b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bae2e8a3_0524_44f0_a81d_2a1a07fee132
ELIN-739031-2017 | EL-413153-2016 | 1/16/2017 10:25:20 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Missing_plates1.png,Missing_plates2.png The 100 amp 120/240volt combination sub-distribution panel has a missing breaker filler plate and a missing knock out filler, this can expose a person(s) to an accidental contact issue and this is a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Missing_plates1.png | file://x:/photopub/docs/0000000544/e3bfa921-4edd-4302-a9fa-4a718ff9591e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bae2e8a3_0524_44f0_a81d_2a1a07fee132
ELHE-752638-2017 | HE-498789-2017 | 2/6/2017 2:49:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Conductors_and_cables_not_supported_properly_while_energized1.png,Conductors_and_cables_not_supported_properly_while_energized2.png,Conductors_and_cables_not_supported_properly_while_energized3.png,Conductors_and_cables_not_supported_properly_while_energized4.png,Conductors_and_cables_not_supported_properly_while_energized5.png,Conductors_and_cables_not_supported_properly_while_energized6.png Found branch circuit insulated conductors and cables to be not supported properly and is energized and not safe or authorized for connection to power supply system. When electrical equipment is not supported properly while being energized the electrical equipment conductors are subject to possible mechanical damage and could pose an electrical fire or shock hazard to people and property. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Conductors_and_cables_not_supported_properly_while_energized2.png | file://x:/photopub/docs/0000000554/166a4ec0-d3f3-4453-8165-3c28f3df2993.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93a36f4d_f6a0_49fa_a3d9_acfa68a37fa0
ELHE-752638-2017 | HE-498789-2017 | 2/6/2017 2:49:50 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Conductors_and_cables_not_supported_properly_while_energized1.png,Conductors_and_cables_not_supported_properly_while_energized2.png,Conductors_and_cables_not_supported_properly_while_energized3.png,Conductors_and_cables_not_supported_properly_while_energized4.png,Conductors_and_cables_not_supported_properly_while_energized5.png,Conductors_and_cables_not_supported_properly_while_energized6.png Found branch circuit insulated conductors and cables to be not supported properly and is energized and not safe or authorized for connection to power supply system. When electrical equipment is not supported properly while being energized the electrical equipment conductors are subject to possible mechanical damage and could pose an electrical fire or shock hazard to people and property. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Conductors_and_cables_not_supported_properly_while_energized6.png | file://x:/photopub/docs/0000000554/652e0553-9cff-472a-b44b-8ebfd546b1c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93a36f4d_f6a0_49fa_a3d9_acfa68a37fa0
ELIN-715854-2016 | 4890861 | 12/6/2016 1:39:57 PM | ASSESS: EL: Final | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | Dry box and fitting installed in wet location. Hazard is corrosion and a possible thermal effect if current state. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Outdoor_light_.png | file://x:/photopub/docs/0000000527/74a0501f-b7bb-4108-968a-fa7c755050b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81651642_2049_46fa_a264_ac8fa2c8c71b
ELIN-754473-2017 | EL-499414-2017 | 2/10/2017 10:49:02 AM | ASSESS: EL: Service Connection | png | #asFound Conductors from metre base to slab | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Consumer_service__consumer_service_conductor1.png,Consumer_service__consumer_service_conductor2.png Consumer service conductor from metre base to panelboard exceed 1.5 m in length. The consumer service conductors lack the necessary overcurrent protection from the utility should the consumer service conductors be damaged. See bcsa info bulletin in el 2012 revision 03, item f on page 4 of 5. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Consumer_service__consumer_service_conductor1.png | file://x:/photopub/docs/0000000556/0f566430-872c-47f7-ad26-faf0dfc96589.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ee785b8_0741_4d99_af85_505743f44e5c
ELIN-754473-2017 | EL-499414-2017 | 2/10/2017 10:49:02 AM | ASSESS: EL: Service Connection | png | #asFound Conductors exiting slab to panelboard located in garage | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Consumer_service__consumer_service_conductor1.png,Consumer_service__consumer_service_conductor2.png Consumer service conductor from metre base to panelboard exceed 1.5 m in length. The consumer service conductors lack the necessary overcurrent protection from the utility should the consumer service conductors be damaged. See bcsa info bulletin in el 2012 revision 03, item f on page 4 of 5. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Consumer_service__consumer_service_conductor2.png | file://x:/photopub/docs/0000000556/c4f0c996-c6f9-4f9d-9ac3-7b1a11b936fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ee785b8_0741_4d99_af85_505743f44e5c
BPVOP-755276-2017 | UW-500254-2017 | 2/10/2017 11:26:55 AM | ASSESS: BPV OP: Compliance Boiler | png | #asFound Unit | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Unit.png A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Unit.png | file://x:/photopub/docs/0000000556/8cd924ee-09b6-4544-9b32-4e5ed1ca827b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b084497_e82e_439c_a4e5_bdeddfb9604f
ELHE-760192-2017 | HE-502901-2017 | 2/20/2017 3:23:52 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 3 | #Damaged_meter_base_And_conduit1.png,Damaged_meter_base_And_conduit2.png,Damaged_meter_base_And_conduit3.png Damaged has been done to the meter base and Utility measurement meter conduit. The damage is human interference related to sabotage. Service is disconnected from the Utility supply. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Damaged_meter_base_And_conduit2.png | file://x:/photopub/docs/0000000559/61b69b7c-412d-4aa1-bae3-1a7165b61374.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__696789c3_c819_4bb8_ad89_9f5e7b832994
ELHE-760192-2017 | HE-502901-2017 | 2/20/2017 3:23:52 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 3 | #Damaged_meter_base_And_conduit1.png,Damaged_meter_base_And_conduit2.png,Damaged_meter_base_And_conduit3.png Damaged has been done to the meter base and Utility measurement meter conduit. The damage is human interference related to sabotage. Service is disconnected from the Utility supply. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Damaged_meter_base_And_conduit3.png | file://x:/photopub/docs/0000000559/ff71a57d-3936-431c-b1a4-cf2671fdc526.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__696789c3_c819_4bb8_ad89_9f5e7b832994
ELHE-760192-2017 | HE-502901-2017 | 2/20/2017 3:23:52 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 3 | #Damaged_meter_base_And_conduit1.png,Damaged_meter_base_And_conduit2.png,Damaged_meter_base_And_conduit3.png Damaged has been done to the meter base and Utility measurement meter conduit. The damage is human interference related to sabotage. Service is disconnected from the Utility supply. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Damaged_meter_base_And_conduit1.png | file://x:/photopub/docs/0000000559/12f84938-ce23-4dfe-87de-a994bc3617e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__696789c3_c819_4bb8_ad89_9f5e7b832994
ELIN-759087-2017 | EL-502274-2017 | 2/20/2017 5:14:27 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #Underground.png This assessment found an underground conduit installed approximately 50mm beside a water line rather than the required 300mm separation. The caution tape was installed directly on top of the conduit rather than in the middle of the trench as required; providing no warning for persons digging and presenting a shock hazard. Should the water line require repair a shock hazard is also present because the water line is so close. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Underground.png | file://x:/photopub/docs/0000000560/5aa498c2-7b76-4e72-91eb-dba089441a8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__efbe84ab_bc81_4bac_acec_5b9327db51a6
BPVOP-734383-2017 | 3550590 | 1/5/2017 12:00:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP195 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | 3 | 3 | Repacement Gauge glass and shutoff valves rated for 100 psi steam pressure Boiler MAWP is 150 psi. | 3 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | Boiler_Flue_piping_with_corrosion.png | file://x:/photopub/docs/0000000540/423422a4-ffc8-4b3a-8bf9-9e2ff5fc1b6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ac06e81_fa25_42b5_8eda_3c526a04bca2
BPVOP-734383-2017 | 3550590 | 1/5/2017 12:00:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP195 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | 3 | 3 | Repacement Gauge glass and shutoff valves rated for 100 psi steam pressure Boiler MAWP is 150 psi. | 3 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | Gauge_Glass_with_MAWP_of_100_psi.png | file://x:/photopub/docs/0000000540/4161fcdf-e2dd-46e1-a434-248e67dade0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ac06e81_fa25_42b5_8eda_3c526a04bca2
ELIN-732974-2017 | UW-486835-2017 | 1/4/2017 7:16:56 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | C.png | file://x:/photopub/docs/0000000539/2998526a-e62f-4cf9-b5c0-23c39810df1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7971f1f3_c77c_4d51_8577_e5c65d211aa2
ELIN-732974-2017 | UW-486835-2017 | 1/4/2017 7:16:56 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | B.png | file://x:/photopub/docs/0000000539/b8c94881-c2d5-4f54-b140-f1fb8a0ef79c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7971f1f3_c77c_4d51_8577_e5c65d211aa2
ELIN-732974-2017 | UW-486835-2017 | 1/4/2017 7:16:56 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | A.png | file://x:/photopub/docs/0000000539/10d01f31-d6ba-47a9-8e4f-80cee7125fa0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7971f1f3_c77c_4d51_8577_e5c65d211aa2
ELIN-732974-2017 | UW-486835-2017 | 1/4/2017 7:16:56 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Tuesday_Dec_27.png | file://x:/photopub/docs/0000000539/3ef06d0e-d042-4024-b5fd-a980c13a00e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7971f1f3_c77c_4d51_8577_e5c65d211aa2
ELIN-750694-2017 | EL-496616-2017 | 2/3/2017 11:04:01 AM | ASSESS: EL: Service Connection | png | #asFound Behind meters | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Consumer_service1.png,Consumer_service2.png The unprotected consumer services are installed inside a dwelling unit behind the quad meter assembly. The individual suites consumer service are entering in a crawl space to main floor, this exceeds the maximum permitted length. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Consumer_service2.png | file://x:/photopub/docs/0000000553/f8843581-5d0b-479f-a6d4-32dd7e4ad6b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e397224e_70e3_4b70_8294_fac2ed9838e5
ELIN-750694-2017 | EL-496616-2017 | 2/3/2017 11:04:01 AM | ASSESS: EL: Service Connection | png | #asFound From crawl space | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Consumer_service1.png,Consumer_service2.png The unprotected consumer services are installed inside a dwelling unit behind the quad meter assembly. The individual suites consumer service are entering in a crawl space to main floor, this exceeds the maximum permitted length. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Consumer_service1.png | file://x:/photopub/docs/0000000553/1f26b305-1683-401f-9b0b-334e39b2d03a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e397224e_70e3_4b70_8294_fac2ed9838e5
ELIN-749055-2017 | EL-489759-2017 | 2/1/2017 1:36:06 PM | ASSESS: EL: Final | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Panel_fillers_not_in_place_exposed_bussing.png Sub distribution panel located beside newly installed main panel. Circuit breaker that protects the sub distribution panel is in the off position at time of assessment. Turning the circuit breaker on would energize the bussing in this sub distribution panel, and would provide a shock or fire hazard if people or equipment were to come in contact with the bussing. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Panel_fillers_not_in_place_exposed_bussing.png | file://x:/photopub/docs/0000000551/61be71c0-86ba-44bc-a9c0-a313674afa98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e34c9a40_3744_4523_bea1_d4f36befbce6
ELIN-756512-2017 | EL-449030-2016 | 2/15/2017 1:35:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Nmsc1.png,Nmsc2.png,Nmsc3.png Cables are subject to mechanical damage and are not adequately protected with properly sized overcurrent devices. These are possible shock and fire hazards. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Nmsc3.png | file://x:/photopub/docs/0000000557/78ac4a51-94c7-40b1-80cf-74f835cbc846.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42d982ae_73fe_4cd8_837a_5930063c9ee6
ELIN-756512-2017 | EL-449030-2016 | 2/15/2017 1:35:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Nmsc1.png,Nmsc2.png,Nmsc3.png Cables are subject to mechanical damage and are not adequately protected with properly sized overcurrent devices. These are possible shock and fire hazards. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Nmsc2.png | file://x:/photopub/docs/0000000557/c5890baa-4f6e-4b72-8db1-ae2d8cbd229c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42d982ae_73fe_4cd8_837a_5930063c9ee6
ELIN-756512-2017 | EL-449030-2016 | 2/15/2017 1:35:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Nmsc1.png,Nmsc2.png,Nmsc3.png Cables are subject to mechanical damage and are not adequately protected with properly sized overcurrent devices. These are possible shock and fire hazards. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Nmsc1.png | file://x:/photopub/docs/0000000557/c95a50a8-5e60-4b75-81b0-c86601c9754f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42d982ae_73fe_4cd8_837a_5930063c9ee6
GAIN-727921-2016 | GA-356717-2016 | 1/29/2017 2:28:45 PM | ASSESS: GA: Final | png | #asFound | GA113 | Special/ positive vent system undersized for the length of run/elbows but appliance operates | 2 | 2 | #Reznor1.png,Reznor2.png All 3 unit heaters venting undersized to manufacture instructions, maximum total length is 50 feet, heater lengths are 64 feet, 80 feet, 89 feet. This could cause condensation build up of products of combustion to not terminate properly to the outdoors. | 2 | Special/ positive vent system undersized for the length of run/elbows but appliance operates | Reznor1.png | file://x:/photopub/docs/0000000549/ac3ae32e-8e8c-4425-83bb-7ee7b4bae47e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7b3ced9_4104_4e03_a539_1ea8fefe8b40
GAIN-727921-2016 | GA-356717-2016 | 1/29/2017 2:28:45 PM | ASSESS: GA: Final | png | #asFound | GA113 | Special/ positive vent system undersized for the length of run/elbows but appliance operates | 2 | 2 | #Reznor1.png,Reznor2.png All 3 unit heaters venting undersized to manufacture instructions, maximum total length is 50 feet, heater lengths are 64 feet, 80 feet, 89 feet. This could cause condensation build up of products of combustion to not terminate properly to the outdoors. | 2 | Special/ positive vent system undersized for the length of run/elbows but appliance operates | Reznor2.png | file://x:/photopub/docs/0000000549/14e9fd9d-9dd2-4da4-9916-e78f38aa1023.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7b3ced9_4104_4e03_a539_1ea8fefe8b40
ELOP-723456-2016 | EL-476022-2016 | 12/21/2016 2:21:01 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | An extension cord has been permanently installed and run under an exterior door to power some electric heat mats around a hot tub, the cord has been run to a general 15 amp 120 volt receptacle inside the building. This poses a shock hazard to persons and potential damage to the equipment. | 4 | Conductors, Misuse of flexible cords. | Heat_Mats.png | file://x:/photopub/docs/0000000535/7c35060f-3745-4983-9793-d5ad36785207.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5A2C6E5F_F70D_46A5_8FDC_0C37E5065524
ELOP-723454-2016 | EL-476023-2016 | 12/21/2016 12:04:50 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | The cord from the wall mounted TV has been run into the wall through a hole and then fished down to another opening at the baseboard where it comes out of the wall and is mounted to the baseboard running to a 15 amp 120 volt receptacle down the wall line. This poses a shock hazard for persons and potential damage to the TV equipment has the cord is not designed to be fastened in place or fished through walls. | 4 | Conductors, Misuse of flexible cords. | TV_Cord.png | file://x:/photopub/docs/0000000535/e176d5cc-053a-40c0-a807-0762b714e5eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76060BE5_EF5E_45CE_ABD2_3FDBBED0C7E1
ELOP-723454-2016 | EL-476023-2016 | 12/21/2016 12:04:50 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | The cord from the wall mounted TV has been run into the wall through a hole and then fished down to another opening at the baseboard where it comes out of the wall and is mounted to the baseboard running to a 15 amp 120 volt receptacle down the wall line. This poses a shock hazard for persons and potential damage to the TV equipment has the cord is not designed to be fastened in place or fished through walls. | 4 | Conductors, Misuse of flexible cords. | TV_Cord_at_baseboard.png | file://x:/photopub/docs/0000000535/41775031-d46a-4300-8879-caddf805c7ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76060BE5_EF5E_45CE_ABD2_3FDBBED0C7E1
ELOP-723456-2016 | EL-476022-2016 | 12/21/2016 2:21:01 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | An extension cord has been permanently installed and run under an exterior door to power some electric heat mats around a hot tub, the cord has been run to a general 15 amp 120 volt receptacle inside the building. This poses a shock hazard to persons and potential damage to the equipment. | 4 | Conductors, Misuse of flexible cords. | Cord_to_Heat_Mats.png | file://x:/photopub/docs/0000000535/f0486ebf-627c-4b03-9334-ff901f952e04.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5A2C6E5F_F70D_46A5_8FDC_0C37E5065524
ELIN-734163-2017 | EL-469654-2016 | 2/1/2017 8:43:50 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Bulkley.png The code requires that metal service conduits be bonded with bond bushing. The code requires this because it is on the supply side of the over current protection. It was observed that the pipe between the switch and meterbase has no bond bushing. Without proper bonding the pipe could become energized and without a reference to ground would not trip the supply authority over current protection. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Bulkley.png | file://x:/photopub/docs/0000000551/d854eadf-c19f-4be2-9264-5bb0742e87b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ce1c32_61f4_4a68_804d_b9880c23cd79
ELHE-759971-2017 | HE-502769-2017 | 2/20/2017 10:41:08 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cables and electrical equipment that are approved for dry locations use only, has become wet and is not approved for the use and has lost its insulation integrity and is not authorized for connection or use. | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors1.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors2.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors3.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors4.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors5.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors6.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors7.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors8.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors9.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors10.png,Dry_location_type_elec | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors6.png | file://x:/photopub/docs/0000000560/ebfdc330-0d89-4650-847b-16af604c347e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33e33e58_a028_4b39_8220_81b3eac993b9
GAIN-715568-2016 | GA-399345-2016 | 12/5/2016 2:29:02 PM | ASSESS: GA: Final | png | #asFound | GA124 | Blocked combustion air supply | 4 | 4 | Termination for water heater installed inches above the ducting and water heater in service and combustion air and exhaust blocked by snow and ice. This is a hazard as insignificant air can be brought to appliance and exhaust could recirculate into combustion chamber or building. | 4 | Blocked combustion air supply | Term_3.png | file://x:/photopub/docs/0000000526/6cad31c4-eff4-482e-8181-1a2e8d8d8a1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71ddfcd6_3223_436b_8bfa_8f3438a39310
GAIN-715568-2016 | GA-399345-2016 | 12/5/2016 2:29:02 PM | ASSESS: GA: Final | png | #asFound | GA124 | Blocked combustion air supply | 4 | 4 | Termination for water heater installed inches above the ducting and water heater in service and combustion air and exhaust blocked by snow and ice. This is a hazard as insignificant air can be brought to appliance and exhaust could recirculate into combustion chamber or building. | 4 | Blocked combustion air supply | Term_2.png | file://x:/photopub/docs/0000000526/5cd0028f-b65c-4b57-9e1d-90ebfcb490d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71ddfcd6_3223_436b_8bfa_8f3438a39310
GAIN-715568-2016 | GA-399345-2016 | 12/5/2016 2:29:02 PM | ASSESS: GA: Final | png | #asFound | GA124 | Blocked combustion air supply | 4 | 4 | Termination for water heater installed inches above the ducting and water heater in service and combustion air and exhaust blocked by snow and ice. This is a hazard as insignificant air can be brought to appliance and exhaust could recirculate into combustion chamber or building. | 4 | Blocked combustion air supply | Term1.png | file://x:/photopub/docs/0000000526/808c7854-052f-4a56-a62d-a62e0622926a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71ddfcd6_3223_436b_8bfa_8f3438a39310
ELIN-745813-2017 | EL-473867-2016 | 1/31/2017 12:24:22 PM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Shed_panelboard.png The 30 amp fed 120/240 volt nema 1 panelboard located at the front corner of the shed does not include protection from weather conditions with sliding door in open position and does not include a lockable cover to prevent unauthorized access, this can become an equipment damage issue | 3 | General Equipment is not approved for the specific use | Shed_panelboard.png | file://x:/photopub/docs/0000000551/d1946180-be2d-441d-8173-cf8ee7d09951.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ff7d563_285a_4ce1_a498_5eb67d8773ee
ELIN-748895-2017 | EL-487249-2017 | 2/1/2017 1:16:29 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound Long expanse of wall in living room up to rear entry door without a duplex receptacle. | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #No_outlet.png Rough wire of new single family dwelling. The receptacle spacing in the living room has not been calculated correctly. There is a long expanse of living room level of approximately 3 m without a duplex receptacle. This forces occupants to start using extension cords to our appliances and other electrical items and overloads circuits or causes thermal damage to the flexible cords and possibly a fire. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | No_outlet.png | file://x:/photopub/docs/0000000551/57996b5b-bef5-40ce-9d0b-5961c72eb58b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c699ec99_715d_4dfa_b070_44d6f9751e20
ELIN-739583-2017 | EL-439021-2016 | 1/17/2017 3:34:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 3 | #11.png The service cable is being damaged on the edge of the PVC conduit being used for its mechanical protection. Further damage over time may result is a shock or fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 11.png | file://x:/photopub/docs/0000000544/5491bdea-fa37-42c4-a953-3223309b232f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46dd3014_e3b3_473f_8282_407ad28791e2
ELHE-741091-2017 | HE-492291-2017 | 1/16/2017 1:23:16 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound unapproved_damaged_flexible_cord | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 4 | #unapproved_damaged_flexible_cord1.png,unapproved_damaged_flexible_cord2.png,unapproved_damaged_flexible_cord3.png,unapproved_damaged_flexible_cord4.png,unapproved_damaged_flexible_cord5.png,unapproved_damaged_flexible_cord6.png,unapproved_damaged_flexible_cord7.png Found unapproved, damaged and non-compliant flexible extension cord which was manufactured on site. The flexible cord is missing covers, has a plastic box on cord end which is portable and has water and mud on the product while there is no GFCI protection. When temporary electrical equipment wiring (such as flexible cord and box) is manufactured on site and is not approved for the use and is not mounted in place, the portable electrical equipment can become wet, damaged and unsafe and is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | unapproved_damaged_flexible_cord2.png | file://x:/photopub/docs/0000000547/794b8199-3e45-4d98-8ebf-affe6c5a51d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a9df29c_3147_4075_87ba_b12698235d34
ELHE-741091-2017 | HE-492291-2017 | 1/16/2017 1:23:16 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound unapproved_damaged_flexible_cord subjected to boards with nails damages and buried in mud and water and no GFCI protection. | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 4 | #unapproved_damaged_flexible_cord1.png,unapproved_damaged_flexible_cord2.png,unapproved_damaged_flexible_cord3.png,unapproved_damaged_flexible_cord4.png,unapproved_damaged_flexible_cord5.png,unapproved_damaged_flexible_cord6.png,unapproved_damaged_flexible_cord7.png Found unapproved, damaged and non-compliant flexible extension cord which was manufactured on site. The flexible cord is missing covers, has a plastic box on cord end which is portable and has water and mud on the product while there is no GFCI protection. When temporary electrical equipment wiring (such as flexible cord and box) is manufactured on site and is not approved for the use and is not mounted in place, the portable electrical equipment can become wet, damaged and unsafe and is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | unapproved_damaged_flexible_cord6.png | file://x:/photopub/docs/0000000547/a855caa9-9f4e-4abc-a91c-e9079551601d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a9df29c_3147_4075_87ba_b12698235d34
ELHE-741091-2017 | HE-492291-2017 | 1/16/2017 1:23:16 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound unapproved_damaged_flexible_cord | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 4 | #unapproved_damaged_flexible_cord1.png,unapproved_damaged_flexible_cord2.png,unapproved_damaged_flexible_cord3.png,unapproved_damaged_flexible_cord4.png,unapproved_damaged_flexible_cord5.png,unapproved_damaged_flexible_cord6.png,unapproved_damaged_flexible_cord7.png Found unapproved, damaged and non-compliant flexible extension cord which was manufactured on site. The flexible cord is missing covers, has a plastic box on cord end which is portable and has water and mud on the product while there is no GFCI protection. When temporary electrical equipment wiring (such as flexible cord and box) is manufactured on site and is not approved for the use and is not mounted in place, the portable electrical equipment can become wet, damaged and unsafe and is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | unapproved_damaged_flexible_cord1.png | file://x:/photopub/docs/0000000547/74e2ca7e-114e-4ac9-8312-8f02159ff412.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a9df29c_3147_4075_87ba_b12698235d34
ELHE-741091-2017 | HE-492291-2017 | 1/16/2017 1:23:16 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound unapproved_damaged_flexible_cord subjected to boards with nails damages and buried in mud and water and no GFCI protection. | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 4 | #unapproved_damaged_flexible_cord1.png,unapproved_damaged_flexible_cord2.png,unapproved_damaged_flexible_cord3.png,unapproved_damaged_flexible_cord4.png,unapproved_damaged_flexible_cord5.png,unapproved_damaged_flexible_cord6.png,unapproved_damaged_flexible_cord7.png Found unapproved, damaged and non-compliant flexible extension cord which was manufactured on site. The flexible cord is missing covers, has a plastic box on cord end which is portable and has water and mud on the product while there is no GFCI protection. When temporary electrical equipment wiring (such as flexible cord and box) is manufactured on site and is not approved for the use and is not mounted in place, the portable electrical equipment can become wet, damaged and unsafe and is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | unapproved_damaged_flexible_cord7.png | file://x:/photopub/docs/0000000547/d33fc6f6-b3f2-4a7d-a0b6-a6d8196f1b1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a9df29c_3147_4075_87ba_b12698235d34
ELHE-741091-2017 | HE-492291-2017 | 1/16/2017 1:23:16 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound unapproved_damaged_flexible_cord subjected to boards with nails damages and buried in mud and water and no GFCI protection. | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 4 | #unapproved_damaged_flexible_cord1.png,unapproved_damaged_flexible_cord2.png,unapproved_damaged_flexible_cord3.png,unapproved_damaged_flexible_cord4.png,unapproved_damaged_flexible_cord5.png,unapproved_damaged_flexible_cord6.png,unapproved_damaged_flexible_cord7.png Found unapproved, damaged and non-compliant flexible extension cord which was manufactured on site. The flexible cord is missing covers, has a plastic box on cord end which is portable and has water and mud on the product while there is no GFCI protection. When temporary electrical equipment wiring (such as flexible cord and box) is manufactured on site and is not approved for the use and is not mounted in place, the portable electrical equipment can become wet, damaged and unsafe and is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | unapproved_damaged_flexible_cord4.png | file://x:/photopub/docs/0000000547/9bc93163-9f12-4a27-9ef2-5a8f1489c2bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a9df29c_3147_4075_87ba_b12698235d34
ELIN-732872-2017 | EL-448553-2016 | 1/17/2017 10:34:56 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #A1.png,A2.png Bond wire not connected to panel enclosure. This is a shock hazard as the upstream over-current protection will not function properly. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | A2.png | file://x:/photopub/docs/0000000544/897b3cc3-fad4-4235-bc39-84075c0e3bea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3197b7dc_a10f_47b0_8dfe_cb6e5e41c954
ELIN-732875-2017 | EL-436518-2016 | 1/17/2017 11:58:59 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Z1.png,Z2.png,Z3.png Light in closet permanently connected with fixture wire. | 4 | Conductors, Misuse of flexible cords. | Z1.png | file://x:/photopub/docs/0000000544/07f6691c-54d8-4ed8-8406-289f96d23c21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f153252_4d6f_47db_a7de_16fdf1ae80c1
ELIN-732872-2017 | EL-448553-2016 | 1/17/2017 10:34:56 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #A1.png,A2.png Bond wire not connected to panel enclosure. This is a shock hazard as the upstream over-current protection will not function properly. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | A1.png | file://x:/photopub/docs/0000000544/048918df-0c44-4aba-abb9-31bcc7a612b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3197b7dc_a10f_47b0_8dfe_cb6e5e41c954
ELIN-732875-2017 | EL-436518-2016 | 1/17/2017 11:58:59 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Z1.png,Z2.png,Z3.png Light in closet permanently connected with fixture wire. | 4 | Conductors, Misuse of flexible cords. | Z2.png | file://x:/photopub/docs/0000000544/bd58f6ec-b59b-4260-b84c-2bf2fcef9f9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f153252_4d6f_47db_a7de_16fdf1ae80c1
ELIN-732875-2017 | EL-436518-2016 | 1/17/2017 11:58:59 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Z1.png,Z2.png,Z3.png Light in closet permanently connected with fixture wire. | 4 | Conductors, Misuse of flexible cords. | Z3.png | file://x:/photopub/docs/0000000544/cd840fde-7401-4f4d-9d96-6d1711d1b0c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f153252_4d6f_47db_a7de_16fdf1ae80c1
ELIN-760922-2017 | EL-503240-2017 | 2/22/2017 1:36:25 PM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #5.png Consumers service point of attachment is above point of emergence of conductors. This could allow for moisture to enter consumers meter base. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 5.png | file://x:/photopub/docs/0000000561/1210a2a2-c9dc-4345-ab22-0e0240942452.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e53ba72c_6bc0_4ac7_b035_ebf744ec4ca0
ELIN-759721-2017 | EL-481876-2016 | 2/20/2017 12:55:24 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #1A.png Cables located to close to edge of stud. If penetrated by gyrocompass screws a shock hazard may be present. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 1A.png | file://x:/photopub/docs/0000000559/a882b79c-0a7c-4357-ba7c-49b8a175a6c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__adb26f8c_9fb4_42f8_8996_539162d95e55
ELIN-756333-2017 | EL-500733-2017 | 2/20/2017 2:21:21 PM | ASSESS: EL: Final | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 4 | #1.png Opening between outlet box and finished wall. Should arcing occur during a fault the sparks can leave the outlet box and fall into the opening between the front edge of the outlet box and the wall. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 1.png | file://x:/photopub/docs/0000000559/21766198-2cb8-409d-be61-ba4ace1e77ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7e18b77_0fe3_48ba_809f_50d246f5b5fc
ELIN-723637-2016 | EL-477211-2016 | 12/21/2016 7:56:51 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found bonding is not done correctly and 120/240 volt 60 amp rated feeder cable has aluminum bonding conductor strip that is not terminated at all to panelboard metal enclosure for properly bonding all electrical equipment. When electrical equipment is not bonded and if there is a fault condition on the electrical system, the over-current devices may not operate immediately or effectively or properly to open and clear the fault on the electrical system and could cause an electrical fire or shock hazard to people or property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | feeder_bonding_conductor_strip_is_not_terminated_to_panel_metal_enclosure.png | file://x:/photopub/docs/0000000534/33f9ad57-6b04-43ac-9785-2b6a583fcc6f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ecc0e4b_eadc_4f2a_bb67_582562834e0b
GAIN-713557-2016 | GA-399960-2016 | 12/5/2016 10:30:47 AM | ASSESS: GA: Final | png | #asFound | GA080 | Line pressure regulator without required overpressure protection in place | 3 | 2 | Vent limiter not installed in line pressure regulator. A failure of the device could allow gas pressure and volume to enter the occupied space in excess of the limits allowed under regulations. Possible fire risk. Valve to appliance was off at time of assessment. | 3 | Line pressure regulator without required overpressure protection in place | Church.png | file://x:/photopub/docs/0000000526/ee6a7066-fad8-4310-af72-4a3f165af733.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b673f5e4_55ba_493c_9e56_7361e604a3cb
ELOP-735173-2017 | EL-445887-2016 | 1/9/2017 12:54:14 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | #Panel_e_open.png Electrical panel with open breaker spaces creating a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Panel_e_open.png | file://x:/photopub/docs/0000000540/03b9fb49-e065-497b-b8a3-76d235dc513c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__418c9625_4d09_46d9_9911_7b4fbe2fee84
BPVOP-740943-2017 | 3045551 | 1/18/2017 9:12:13 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | #Pitting_.png Pressure retaining components must be fit for service and maintain minimal required shell thickness in order maintain maximum rated working pressure. I found active general corrosion, which could reduce the allowable metal thickness. Potential exists for an incident due to deteriorated condition of pressure retaining parts | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Pitting_.png | file://x:/photopub/docs/0000000544/45e17a21-f203-41cc-aa3f-7b7991943f15.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc24f1a5_3151_4560_89ac_a9e5206c032c
GAUP-729350-2016 | UW-484799-2016 | 12/23/2016 2:11:23 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | The as found hazard was a portion of type c vent utilized in a category three venting system. This is a hazard because c-vent is not a sealed venting system and can allow flue gasses to escape into the room and it is also susceptible to deterioration from condensate. | 3 | Unapproved venting material | BH_to_C_vent_2.png | file://x:/photopub/docs/0000000535/f258fba7-330d-4f9f-812f-96657f2dbdb7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b8f2c29_4d56_47eb_a3bb_ceb1fe4b88ad
GAUP-729350-2016 | UW-484799-2016 | 12/23/2016 2:11:23 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | The as found hazard was a portion of type c vent utilized in a category three venting system. This is a hazard because c-vent is not a sealed venting system and can allow flue gasses to escape into the room and it is also susceptible to deterioration from condensate. | 3 | Unapproved venting material | BH_to_C_vent.png | file://x:/photopub/docs/0000000535/ba54de04-3473-4247-a1e5-f76e664503ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b8f2c29_4d56_47eb_a3bb_ceb1fe4b88ad
BPVIN-760278-2017 | BPV-399898-2016 | 2/21/2017 9:48:27 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | #Buffer_tank_and_Safety_Relief_Valve_1.png,Buffer_tank_and_Safety_Relief_Valve_2.png During the inspection of a buffer tank with MAWP of 125 psig it was found that the Safety Relief Valves set point was 150 psig. In case of an overpressure situation the Safety Relief Valves will not protect this pressure vessel. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | Buffer_tank_and_Safety_Relief_Valve_1.png | file://x:/photopub/docs/0000000560/d90f7908-150a-47cf-9275-f4d19497c1a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__868d925f_09b4_41bd_88cd_3a9e03345b24
BPVIN-760278-2017 | BPV-399898-2016 | 2/21/2017 9:48:27 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | #Buffer_tank_and_Safety_Relief_Valve_1.png,Buffer_tank_and_Safety_Relief_Valve_2.png During the inspection of a buffer tank with MAWP of 125 psig it was found that the Safety Relief Valves set point was 150 psig. In case of an overpressure situation the Safety Relief Valves will not protect this pressure vessel. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | Buffer_tank_and_Safety_Relief_Valve_2.png | file://x:/photopub/docs/0000000560/dc5439dc-8876-4efc-aac7-7265740de38c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__868d925f_09b4_41bd_88cd_3a9e03345b24
ELHE-741091-2017 | HE-492291-2017 | 1/16/2017 1:23:16 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound unapproved_damaged_flexible_cord subjected to boards with nails damages and buried in mud and water and no GFCI protection. | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 4 | #unapproved_damaged_flexible_cord1.png,unapproved_damaged_flexible_cord2.png,unapproved_damaged_flexible_cord3.png,unapproved_damaged_flexible_cord4.png,unapproved_damaged_flexible_cord5.png,unapproved_damaged_flexible_cord6.png,unapproved_damaged_flexible_cord7.png Found unapproved, damaged and non-compliant flexible extension cord which was manufactured on site. The flexible cord is missing covers, has a plastic box on cord end which is portable and has water and mud on the product while there is no GFCI protection. When temporary electrical equipment wiring (such as flexible cord and box) is manufactured on site and is not approved for the use and is not mounted in place, the portable electrical equipment can become wet, damaged and unsafe and is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | unapproved_damaged_flexible_cord5.png | file://x:/photopub/docs/0000000547/5fa74de0-5658-4f64-91db-1e73e34dc4b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a9df29c_3147_4075_87ba_b12698235d34
ELHE-741091-2017 | HE-492291-2017 | 1/16/2017 1:23:16 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound unapproved_damaged_flexible_cord subjected to boards with nails damages and buried in mud and water and no GFCI protection. | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 4 | #unapproved_damaged_flexible_cord1.png,unapproved_damaged_flexible_cord2.png,unapproved_damaged_flexible_cord3.png,unapproved_damaged_flexible_cord4.png,unapproved_damaged_flexible_cord5.png,unapproved_damaged_flexible_cord6.png,unapproved_damaged_flexible_cord7.png Found unapproved, damaged and non-compliant flexible extension cord which was manufactured on site. The flexible cord is missing covers, has a plastic box on cord end which is portable and has water and mud on the product while there is no GFCI protection. When temporary electrical equipment wiring (such as flexible cord and box) is manufactured on site and is not approved for the use and is not mounted in place, the portable electrical equipment can become wet, damaged and unsafe and is a possible electrical fire or shock hazard to people and property. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | unapproved_damaged_flexible_cord3.png | file://x:/photopub/docs/0000000547/47f05a88-1545-47d8-a240-1e1518c307f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a9df29c_3147_4075_87ba_b12698235d34
ELIN-712782-2016 | EL-469088-2016 | 11/30/2016 2:41:26 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | The service mast must be supported at the highest location possible to prevent strain from the weight of overhead conductors from pulling or bending the service mast. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 301_Poplar_service_mast_.png | file://x:/photopub/docs/0000000525/daec9d4a-f0b5-40cb-82be-00520e48babd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df5f8dee_3159_414b_ac20_ef0f3134aeba
GAIN-717247-2016 | GA-474016-2016 | 12/6/2016 12:31:11 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | Clearance from vent termination to combustion air intake not maintained. Clearance must be maintained to prevent recirculating of combustion product causing incomplete combustion and carbon monoxide production. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Clearance_to_air_intake_not_maintained.png | file://x:/photopub/docs/0000000526/fef731a0-0c0c-411b-812c-090a4e4ba0f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__048d410b_a886_4ab9_ad66_52a7a4fe0cba
GAIN-715864-2016 | GA-473820-2016 | 12/6/2016 2:29:15 PM | ASSESS: GA: Final | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | Clearance to mechanical combustion air intake from a regulator relief not maintained. Clearance must be maintained to prevent combustible gas from being drawn into the combustion air intake of an appliance, which could cause fire or explosion on startup of the appliance. | 3 | insufficient mechanical air intake clearance to gas regulator relief | Clearance_to_service_regulator_not_maintained.png | file://x:/photopub/docs/0000000526/c2a6e391-6338-47bd-8a32-265ca67746e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e978fe5a_2106_4e9f_abdf_fc744d21a391
BPVIN-749094-2017 | BPV-496796-2017 | 1/31/2017 11:56:05 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP014 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | 1 | 1 | #Clearances.png | 1 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | Clearances.png | file://x:/photopub/docs/0000000553/14850afc-06ba-4dec-b72b-cb8f53bcd34f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e54f8a31_91df_4659_8dd0_e0fddecff5c0
GAUP-729350-2016 | UW-484799-2016 | 12/23/2016 2:11:23 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | The as found hazard was a portion of type c vent utilized in a category three venting system. This is a hazard because c-vent is not a sealed venting system and can allow flue gasses to escape into the room and it is also susceptible to deterioration from condensate. | 3 | Unapproved venting material | Missing_limiter.png | file://x:/photopub/docs/0000000535/2ce88ca4-513e-494d-88f9-2139b28591d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b8f2c29_4d56_47eb_a3bb_ceb1fe4b88ad
GAUP-729350-2016 | UW-484799-2016 | 12/23/2016 2:11:23 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | The as found hazard was a portion of type c vent utilized in a category three venting system. This is a hazard because c-vent is not a sealed venting system and can allow flue gasses to escape into the room and it is also susceptible to deterioration from condensate. | 3 | Unapproved venting material | C_vent_term_hood.png | file://x:/photopub/docs/0000000535/cc9d3aca-5cb1-4d04-9bc6-bcbba751dd0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b8f2c29_4d56_47eb_a3bb_ceb1fe4b88ad
GAUP-729350-2016 | UW-484799-2016 | 12/23/2016 2:11:23 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | The as found hazard was a portion of type c vent utilized in a category three venting system. This is a hazard because c-vent is not a sealed venting system and can allow flue gasses to escape into the room and it is also susceptible to deterioration from condensate. | 3 | Unapproved venting material | Boiler_data_plate.png | file://x:/photopub/docs/0000000535/2348ecd3-a7fe-47cd-9696-17db20ea1ef2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b8f2c29_4d56_47eb_a3bb_ceb1fe4b88ad
GAUP-729350-2016 | UW-484799-2016 | 12/23/2016 2:11:23 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | The as found hazard was a portion of type c vent utilized in a category three venting system. This is a hazard because c-vent is not a sealed venting system and can allow flue gasses to escape into the room and it is also susceptible to deterioration from condensate. | 3 | Unapproved venting material | Burner_data_plate.png | file://x:/photopub/docs/0000000535/ae256438-aad2-4e02-adbf-83e97506ac1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b8f2c29_4d56_47eb_a3bb_ceb1fe4b88ad
ELIN-728967-2016 | EL-458334-2016 | 12/23/2016 9:23:57 AM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Meterbase_.png | file://x:/photopub/docs/0000000535/37a462c4-0198-407d-8b31-3a4cebb9b42b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__270096aa_ae32_48b0_aecd_575df7fdaaf7
PROP-739288-2017 | PR-480013-2016 | 1/16/2017 10:01:44 AM | ASSESS: PR OP: Operational | png | #asFound This shows the open access to the underside of the conveyor, caused by a unattached section of skirting | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | #Bigfoot_skirting_section_failed.png Conveyor skirting has come loose from structure. A person could fall into the underside of conveyor, where moving parts are present. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Bigfoot_skirting_section_failed.png | file://x:/photopub/docs/0000000544/0590194b-c2ae-4d58-bd7b-1a8da48c3504.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ec0aaab_9447_4c2a_bdd5_ae6e791af6bd
ELIN-701692-2016 | EL-455414-2016 | 12/5/2016 1:32:10 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | A central electric furnace was installed which requires 45 amps at 240 volts to operate. The furnace was connected to a 50 amp circuit breaker rated for a maximum connected load of 40 amps when utilized with heating equipment based on the rating of the panelboard it was installed in. Circuit breakers subjected to loads in excess of their rating can fail unpredictably damaging property or injuring persons. | 3 | Conductors Equipment is not approved for the specific use. | 50_amp_breaker_on_45_amp_heating_load.png | file://x:/photopub/docs/0000000526/0c60f1b9-ab67-4c2e-85b2-64398188632c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d336bc1_b823_4c89_881c_ca4adf7ea6ef
ELHE-725300-2016 | HE-482279-2016 | 12/16/2016 2:11:26 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | The 15 amp 120 volt receptacles in the kitchen are missing cover plates and one is hanging out of wall. This is a shock hazard to any persons in the area | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Kitchen__1.png | file://x:/photopub/docs/0000000532/76221de7-1315-4586-9a83-bc6cfa84fd19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac2fcb3b_904c_4a6e_9f1d_b1da60434e20
ELHE-725300-2016 | HE-482279-2016 | 12/16/2016 2:11:26 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | The 15 amp 120 volt receptacles in the kitchen are missing cover plates and one is hanging out of wall. This is a shock hazard to any persons in the area | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Kitchen__2.png | file://x:/photopub/docs/0000000532/df4a72b8-c290-40d8-a86e-c48150f13e7f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac2fcb3b_904c_4a6e_9f1d_b1da60434e20
ELIN-727043-2016 | EL-403333-2016 | 12/22/2016 9:48:15 AM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | No covers installed. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | D.png | file://x:/photopub/docs/0000000534/fda82b4a-e327-4359-9d2b-c63e63a3f237.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4bfa76d_7ede_43f7_b0e2_fdba6bccab8b
ELIN-727043-2016 | EL-403333-2016 | 12/22/2016 9:48:15 AM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | No covers installed. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | b.png | file://x:/photopub/docs/0000000534/e3534a50-ae5c-4f1e-878d-f77fc7f9fa65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4bfa76d_7ede_43f7_b0e2_fdba6bccab8b
EDRI-751492-2017 | ED-426307-2016 | 2/3/2017 | ASSESS: ED RI: Initial | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | #No_hoarding.png Braces for the tower structure of the hoist is normally blocked off by hoarding, preventing access to the tower, where a 4000 pound counterweight runs up and down the tower (through the braces). No hoarding was present on the top two braces, providing people with a means to walk out to the tower where a fast moving 4000 pound counterweight runs up and down the tower. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | No_hoarding.png | file://x:/photopub/docs/0000000553/59dc824f-4242-448d-a3ab-573f51c4bf40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d180143_cd34_4b01_ad84_521b0a55b3a0
ELIN-730675-2016 | EL-485423-2016 | 12/30/2016 11:26:18 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Service connection for new single-family dwelling. The grounding electrode for the service has not been buried in the earth. Therefore there is no effective system ground. This can negatively affect the tripping of circuit breakers in a fault. It is a shock and fire hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Electrode_laying_on_earth_.png | file://x:/photopub/docs/0000000536/05408a33-8865-49d1-8717-09cfc8a44460.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ece89bdf_d7a3_4afe_8a38_da2e9cde5702
PROP-739291-2017 | PR-480015-2016 | 1/16/2017 10:52:01 AM | ASSESS: PR OP: Operational | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | #Skirting_damaged_by_groomer_4_section_length.png Walkway had been damaged by groomer, skirting attached to that section of walkway my be damaged | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Skirting_damaged_by_groomer_4_section_length.png | file://x:/photopub/docs/0000000544/276891b1-1a3a-402b-af88-7b53ce947dec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de48935e_324e_4655_9687_5522cc7f724d
PROP-599985-2016 | 2224216 | 1/24/2017 10:43:12 AM | ASSESS: PR OP: RAP | png | #asFound Safety gate cable is fixed on outside end | PR025 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Safety_gate_not_detachable_on_both_ends.png The cable of a current carrying type safety gate does not detach at both ends (one end is fixed). This result a hazard in which a passenger who traveled through the safety gate may become entangled with the safety gate cable. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Safety_gate_not_detachable_on_both_ends.png | file://x:/photopub/docs/0000000548/5bf8ed27-af34-4baa-98eb-8ac58bb52dea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6A741D68_793A_4BCB_B609_6A92DD036177
PROP-599986-2016 | 3944656 | 1/24/2017 2:37:04 PM | ASSESS: PR OP: RAP | png | #asFound Top station pull cord not labeled | PR024 | Procedures not posted Improper training or procedure | 1 | 1 | #Manual_stopping_devices_not_tagged1.png,Manual_stopping_devices_not_tagged2.png,Manual_stopping_devices_not_tagged3.png It was observed that the an attendant stop button and a stop pull cord device was not tagged indicting the function. Stopping devices are to be labeled so that a person can identify the function. | 1 | Procedures not posted Improper training or procedure | Manual_stopping_devices_not_tagged3.png | file://x:/photopub/docs/0000000548/a92d26c4-ffb1-4aee-84fe-a1b75a050508.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14D497A1_6C67_476E_87DE_73E40453C99B
PROP-599986-2016 | 3944656 | 1/24/2017 2:37:04 PM | ASSESS: PR OP: RAP | png | #asFound Pull cord at bottom station | PR024 | Procedures not posted Improper training or procedure | 1 | 1 | #Manual_stopping_devices_not_tagged1.png,Manual_stopping_devices_not_tagged2.png,Manual_stopping_devices_not_tagged3.png It was observed that the an attendant stop button and a stop pull cord device was not tagged indicting the function. Stopping devices are to be labeled so that a person can identify the function. | 1 | Procedures not posted Improper training or procedure | Manual_stopping_devices_not_tagged1.png | file://x:/photopub/docs/0000000548/c642cde9-139e-4e49-8174-4d98fa1eb61d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14D497A1_6C67_476E_87DE_73E40453C99B
PROP-599986-2016 | 3944656 | 1/24/2017 2:37:04 PM | ASSESS: PR OP: RAP | png | #asFound Stop button pedestal not labeled | PR024 | Procedures not posted Improper training or procedure | 1 | 1 | #Manual_stopping_devices_not_tagged1.png,Manual_stopping_devices_not_tagged2.png,Manual_stopping_devices_not_tagged3.png It was observed that the an attendant stop button and a stop pull cord device was not tagged indicting the function. Stopping devices are to be labeled so that a person can identify the function. | 1 | Procedures not posted Improper training or procedure | Manual_stopping_devices_not_tagged2.png | file://x:/photopub/docs/0000000548/98fd30eb-af90-449a-8dc6-bf652e75b06f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14D497A1_6C67_476E_87DE_73E40453C99B
ELIN-727043-2016 | EL-403333-2016 | 12/22/2016 9:48:15 AM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | No covers installed. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | E.png | file://x:/photopub/docs/0000000534/91992558-8002-475c-ad1a-7a31b338fc22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4bfa76d_7ede_43f7_b0e2_fdba6bccab8b
ELIN-727043-2016 | EL-403333-2016 | 12/22/2016 9:48:15 AM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | No covers installed. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | A.png | file://x:/photopub/docs/0000000534/95f7316a-b9f7-4f8f-9e6d-8474ef2efe70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4bfa76d_7ede_43f7_b0e2_fdba6bccab8b
ELIN-727043-2016 | EL-403333-2016 | 12/22/2016 9:48:15 AM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | No covers installed. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | C.png | file://x:/photopub/docs/0000000534/6f0e158a-bd2c-4fef-9682-ea0ad8f243df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4bfa76d_7ede_43f7_b0e2_fdba6bccab8b
GAHE-745677-2017 | HE-494982-2017 | 1/27/2017 1:20:30 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound Propane | GA144 | Missing mandatory safety controls | 4 | 4 | #Propane_system_Cypress_bowl1.png,Propane_system_Cypress_bowl2.png The as found hazard was a propane dispensing station without an emergency shut off means. This could result in personnel not being able to shut off liquid propane in the event of a malfunction or emergency. | 4 | Missing mandatory safety controls | Propane_system_Cypress_bowl2.png | file://x:/photopub/docs/0000000548/24ece195-483b-48e1-bbd7-bd8daeb2a338.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f728ee3_badd_45a3_9702_6b6a3933a314
GAHE-758016-2017 | HE-501610-2017 | 2/16/2017 9:50:14 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Vent.png,Vent_connector.png,Vent_connector2.png Duct work for a forced air furnace has been added on top of draft hood of hot water tank to vent flue gases. Ductwork is not approved as a venting material. Ductwork is not sealed sufficiently to convey the flow of flue gases to chimney, flue gases could leak out not common area leading to possible CO poisoning to office staff and workers | 3 | Unapproved venting material | Vent_connector.png | file://x:/photopub/docs/0000000558/10554ca8-2a39-4838-8cbf-20d1b1ee01c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25b50b1f_b856_482f_b0cf_43c66d629017
GAHE-758016-2017 | HE-501610-2017 | 2/16/2017 9:50:14 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Vent.png,Vent_connector.png,Vent_connector2.png Duct work for a forced air furnace has been added on top of draft hood of hot water tank to vent flue gases. Ductwork is not approved as a venting material. Ductwork is not sealed sufficiently to convey the flow of flue gases to chimney, flue gases could leak out not common area leading to possible CO poisoning to office staff and workers | 3 | Unapproved venting material | Vent.png | file://x:/photopub/docs/0000000558/217ca457-084f-4af9-88c4-cb45237bcc6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25b50b1f_b856_482f_b0cf_43c66d629017
GAHE-758016-2017 | HE-501610-2017 | 2/16/2017 9:50:14 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Vent.png,Vent_connector.png,Vent_connector2.png Duct work for a forced air furnace has been added on top of draft hood of hot water tank to vent flue gases. Ductwork is not approved as a venting material. Ductwork is not sealed sufficiently to convey the flow of flue gases to chimney, flue gases could leak out not common area leading to possible CO poisoning to office staff and workers | 3 | Unapproved venting material | Vent_connector2.png | file://x:/photopub/docs/0000000558/d5c049de-007b-4fee-952e-3e15f7cbf512.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25b50b1f_b856_482f_b0cf_43c66d629017
GAUP-762000-2017 | UW-503894-2017 | 2/22/2017 2:29:14 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound Fully pressurized, open gas line serving a disconnected gas range | GA000 | No Created Hazard Identified | 0 | 0 | #open_gas_line.png | 0 | No Created Hazard Identified | open_gas_line.png | file://x:/photopub/docs/0000000561/96dc0225-d7d1-458e-8bfc-b397937cc832.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d647ed71_f8e4_465a_ae20_a5d0b10bbd0b
ELIN-717777-2016 | EL-476606-2016 | 12/6/2016 10:49:36 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | The EXISTING 200 amp 120/240 volt 1-phase 3-wire service to be RE-connected includes the point of attachment located directly beside a roofline overhang that is impeding with a clear connection point for the utility overhead line. Connection at this point will not give adequate clearance for conductors and will create physical contact of the overhead utility line on the metal roof overhang creating both a shock and thermal hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Angle_building_insulator_rack_view.png | file://x:/photopub/docs/0000000527/b6e939a1-4d2b-477d-9ee9-4358d6e46e01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc897146_aa42_4d28_be10_09f77645863c
ELIN-717777-2016 | EL-476606-2016 | 12/6/2016 10:49:36 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | The EXISTING 200 amp 120/240 volt 1-phase 3-wire service to be RE-connected includes the point of attachment located directly beside a roofline overhang that is impeding with a clear connection point for the utility overhead line. Connection at this point will not give adequate clearance for conductors and will create physical contact of the overhead utility line on the metal roof overhang creating both a shock and thermal hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Front_view.png | file://x:/photopub/docs/0000000527/7698f49f-c6e2-45fd-82a2-fc97965b4db0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc897146_aa42_4d28_be10_09f77645863c
ELIN-717777-2016 | EL-476606-2016 | 12/6/2016 10:49:36 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | The EXISTING 200 amp 120/240 volt 1-phase 3-wire service to be RE-connected includes the point of attachment located directly beside a roofline overhang that is impeding with a clear connection point for the utility overhead line. Connection at this point will not give adequate clearance for conductors and will create physical contact of the overhead utility line on the metal roof overhang creating both a shock and thermal hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Utility_overhead_line_angle.png | file://x:/photopub/docs/0000000527/25f77f46-50c9-41f3-9b8e-ca6097af1778.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc897146_aa42_4d28_be10_09f77645863c
ELIN-741854-2017 | EL-489271-2017 | 1/20/2017 3:32:50 PM | ASSESS: EL: Final | png | #asFound Cord is pinched when door is closed. | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Cord2.png Fire hazard from pinched extension cord. | 4 | Conductors, Misuse of flexible cords. | Cord2.png | file://x:/photopub/docs/0000000546/430abe8a-8515-4c88-9781-74d790b93c39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61685915_a209_4aab_87da_ebb96389a710
GAHE-754269-2017 | HE-499554-2017 | 2/9/2017 8:28:10 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Vent_connector_clearances.png Single wall vent connectors are too close to combustible material. This may eventually lead to a fire hazard. | 3 | Non compliant Type C Vent clearance | Vent_connector_clearances.png | file://x:/photopub/docs/0000000556/a9cf438d-b5aa-4e70-ba64-c9eaa42d6473.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2e51e69_45a4_4a74_a837_6639b99cef0e
ELIN-744623-2017 | EL-483653-2016 | 1/26/2017 11:26:42 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | #Meter_base_connections.png,Panel_board_connections.png Line and neutral connections when cross connected result in dead short circuit and dangerous condition | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Panel_board_connections.png | file://x:/photopub/docs/0000000549/32959056-d61f-4c4a-ae13-2e658d96ad1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca4af4ca_a7b4_442e_a1ed_db4f7d6238cc
ELIN-744623-2017 | EL-483653-2016 | 1/26/2017 11:26:42 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | #Meter_base_connections.png,Panel_board_connections.png Line and neutral connections when cross connected result in dead short circuit and dangerous condition | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Meter_base_connections.png | file://x:/photopub/docs/0000000549/55e402df-5079-4314-8078-59acea0445ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca4af4ca_a7b4_442e_a1ed_db4f7d6238cc
BPVOP-741061-2017 | 3676222 | 1/18/2017 12:55:31 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_relief_valve.png Upon assessment of Hot Water Boiler with Heating surface area of 17.5 quare meters, Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 240*Fahrenheit, it was determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE.png | file://x:/photopub/docs/0000000545/f174f6b0-5428-4ff0-9056-579ac78f3984.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d20dad0_71b3_433b_a880_25911abb3268
BPVOP-741061-2017 | 3676222 | 1/18/2017 12:55:31 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound No record of testing and servicing/replacement of safety relief valve | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_relief_valve.png Upon assessment of Hot Water Boiler with Heating surface area of 17.5 quare meters, Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 240*Fahrenheit, it was determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_relief_valve.png | file://x:/photopub/docs/0000000545/2b63ecb1-1198-4828-b944-58bf025182ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d20dad0_71b3_433b_a880_25911abb3268
ELOP-760049-2017 | 7127 | 2/20/2017 3:10:22 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Panel_filler_missing1.png,Panel_filler_missing2.png Open breaker space on energized panel leaving exposed electrical parts and a potential shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel_filler_missing1.png | file://x:/photopub/docs/0000000560/34112fb6-53af-4b06-87bd-dbf402c2bf89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2da5df1f_ab96_4d50_bd5c_e49d86a0f7e2
ELOP-760049-2017 | 7127 | 2/20/2017 3:10:22 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Panel_filler_missing1.png,Panel_filler_missing2.png Open breaker space on energized panel leaving exposed electrical parts and a potential shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel_filler_missing2.png | file://x:/photopub/docs/0000000560/f3361b1d-05ef-4c96-bcfb-e15b85eb39b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2da5df1f_ab96_4d50_bd5c_e49d86a0f7e2
GAUP-730804-2016 | UW-485621-2016 | 12/29/2016 2:38:35 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | The vent limiters were not installed horizontally, if regulator fails it will allow a excessive amount of gas to escape into a occupied space. | 2 | Not installed according to certified installation instructions | Regulators_.png | file://x:/photopub/docs/0000000536/a804e0db-c3f0-420b-93c2-6df6908d1f9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bb09e2c_a7f7_4bb9_8435_71aecc68eec6
GAHE-742765-2017 | HE-493207-2017 | 1/23/2017 8:50:10 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | #Combustible_material.png Tank surrounded by combustible material. | 2 | Installation clearances or set backs to propane containers not met | Combustible_material.png | file://x:/photopub/docs/0000000546/ee24a027-9127-47cf-b296-3857a4effe25.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07c7e2e7_ddaf_4aab_8fe5_40704cf9efb5
GAHE-742633-2017 | HE-493118-2017 | 1/23/2017 8:11:13 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | #Propane_tank.png Propane tank installed two feet from a building wall. | 2 | Installation clearances or set backs to propane containers not met | Propane_tank.png | file://x:/photopub/docs/0000000546/20a0dc3a-6f8c-494f-a543-f6cb50d0784d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__66cb7d79_2ac4_4d54_b3d0_cc505d8f6186
ELIN-730713-2016 | EL-483588-2016 | 1/3/2017 10:34:25 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 3 | During a service connection inspection, the service panel was found to be located in an old fridge sitting on the ground near where a new house is to be built. The fridge was not secured and easily moved/tipped. The last portion of underground service cable was left laying unprotected on the ground and was under several inches of snow. Both the service panel and the service cable were vulnerable to physical damage which could present a shock hazard to workers in the vicinity. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_on_ground_under_snow_not_protected.png | file://x:/photopub/docs/0000000537/e7224e65-c70b-4843-afeb-975aa15ac34d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11ac9e58_f04f_4678_9f9b_c964f6761116
ELIN-730713-2016 | EL-483588-2016 | 1/3/2017 10:34:25 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 3 | During a service connection inspection, the service panel was found to be located in an old fridge sitting on the ground near where a new house is to be built. The fridge was not secured and easily moved/tipped. The last portion of underground service cable was left laying unprotected on the ground and was under several inches of snow. Both the service panel and the service cable were vulnerable to physical damage which could present a shock hazard to workers in the vicinity. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Fridge_as_service_shed_.png | file://x:/photopub/docs/0000000537/9ce9bb0e-1077-43c4-9f14-0cdc94526923.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11ac9e58_f04f_4678_9f9b_c964f6761116
ELIN-730713-2016 | EL-483588-2016 | 1/3/2017 10:34:25 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 3 | During a service connection inspection, the service panel was found to be located in an old fridge sitting on the ground near where a new house is to be built. The fridge was not secured and easily moved/tipped. The last portion of underground service cable was left laying unprotected on the ground and was under several inches of snow. Both the service panel and the service cable were vulnerable to physical damage which could present a shock hazard to workers in the vicinity. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Fridge_service_shed.png | file://x:/photopub/docs/0000000537/31a88aca-1911-44fd-8a03-395e35086f23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11ac9e58_f04f_4678_9f9b_c964f6761116
ELIN-759999-2017 | UW-502787-2017 | 2/20/2017 10:28:32 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | #Storage1.png,Storage2.png,Storage3.png,Storage4.png,Storage5.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Storage4.png | file://x:/photopub/docs/0000000560/f96e0de7-97f7-41e7-b3fa-91a8c7076c1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5cdc3aea_61d9_4094_9bce_720ca140a9d8
ELIN-759999-2017 | UW-502787-2017 | 2/20/2017 10:28:32 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | #Storage1.png,Storage2.png,Storage3.png,Storage4.png,Storage5.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Storage2.png | file://x:/photopub/docs/0000000560/6f642a90-3051-492d-9ee0-42a4c256abbd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5cdc3aea_61d9_4094_9bce_720ca140a9d8
ELIN-759999-2017 | UW-502787-2017 | 2/20/2017 10:28:32 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | #Storage1.png,Storage2.png,Storage3.png,Storage4.png,Storage5.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Storage3.png | file://x:/photopub/docs/0000000560/99e14d20-b627-47ca-bd78-972c87c8ec07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5cdc3aea_61d9_4094_9bce_720ca140a9d8
ELIN-759999-2017 | UW-502787-2017 | 2/20/2017 10:28:32 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | #Storage1.png,Storage2.png,Storage3.png,Storage4.png,Storage5.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Storage5.png | file://x:/photopub/docs/0000000560/396c0241-52cd-48da-b4d1-95dc44000904.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5cdc3aea_61d9_4094_9bce_720ca140a9d8
ELIN-759999-2017 | UW-502787-2017 | 2/20/2017 10:28:32 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | #Storage1.png,Storage2.png,Storage3.png,Storage4.png,Storage5.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Storage1.png | file://x:/photopub/docs/0000000560/f2628a43-a37d-471a-a165-bff87355d6a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5cdc3aea_61d9_4094_9bce_720ca140a9d8
GAHE-755281-2017 | HE-500256-2017 | 2/10/2017 11:57:26 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA052 | Unprotected temporary hose installations | 3 | 3 | #Temp_hose2.png The as found hazard was a temporary propane installation where the gas hose was inadequately protected from physical damage. This is a hazard because, if any of the gas hose were to be damaged it could lead to a release of propane gas within the building. | 3 | Unprotected temporary hose installations | Temp_hose2.png | file://x:/photopub/docs/0000000556/41897e0e-0627-4545-971e-12335fad5172.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be8ea707_a5f1_40a9_856a_4edc1d12d016
GAIN-731072-2016 | GA-485394-2016 | 1/3/2017 11:25:56 AM | ASSESS: GA: Final | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Angela_chip_wagon.png | file://x:/photopub/docs/0000000538/3195885f-6fa7-4e5c-8ee2-5d166bb5203f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f49b1fd_76b2_4126_afa6_8235841c7362
ELIN-715764-2016 | EL-465655-2016 | 12/12/2016 3:39:41 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Oversized sub feed breaker installed could allow more current to flow than the cable is rated for. This could lead to overheating of the cable and a potential fire hazard. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 60_amp_sub_feed_breaker.png | file://x:/photopub/docs/0000000529/9f500b8f-2997-42d6-baa4-77f2bfff5f06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a0f600c_85fb_4c1e_85c3_7e6f7b6cbfef
ELIN-715764-2016 | EL-465655-2016 | 12/12/2016 3:39:41 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Oversized sub feed breaker installed could allow more current to flow than the cable is rated for. This could lead to overheating of the cable and a potential fire hazard. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | AWG_8_sub_feed_cable.png | file://x:/photopub/docs/0000000529/d4a3fdd0-2267-425e-b0d4-ef75412c57d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a0f600c_85fb_4c1e_85c3_7e6f7b6cbfef
EDIN-752523-2017 | ED-473408-2016 | 2/10/2017 2:10:29 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | #Roof_access_to_room.png A well defined, protected and lit walking path leading from the roof stairwell exit to the room containing the elevator Main Disconnect and Transformers is required. During a section 5.10 (construction use) acceptance assessment it was found that a proper pathway was not provided. This is a roof fall hazard condition for an elevator service person accessing this room containing elevator equipment. It was found the general contractor failed to recognize the need for this pathway for the newly constructed 8 stop MRL Traction elevator located in a residential building. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Roof_access_to_room.png | file://x:/photopub/docs/0000000554/fb134d33-5213-459a-b3fb-4cb17d4ee3ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c57a8924_ad75_4a4b_84ae_8d6d92beaffc
ELOP-748301-2017 | 6134 | 2/21/2017 11:50:51 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL276 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | 2 | 2 | #Fa_and_em1.png,Fa_and_em2.png,Testing_older.png Fire Alarm Panel and Emergency lighting unit without evidence of recent periodic testing. Without proper lighting and fire alarm in the case of an emergency or power outage safe egress from the facility may be limited. | 2 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | Testing_older.png | file://x:/photopub/docs/0000000560/bac47fe5-cc86-468f-9d4d-5c9d1fb522b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__297e4431_6f19_4e81_b4f3_110ff0eb93b1
ELOP-748301-2017 | 6134 | 2/21/2017 11:50:51 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL276 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | 2 | 2 | #Fa_and_em1.png,Fa_and_em2.png,Testing_older.png Fire Alarm Panel and Emergency lighting unit without evidence of recent periodic testing. Without proper lighting and fire alarm in the case of an emergency or power outage safe egress from the facility may be limited. | 2 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | Fa_and_em1.png | file://x:/photopub/docs/0000000560/d8addbb9-3811-474d-a85c-211817052ec7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__297e4431_6f19_4e81_b4f3_110ff0eb93b1
ELOP-748301-2017 | 6134 | 2/21/2017 11:50:51 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL276 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | 2 | 2 | #Fa_and_em1.png,Fa_and_em2.png,Testing_older.png Fire Alarm Panel and Emergency lighting unit without evidence of recent periodic testing. Without proper lighting and fire alarm in the case of an emergency or power outage safe egress from the facility may be limited. | 2 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | Fa_and_em2.png | file://x:/photopub/docs/0000000560/c86ee031-7648-435b-b9cf-bb2a2fa9de41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__297e4431_6f19_4e81_b4f3_110ff0eb93b1
ELOP-748300-2017 | 6140 | 2/21/2017 2:28:48 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL276 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | 2 | 2 | #Fire_alarm2.png Fire alarm panel without evidence of periodic testing. Without a working fire alarm system in the case of an emergency or power outage safe egress from the facility may be limited. | 2 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | Fire_alarm2.png | file://x:/photopub/docs/0000000560/502cd5d9-4035-4db9-9287-c0be0022a942.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64cf1ef9_258f_4f04_a980_872c9e97c348
BPVOP-715791-2016 | 2289539 | 12/8/2016 9:36:12 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided on this hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_.png | file://x:/photopub/docs/0000000529/eadc35d1-9a6e-4957-a140-a1fa58e49456.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a20e348f_6ae7_4df8_863c_6fb3339661d8
BPVOP-715226-2016 | 2294296 | 12/9/2016 10:47:09 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided for this hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_4.png | file://x:/photopub/docs/0000000529/b5f4e92a-11e9-4d55-86e4-85e59e5bcd47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24ae9cc8_62fd_4d62_a3c7_14761b5c0fe2
ELOP-707853-2016 | EL-392294-2016 | 12/8/2016 11:50:13 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 4 | Combustible materials located on transformer. This is a fire hazard as transformers are sources of heat and minimum clearance must be maintained. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | B.png | file://x:/photopub/docs/0000000528/b8538e6f-72e7-4381-b73c-0e33b224c137.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a374ae2_0819_42cc_aef5_47984c425d3d
ELOP-707853-2016 | EL-392294-2016 | 12/8/2016 11:50:13 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 4 | Combustible materials located on transformer. This is a fire hazard as transformers are sources of heat and minimum clearance must be maintained. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | C.png | file://x:/photopub/docs/0000000528/d99ab350-2ba1-4691-8906-f223ff42dde3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a374ae2_0819_42cc_aef5_47984c425d3d
ELOP-707862-2016 | EL-150082-2014 | 12/8/2016 3:14:40 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 3 | Transformer located within 300 mm of plywood wall (combustible materials). | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | G.png | file://x:/photopub/docs/0000000528/858dd435-6279-443a-a781-a9425bc6f86a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65421b7e_c383_4ff3_ac9d_9819d5059fb2
ELOP-707853-2016 | EL-392294-2016 | 12/8/2016 11:50:13 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 4 | Combustible materials located on transformer. This is a fire hazard as transformers are sources of heat and minimum clearance must be maintained. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | A.png | file://x:/photopub/docs/0000000528/28ec0287-5697-43e6-af3f-cfc809c02356.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a374ae2_0819_42cc_aef5_47984c425d3d
ELIN-739327-2017 | EL-480805-2016 | 1/18/2017 1:24:00 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #7.png Boxes not properly bonded. | 3 | Continuity Bonding; method for equipment is not adequate. | 7.png | file://x:/photopub/docs/0000000545/e3cb81d4-8daa-4f92-8a2a-f8baeee162b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b61e4583_0438_4973_a21a_6b0375e331b0
ELIN-756312-2017 | EL-499293-2017 | 2/21/2017 3:22:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL109 | Conductors Identified conductor or neutral conductor has not been properly identified | 1 | 1 | #Neutral_not_identified.png | 1 | Conductors Identified conductor or neutral conductor has not been properly identified | Neutral_not_identified.png | file://x:/photopub/docs/0000000560/5eda1f29-17b5-4bd4-9b77-c70379779b19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e72d0da2_5d3d_4a32_bc54_6ee775698c79
ELIN-756819-2017 | EL-470485-2016 | 2/16/2017 8:47:01 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Shock_hazard1.png,Shock_hazard2.png This assessment found an outdoor receptacle without the required cover. A shock hazard is present as well as a fire hazard if the device becomes wet. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Shock_hazard2.png | file://x:/photopub/docs/0000000558/fb11cc8e-114a-44c5-9866-0fe217fe696d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74d8ce18_9a2f_46fa_aa70_2154fd5fcd7e
ELIN-756819-2017 | EL-470485-2016 | 2/16/2017 8:47:01 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Shock_hazard1.png,Shock_hazard2.png This assessment found an outdoor receptacle without the required cover. A shock hazard is present as well as a fire hazard if the device becomes wet. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Shock_hazard1.png | file://x:/photopub/docs/0000000558/1fbd2f7f-0cef-449d-b3f9-82c7290f7199.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74d8ce18_9a2f_46fa_aa70_2154fd5fcd7e
BPVOP-715227-2016 | 2294297 | 12/9/2016 10:34:53 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided for this hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_1.png | file://x:/photopub/docs/0000000529/4a64698b-c5d5-420f-9cf5-b809230d746f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b874d4d0_5400_4a79_a8c0_fb081ed6e557
ELIN-731752-2017 | EL-452948-2016 | 1/26/2017 1:53:29 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Exposed_main_breaker1.png,Exposed_main_breaker2.png The NON- ENERGIZED SERVICE main combination meter/ breaker unit does not have the protective coverplate installed exposing the main breaker to the elements. This can cause improper operation of the main breaker and is an equipment damage issue. | 0 | No Created Hazard Identified | Exposed_main_breaker2.png | file://x:/photopub/docs/0000000549/bf910fbe-8bf0-4100-9aaf-6218a10fddcf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa8e49c3_dcea_46f1_9275_329418303cd3
ELIN-731752-2017 | EL-452948-2016 | 1/26/2017 1:53:29 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Exposed_main_breaker1.png,Exposed_main_breaker2.png The NON- ENERGIZED SERVICE main combination meter/ breaker unit does not have the protective coverplate installed exposing the main breaker to the elements. This can cause improper operation of the main breaker and is an equipment damage issue. | 0 | No Created Hazard Identified | Exposed_main_breaker1.png | file://x:/photopub/docs/0000000549/537cba8b-fd3e-49f3-a23d-607f84c0cc36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa8e49c3_dcea_46f1_9275_329418303cd3
GAIN-757066-2017 | GA-489343-2017 | 2/23/2017 8:41:22 AM | ASSESS: GA: Rough-In | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 3 | #Regulator.png,Range_piping.png The as-found-condition is that a gas range is installed without the correct pressure regulator. The delivery pressure to the gas range exceeded the maximum pressure allowed for the appliance. The potential hazard is that the appliance will malfunction, resulting in hazardous operation and potential fire damage to the surrounding cabinetry. | 4 | Appliance regulator not installed, incorrect delivery pressure | Range_piping.png | file://x:/photopub/docs/0000000562/ec0fa4ba-2558-4ac8-a67e-a54504c0bdde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__293222f1_9d09_4684_9189_d0686151b742
GAIN-757066-2017 | GA-489343-2017 | 2/23/2017 8:41:22 AM | ASSESS: GA: Rough-In | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 3 | #Regulator.png,Range_piping.png The as-found-condition is that a gas range is installed without the correct pressure regulator. The delivery pressure to the gas range exceeded the maximum pressure allowed for the appliance. The potential hazard is that the appliance will malfunction, resulting in hazardous operation and potential fire damage to the surrounding cabinetry. | 4 | Appliance regulator not installed, incorrect delivery pressure | Regulator.png | file://x:/photopub/docs/0000000562/335817e5-2795-4d58-b1ca-b923658e6bab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__293222f1_9d09_4684_9189_d0686151b742
ELIN-739370-2017 | EL-464295-2016 | 1/18/2017 8:48:05 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #13.png Conductors in trusses over 1m not protected. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 13.png | file://x:/photopub/docs/0000000545/b7b05e28-ca1b-4b35-b881-350505cc865f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__423f59cc_4e77_44fb_81cc_83817f9e8a7f
ELOP-723481-2016 | EL-234450-2015 | 1/18/2017 7:32:35 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | #No_access_to_electrical_equipment.png Various electrical equipment within the production area is not provided with working space around equipment or used as storage. This hinders system operation. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | No_access_to_electrical_equipment.png | file://x:/photopub/docs/0000000545/658d57f0-66a2-4912-b8fc-2a04bba920dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__77e6a8f7_2984_485b_9554_697c2b1cf8d9
GAIN-696188-2016 | GA-252467-2015 | 1/3/2017 2:48:20 PM | ASSESS: GA: Rough-In | png | #asFound | GA141 | Missing make up air exhaust interlocks | 3 | 3 | As found hazard is that there is no interlock on the exhaust fan serving a forge. If the exhaust fan fails, products of combustion from the forge will enter the occupied space,posing a risk to human health | 3 | Missing make up air exhaust interlocks | Forge_with_exhausthood.png | file://x:/photopub/docs/0000000538/884ebf71-6702-4a85-8a17-374c98155aea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf805f02_ea81_4bd0_b8d8_8443a7766cf5
GAIN-735399-2017 | GA-484195-2016 | 1/16/2017 1:37:38 PM | ASSESS: GA: Rough-In | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Open_gasline_at_meter.png All gas outlets must be capped when not connected to an appliance. If gas valve was accidentally opened, fire or explosion could result | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Open_gasline_at_meter.png | file://x:/photopub/docs/0000000544/8f74471f-4b08-47ef-a907-242e6a039b20.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b43c9236_dcd8_4ce3_a2fb_4df4b76714f6
ELIN-754286-2017 | EL-459780-2016 | 2/8/2017 11:21:37 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Splitter_.png In a new staff housing facility, a 15amp 120volt single outlet on top of range was found with a power splitter and 3 appliances being used. This can lead to a "Thermal Effect" hazard. Pic attached | 4 | Conductors, Misuse of flexible cords. | Splitter_.png | file://x:/photopub/docs/0000000556/b34108f8-9e45-48f9-b516-6b7f67cae3f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae1b12da_ad3e_4b38_8f45_bc51d67bf478
ELIN-757253-2017 | EL-486612-2017 | 2/16/2017 4:19:09 PM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #H1.png,H2.png,H3.png,H4.png,H5.png Cable for electric range was damaged by improper termination. Several of the copper strands were cut/broken. During inspection it was found that there were only three strands remaining between the two conductors terminated at the breaker. This would have caused a fire. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | H3.png | file://x:/photopub/docs/0000000558/d12eed46-0c34-4f3c-86d8-c8f67e315a38.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f98b26f_d4c4_4d24_8e21_c4ba277af568
ELIN-757253-2017 | EL-486612-2017 | 2/16/2017 4:19:09 PM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #H1.png,H2.png,H3.png,H4.png,H5.png Cable for electric range was damaged by improper termination. Several of the copper strands were cut/broken. During inspection it was found that there were only three strands remaining between the two conductors terminated at the breaker. This would have caused a fire. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | H1.png | file://x:/photopub/docs/0000000558/a16d910b-834a-4241-8bdd-f5a33252a56f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f98b26f_d4c4_4d24_8e21_c4ba277af568
ELIN-757253-2017 | EL-486612-2017 | 2/16/2017 4:19:09 PM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #H1.png,H2.png,H3.png,H4.png,H5.png Cable for electric range was damaged by improper termination. Several of the copper strands were cut/broken. During inspection it was found that there were only three strands remaining between the two conductors terminated at the breaker. This would have caused a fire. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | H5.png | file://x:/photopub/docs/0000000558/6dae30ad-8d53-4101-ae39-e0f60e7ffc7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f98b26f_d4c4_4d24_8e21_c4ba277af568
ELIN-747294-2017 | EL-423263-2016 | 2/16/2017 7:53:34 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | #Neutral_ground.png The main ground terminates to the metal can instead of the system Neutral. Potential shock hazard exists when incorrectly installed. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Neutral_ground.png | file://x:/photopub/docs/0000000558/793126db-0b0e-4952-9955-e381f43de2d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__018ac950_36be_4a94_83b7_3730b826be31
ELIN-756332-2017 | EL-471606-2016 | 2/16/2017 10:53:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL288 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Panel_not_protected_.png This assessment found that the Panel is not protected sufficiently from weather, if it gets wet a shock hazard exists | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Panel_not_protected_.png | file://x:/photopub/docs/0000000558/42d40430-9c93-4cd7-b628-09fa1ced7baf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08d053e9_5f1f_418e_857b_b0ce22c32f73
BPVIN-742078-2017 | UW-433445-2016 | 1/26/2017 11:51:00 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP123 | 3.1.1 Safeties will not function - Pressure Relief Device Safety relief valve removed or bypassed | 5 | 5 | #Prd_outlet.png All pressure retaining equipment shall have pressure relief device in order to protect the equipment from overpressure and damage. I found a pressure relief device on this hot water heater located after a shutoff valve. A potential exists for an overpressure incident or rupture. | 5 | 3.1.1 Safeties will not function - Pressure Relief Device Safety relief valve removed or bypassed | Prd_outlet.png | file://x:/photopub/docs/0000000549/a72ea10c-b759-4677-86ad-aaf60220e4b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e545d513_b8be_47a9_9c19_7da97da10a24
ELHE-759971-2017 | HE-502769-2017 | 2/20/2017 10:41:08 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cables and electrical equipment that are approved for dry locations use only, has become wet and is not approved for the use and has lost its insulation integrity and is not authorized for connection or use. | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors1.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors2.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors3.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors4.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors5.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors6.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors7.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors8.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors9.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors10.png,Dry_location_type_elec | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors12.png | file://x:/photopub/docs/0000000560/e2bd5a84-1bed-4b98-9fb4-0eed6f094610.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33e33e58_a028_4b39_8220_81b3eac993b9
GAIN-740031-2017 | GA-491397-2017 | 1/27/2017 10:40:28 AM | ASSESS: GA: Final | png | #asFound | GA070 | Undersized hose or appliance connector | 3 | 3 | #unit_heater.png Insufficient flow through connector can cause appliance to under fire which could eventually lead to sooting and possible CO. | 3 | Undersized hose or appliance connector | unit_heater.png | file://x:/photopub/docs/0000000549/82f5f037-0c3b-4404-ae6f-0ece384ac680.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75d875f1_db40_443a_b97b_9b0551dba0c2
ELIN-736800-2017 | EL-450016-2016 | 1/11/2017 2:14:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Rigid_PVC_insulated_wall.png Rigid PVC is installed in a wall that will be thermally insulated and lacks protection from penetration by siding fasteners. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Rigid_PVC_insulated_wall.png | file://x:/photopub/docs/0000000541/fff1fdfe-acfb-4202-82c5-058dc9abf18c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba24915a_6cd5_40d8_befe_add1e6dcd558
ELIN-757253-2017 | EL-486612-2017 | 2/16/2017 4:19:09 PM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #H1.png,H2.png,H3.png,H4.png,H5.png Cable for electric range was damaged by improper termination. Several of the copper strands were cut/broken. During inspection it was found that there were only three strands remaining between the two conductors terminated at the breaker. This would have caused a fire. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | H2.png | file://x:/photopub/docs/0000000558/fd291d2f-336f-4568-b6d1-945ef103beb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f98b26f_d4c4_4d24_8e21_c4ba277af568
ELIN-757253-2017 | EL-486612-2017 | 2/16/2017 4:19:09 PM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #H1.png,H2.png,H3.png,H4.png,H5.png Cable for electric range was damaged by improper termination. Several of the copper strands were cut/broken. During inspection it was found that there were only three strands remaining between the two conductors terminated at the breaker. This would have caused a fire. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | H4.png | file://x:/photopub/docs/0000000558/96dac786-7fef-43c2-803e-7e84826c90ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f98b26f_d4c4_4d24_8e21_c4ba277af568
GAHE-754274-2017 | HE-486233-2017 | 2/24/2017 9:53:43 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA163 | Use of appliance/accessories that creates a immediate hazard (Risk Registry Item GA-04) | 5 | 5 | #Unapproved_appliance.png An unapproved burner installed to a gas line is left burning unattended. Appliance is not a certified appliance, left in an unsafe manner. Appliance could fall over, cause a gas leak or explosion. Burner is not approved for this type of use without safeties installed for flame rectification | 5 | Use of appliance/accessories that creates a immediate hazard (Risk Registry Item GA-04) | Unapproved_appliance.png | file://x:/photopub/docs/0000000562/e7911184-704a-4903-bb81-e84af5fabf69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f473546a_ff9f_458c_88ed_54e0ba800bf3
ELIN-723421-2016 | EL-449696-2016 | 12/14/2016 9:16:33 AM | ASSESS: EL: Service Connection | png | #asFound | EL191 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | 3 | 3 | Panel cover has been left off. This is a possible shock hazard. | 3 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | Panel_cover_left_off.png | file://x:/photopub/docs/0000000531/da2b379f-4119-4231-a5eb-dd32df5c7267.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce8c07af_9035_4eb0_b0a9_468470601262
ELIN-723421-2016 | EL-449696-2016 | 12/14/2016 9:16:33 AM | ASSESS: EL: Service Connection | png | #asFound | EL191 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | 3 | 3 | Panel cover has been left off. This is a possible shock hazard. | 3 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, not within area of energized parts. | Fan.png | file://x:/photopub/docs/0000000531/08d26943-7f76-47c1-94de-310078964bf8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce8c07af_9035_4eb0_b0a9_468470601262
GAHE-747943-2017 | HE-496160-2017 | 2/16/2017 9:04:10 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound No hydrostatic relief installed between pump and manual valve. | GA089 | No hydrostatic relief in liquid propane system where required | 5 | 5 | #No_hydrostatic_relief.png When dispensing liquid propane from a tank into a piping system there must by a way to relieve pressure if liquid propane could be trapped due to expansion, Hydrostatic relief valves are installed to prevent overpressuring, If a overpressure situation happens there could be premature failure of fittings and pipe releasing propane gas into the atmosphere. | 5 | No hydrostatic relief in liquid propane system where required | No_hydrostatic_relief.png | file://x:/photopub/docs/0000000558/0cc62d13-b099-48b7-96cf-7693181ba6d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2823ad76_10fd_45a8_bc70_f9be6063fe59
ELHE-722393-2016 | HE-479948-2016 | 12/13/2016 10:54:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Electrical enclosure not properly bonded. This is a shock hazard as protection devices will not operate properly. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | A.png | file://x:/photopub/docs/0000000531/d52bb28e-fd33-410d-9f4f-9dbc3e58bc57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a46d61b0_9477_49bc_a125_2fd3272da0fe
ELHE-722393-2016 | HE-479948-2016 | 12/13/2016 10:54:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Electrical enclosure not properly bonded. This is a shock hazard as protection devices will not operate properly. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | C.png | file://x:/photopub/docs/0000000531/3d7a5019-85ce-4e68-8396-bbfb2afb5f41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a46d61b0_9477_49bc_a125_2fd3272da0fe
ELHE-722393-2016 | HE-479948-2016 | 12/13/2016 10:54:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Electrical enclosure not properly bonded. This is a shock hazard as protection devices will not operate properly. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | E.png | file://x:/photopub/docs/0000000531/dc6a7710-e9ff-4b22-b026-7fbdc2a7cecd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a46d61b0_9477_49bc_a125_2fd3272da0fe
ELHE-722393-2016 | HE-479948-2016 | 12/13/2016 10:54:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Electrical enclosure not properly bonded. This is a shock hazard as protection devices will not operate properly. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | F.png | file://x:/photopub/docs/0000000531/e061183f-374e-450f-8cf3-48f1015c9dab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a46d61b0_9477_49bc_a125_2fd3272da0fe
ELHE-722393-2016 | HE-479948-2016 | 12/13/2016 10:54:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Electrical enclosure not properly bonded. This is a shock hazard as protection devices will not operate properly. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | G.png | file://x:/photopub/docs/0000000531/7c99613c-0afe-4cd5-8824-9041a5199836.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a46d61b0_9477_49bc_a125_2fd3272da0fe
ELHE-722393-2016 | HE-479948-2016 | 12/13/2016 10:54:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Electrical enclosure not properly bonded. This is a shock hazard as protection devices will not operate properly. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | B.png | file://x:/photopub/docs/0000000531/b0c189ea-d2f6-4fc0-b51f-a7089c435850.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a46d61b0_9477_49bc_a125_2fd3272da0fe
ELHE-722393-2016 | HE-479948-2016 | 12/13/2016 10:54:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Electrical enclosure not properly bonded. This is a shock hazard as protection devices will not operate properly. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | I.png | file://x:/photopub/docs/0000000531/8c9aa91d-791c-4344-932f-a8b74b0f1519.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a46d61b0_9477_49bc_a125_2fd3272da0fe
ELHE-722393-2016 | HE-479948-2016 | 12/13/2016 10:54:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Electrical enclosure not properly bonded. This is a shock hazard as protection devices will not operate properly. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | H.png | file://x:/photopub/docs/0000000531/0ad08777-abb6-49ac-9875-a19b0014c9ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a46d61b0_9477_49bc_a125_2fd3272da0fe
ELHE-722393-2016 | HE-479948-2016 | 12/13/2016 10:54:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Electrical enclosure not properly bonded. This is a shock hazard as protection devices will not operate properly. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | J.png | file://x:/photopub/docs/0000000531/c8635084-168c-4c38-9994-d3c90dba65d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a46d61b0_9477_49bc_a125_2fd3272da0fe
ELHE-722393-2016 | HE-479948-2016 | 12/13/2016 10:54:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Electrical enclosure not properly bonded. This is a shock hazard as protection devices will not operate properly. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | D.png | file://x:/photopub/docs/0000000531/08e305e8-d01b-4db9-ae7c-0ea77d57b84d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a46d61b0_9477_49bc_a125_2fd3272da0fe
GAIN-742692-2017 | GA-472766-2016 | 1/27/2017 9:38:45 AM | ASSESS: GA: Final | JPG | #asFound Regulator relief clearance not maintained. | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #image1.JPG,image2.JPG While assessing an commercial installation permit I found four regulator relief vents terminated too close to mechanical air intakes of their adjacent units. Should the regulators relieve while the units are drawing in fresh air raw gas would be drawn into the occupied space. This would cause the potential for a fire, or explosion. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | image1.JPG | file://x:/photopub/docs/0000000549/5a3986aa-11b1-4f4e-8a8d-448d5de4eb79.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06324411_2182_4c3b_b20b_390bfbc81a1a
GAIN-742692-2017 | GA-472766-2016 | 1/27/2017 9:38:45 AM | ASSESS: GA: Final | JPG | #asFound Regulator relief clearance not maintained. | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #image1.JPG,image2.JPG While assessing an commercial installation permit I found four regulator relief vents terminated too close to mechanical air intakes of their adjacent units. Should the regulators relieve while the units are drawing in fresh air raw gas would be drawn into the occupied space. This would cause the potential for a fire, or explosion. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | image2.JPG | file://x:/photopub/docs/0000000549/d33dc686-86d6-43cc-8856-48e9bd8aa9c2.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06324411_2182_4c3b_b20b_390bfbc81a1a
ELHE-759971-2017 | HE-502769-2017 | 2/20/2017 10:41:08 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cables and electrical equipment that are approved for dry locations use only, has become wet and is not approved for the use and has lost its insulation integrity and is not authorized for connection or use. | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors1.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors2.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors3.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors4.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors5.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors6.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors7.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors8.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors9.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors10.png,Dry_location_type_elec | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors2.png | file://x:/photopub/docs/0000000560/7b419b0c-0869-45a0-9c1d-39854d1beb71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33e33e58_a028_4b39_8220_81b3eac993b9
ELHE-759971-2017 | HE-502769-2017 | 2/20/2017 10:41:08 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cables and electrical equipment that are approved for dry locations use only, has become wet and is not approved for the use and has lost its insulation integrity and is not authorized for connection or use. | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors1.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors2.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors3.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors4.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors5.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors6.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors7.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors8.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors9.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors10.png,Dry_location_type_elec | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors10.png | file://x:/photopub/docs/0000000560/16caac35-a4ec-42a1-b571-a64c1e2108f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33e33e58_a028_4b39_8220_81b3eac993b9
ELHE-759971-2017 | HE-502769-2017 | 2/20/2017 10:41:08 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cables and electrical equipment that are approved for dry locations use only, has become wet and is not approved for the use and has lost its insulation integrity and is not authorized for connection or use. | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors1.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors2.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors3.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors4.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors5.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors6.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors7.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors8.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors9.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors10.png,Dry_location_type_elec | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors7.png | file://x:/photopub/docs/0000000560/ecba99ff-93a1-4b37-b97a-8778f7648073.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33e33e58_a028_4b39_8220_81b3eac993b9
ELIN-754568-2017 | EL-499282-2017 | 2/17/2017 1:42:43 PM | ASSESS: EL: Final | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 3 | #Service_equipment_mounted_to_rotten_post_and_plywood1.png,Service_equipment_mounted_to_rotten_post_and_plywood2.png,Service_equipment_mounted_to_rotten_post_and_plywood3.png,Service_equipment_mounted_to_rotten_post_and_plywood4.png,Service_equipment_mounted_to_rotten_post_and_plywood5.png,Service_equipment_mounted_to_rotten_post_and_plywood6.png,Service_equipment_mounted_to_rotten_post_and_plywood7.png Over head service conductors and service equipment such as conduits, cables, meter base, panels, and switches are required to be mounted to approved, treated poles that are installed in compliance with the code. This is to ensure the equipment is properly supported and will remain so for an extended period of time. This existing installation for an over head 60A 120/240V service to a mobile home on a residential property has over head service supply conductors and service equipment supported by and mounted to an 8" x 8" post planted in the ground. The post is rotten at the bottom and the plywood and 2" x 4" su | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Service_equipment_mounted_to_rotten_post_and_plywood3.png | file://x:/photopub/docs/0000000559/d0814a64-8bc4-4717-bc10-2799a24cc868.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a649c7ec_2d8c_41bd_94f8_e9ef7a957cff
BPVOP-757959-2017 | 3490982 | 2/16/2017 7:09:22 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | #HP110241_blow-down_line.png Pressure and temperature ratings of some components within the blow-off piping is below that required by the National Board Inspection Code. Failure of a component during blow-down of the boiler could subject personnel to injury or death by impact from flying debris and/or scalding from steam and hot water. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | HP110241_blow-down_line.png | file://x:/photopub/docs/0000000558/1eba0350-17c9-4f2d-aad3-0b579aa046da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3650fbf_7f3a_40b9_8108_1e4b14fca76b
ELHE-759971-2017 | HE-502769-2017 | 2/20/2017 10:41:08 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cables and electrical equipment that are approved for dry locations use only, has become wet and is not approved for the use and has lost its insulation integrity and is not authorized for connection or use. | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors1.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors2.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors3.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors4.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors5.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors6.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors7.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors8.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors9.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors10.png,Dry_location_type_elec | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors3.png | file://x:/photopub/docs/0000000560/045659c1-9d62-4b5c-ad15-63116cb73583.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33e33e58_a028_4b39_8220_81b3eac993b9
ELHE-759971-2017 | HE-502769-2017 | 2/20/2017 10:41:08 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cables and electrical equipment that are approved for dry locations use only, has become wet and is not approved for the use and has lost its insulation integrity and is not authorized for connection or use. | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors1.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors2.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors3.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors4.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors5.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors6.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors7.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors8.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors9.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors10.png,Dry_location_type_elec | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors4.png | file://x:/photopub/docs/0000000560/c67eccf7-56b3-48f7-95b2-6bb316798035.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33e33e58_a028_4b39_8220_81b3eac993b9
ELHE-759971-2017 | HE-502769-2017 | 2/20/2017 10:41:08 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cables and electrical equipment that are approved for dry locations use only, has become wet and is not approved for the use and has lost its insulation integrity and is not authorized for connection or use. | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors1.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors2.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors3.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors4.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors5.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors6.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors7.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors8.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors9.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors10.png,Dry_location_type_elec | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors1.png | file://x:/photopub/docs/0000000560/a414a852-6d35-47cf-9bf6-983756f043d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33e33e58_a028_4b39_8220_81b3eac993b9
ELHE-759971-2017 | HE-502769-2017 | 2/20/2017 10:41:08 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cables and electrical equipment that are approved for dry locations use only, has become wet and is not approved for the use and has lost its insulation integrity and is not authorized for connection or use. | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors1.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors2.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors3.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors4.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors5.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors6.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors7.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors8.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors9.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors10.png,Dry_location_type_elec | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors9.png | file://x:/photopub/docs/0000000560/a8ffb273-ff86-4041-9cf2-7c593213fdc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33e33e58_a028_4b39_8220_81b3eac993b9
ELHE-759971-2017 | HE-502769-2017 | 2/20/2017 10:41:08 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cables and electrical equipment that are approved for dry locations use only, has become wet and is not approved for the use and has lost its insulation integrity and is not authorized for connection or use. | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors1.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors2.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors3.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors4.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors5.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors6.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors7.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors8.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors9.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors10.png,Dry_location_type_elec | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors13.png | file://x:/photopub/docs/0000000560/6ee39543-f9e6-43d0-96bc-50bf521226eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33e33e58_a028_4b39_8220_81b3eac993b9
GAIN-722854-2016 | GA-474987-2016 | 12/15/2016 10:52:27 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | While assessing the installation of a direct fired make up air unit, I found a regulator relief located too close to the mechanical air intake for the unit. Should the unit be running and the regulator relieve, raw gas would be drawn into the unit. This could potentially cause the unit to over fire, creating a fire hazard. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Non_compliant_clearance.png | file://x:/photopub/docs/0000000532/0483d334-6a78-4375-8a2b-fc906bcb36f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__966e65d7_1409_47db_980f_5eef87f1fb8c
GAIN-722854-2016 | GA-474987-2016 | 12/15/2016 10:52:27 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | While assessing the installation of a direct fired make up air unit, I found a regulator relief located too close to the mechanical air intake for the unit. Should the unit be running and the regulator relieve, raw gas would be drawn into the unit. This could potentially cause the unit to over fire, creating a fire hazard. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Measurement.png | file://x:/photopub/docs/0000000532/7ffd1cb5-3955-4ad3-bb2c-f2399848f19d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__966e65d7_1409_47db_980f_5eef87f1fb8c
ELIN-739386-2017 | EL-489247-2017 | 1/20/2017 9:55:36 AM | ASSESS: EL: Final | png | #asFound | EL133 | Installation of electrical equipment General: improper polarity at receptacle. | 3 | 3 | #Furnace_Room_Receptacle.png A 15 amp 120 volt receptacle located in the furnace utility room when tested shows a reverse polarity connection. This poses potential harm the electrical equipment plugged into this receptacle and to the persons using the equipment. Without the proper polarity equipment is not properly protected, the overcurrent device protecting the receptacle may not function and persons may be shocked are harmed because the connections to the equipment will be reversed. | 3 | Installation of electrical equipment General: improper polarity at receptacle. | Furnace_Room_Receptacle.png | file://x:/photopub/docs/0000000546/a84cb73a-e36b-476a-a6cd-96a6be7eb6e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b2984e4a_6707_4ef3_b99d_178cdfbf52e8
ELIN-737091-2017 | EL-488475-2017 | 2/8/2017 8:04:06 AM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Condensation_on_low_ceiling_lighting1.png,Condensation_on_low_ceiling_lighting2.png In an existing grouped together modular staff housing facility, numerous 15amp 120volt light fixtures were found in the shower rooms with their lampshades removed or destroyed and with condensation dripping from an unapproved lighting unit. This is a shock hazard. Pic attached. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Condensation_on_low_ceiling_lighting1.png | file://x:/photopub/docs/0000000559/a3a01e29-977c-4b5a-abda-a2bf2a65ef5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b273654c_1ed1_459f_bc95_e2ff7dfdd564
ELIN-737091-2017 | EL-488475-2017 | 2/8/2017 8:04:06 AM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Condensation_on_low_ceiling_lighting1.png,Condensation_on_low_ceiling_lighting2.png In an existing grouped together modular staff housing facility, numerous 15amp 120volt light fixtures were found in the shower rooms with their lampshades removed or destroyed and with condensation dripping from an unapproved lighting unit. This is a shock hazard. Pic attached. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Condensation_on_low_ceiling_lighting2.png | file://x:/photopub/docs/0000000559/e494e2d0-6754-4357-a558-ee200779fcc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b273654c_1ed1_459f_bc95_e2ff7dfdd564
ELIN-722815-2016 | EL-369809-2016 | 12/14/2016 12:16:10 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Damaged and unproved cables may cause fire | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Damaged_cable2.png | file://x:/photopub/docs/0000000531/d47d5e5e-1c6c-4591-a0bb-01fcf3000096.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed66b3a6_c749_4580_bb7a_95cd1f7272f8
ELIN-722815-2016 | EL-369809-2016 | 12/14/2016 12:16:10 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Damaged and unproved cables may cause fire | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Damaged_cable1.png | file://x:/photopub/docs/0000000531/dc58c32e-2d2c-4834-9d54-e6db0c93a4f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed66b3a6_c749_4580_bb7a_95cd1f7272f8
ELIN-722815-2016 | EL-369809-2016 | 12/14/2016 12:16:10 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Damaged and unproved cables may cause fire | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Unprotected_cable.png | file://x:/photopub/docs/0000000531/461ece54-cfa9-4268-8427-93bb80ecd698.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed66b3a6_c749_4580_bb7a_95cd1f7272f8
ELIN-759410-2017 | EL-411828-2016 | 2/23/2017 10:18:49 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Kitchen_Island_Plug.png 15 amp 120 volt receptacles located within 1.5 meters of kitchen and laundry sinks have not been GFCI protected, this poses a shock hazard to persons using these receptacles and to electrical components plugged into them. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Kitchen_Island_Plug.png | file://x:/photopub/docs/0000000561/c04d7f71-339a-4d87-8d82-45df42fe0c83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fc678fd_fc08_494d_beed_555c2af70daa
ELHE-758366-2017 | HE-501875-2017 | 2/16/2017 3:45:53 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Receptacle that has been pulled out of device box | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Receptacle_pulled_out_of_device_box.png Receptacle has been pulled out of the device box. Exposed receptacle terminations as well as conductors. Contact with terminals or conductors would provide a risk of shock and fire to persons and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Receptacle_pulled_out_of_device_box.png | file://x:/photopub/docs/0000000558/45a7e33a-4c46-4c8a-8f86-fd4be847633e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f6e9b74_9d17_47f2_bc02_4d3da275e237
GAIN-753927-2017 | GA-498639-2017 | 2/17/2017 11:04:13 AM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | #Gas_connector_used_on_tube_heater.png Certified gas connector not approved for application. A gas connector used to connect a tube heater can be damaged by movement of the tube heater causing uncontrolled release of gas. | 2 | Certified appliance connector installed but not approved for application | Gas_connector_used_on_tube_heater.png | file://x:/photopub/docs/0000000559/6eb9c2b6-5a1e-4420-8ecf-c053ef230b59.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46929b96_f37d_4a61_9280_91545124c497
ELOP-655486-2016 | 1292 | 1/23/2017 4:08:13 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #Block_heater_cord1.png,Block_heater_cord2.png In an existing commercial space, a 20amp 120volt Block heater cord and outlet was found in an energized state with signs of wear and tear on the product. This can lead to an "Equipment Damage" hazard. Pic attached. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Block_heater_cord1.png | file://x:/photopub/docs/0000000551/52200439-aca5-4ec3-8648-c02de84755cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__A3463CC0_C2C2_45A9_87A3_A74016081048
ELOP-655486-2016 | 1292 | 1/23/2017 4:08:13 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #Block_heater_cord1.png,Block_heater_cord2.png In an existing commercial space, a 20amp 120volt Block heater cord and outlet was found in an energized state with signs of wear and tear on the product. This can lead to an "Equipment Damage" hazard. Pic attached. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Block_heater_cord2.png | file://x:/photopub/docs/0000000551/0c6b148b-ef8a-4669-96c5-7324e366caa6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__A3463CC0_C2C2_45A9_87A3_A74016081048
ELHE-759971-2017 | HE-502769-2017 | 2/20/2017 10:41:08 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cables and electrical equipment that are approved for dry locations use only, has become wet and is not approved for the use and has lost its insulation integrity and is not authorized for connection or use. | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors1.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors2.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors3.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors4.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors5.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors6.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors7.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors8.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors9.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors10.png,Dry_location_type_elec | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors8.png | file://x:/photopub/docs/0000000560/4ef1b855-51d5-461b-8974-01ebb60fcc89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33e33e58_a028_4b39_8220_81b3eac993b9
ELHE-759971-2017 | HE-502769-2017 | 2/20/2017 10:41:08 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cables and electrical equipment that are approved for dry locations use only, has become wet and is not approved for the use and has lost its insulation integrity and is not authorized for connection or use. | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors1.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors2.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors3.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors4.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors5.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors6.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors7.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors8.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors9.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors10.png,Dry_location_type_elec | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors11.png | file://x:/photopub/docs/0000000560/406828ed-7a75-494d-9c9a-1feb81cc8a8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33e33e58_a028_4b39_8220_81b3eac993b9
ELHE-758252-2017 | HE-501784-2017 | 2/21/2017 9:34:00 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Panel_Openings.png Openings in the cover of a 100 amp 240 volt panel and other similar electrical equipment, outlet boxes and switches have not been filled to protect from accidental contact by persons. This poses a shock hazard and risk of mechanical damage to the electrical equipment. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Panel_Openings.png | file://x:/photopub/docs/0000000561/8d4446c7-bcb2-4ff5-a185-aff66d05eab9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1fafd8e2_a893_4574_9ed8_0335886549af
ELIN-760706-2017 | EL-500618-2017 | 2/21/2017 12:18:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #Poorly_bonded_mast_pipe.png Electrical which is not bonded correctly could remain energized and become a shock hazard if accidentally energized by incorrectly installed equipment | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Poorly_bonded_mast_pipe.png | file://x:/photopub/docs/0000000561/0996c909-49ef-4e83-9554-dec540f46f2d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ab585ec_645e_4871_af23_27164ca7e370
ELIN-760492-2017 | EL-462647-2016 | 2/23/2017 10:54:59 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #All_white_service_conductors_.png Improperly identified conductors may result in cross connections which cause equipment damage or personal injury | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | All_white_service_conductors_.png | file://x:/photopub/docs/0000000562/5debe09a-b4ed-4bac-a719-42b72cee0051.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e55ac578_e274_42fc_8ec4_1d38661bf0cf
ELIN-760497-2017 | EL-498879-2017 | 2/23/2017 12:27:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | #Ground.png Bond This assessment found the grounding conductor connected to the meter can instead of the system neutral. When properly connected this conductor provides a path back to the source, reducing the shock hazard by creating an equipotential plane. It also allows the overcurrent device to operate as intended reducing the shock and fire hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground.png | file://x:/photopub/docs/0000000562/e5feb908-7a65-4637-896b-e23a00b1906b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d942a6b7_d528_41bd_ac48_f6b844235f5d
ELIN-722465-2016 | EL-466698-2016 | 12/20/2016 2:46:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | Bonding lug inadequately installed within meter base, which may lead to possible unbonded section of electrical installation. | 3 | Continuity Bonding; method for equipment is not adequate. | Bonding_Lug.png | file://x:/photopub/docs/0000000534/1cc469d0-34b7-426b-9329-68dad074c75f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ebbd2f4_7697_4a6e_a78e_34d5c3414bc1
ELIN-732634-2017 | EL-419143-2016 | 1/6/2017 9:03:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound The only bonding path provided to ground is for the metering compartment. | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Grounding_CT_Cabinet.png,Main_Switch.png A 480 volt 600 amp ungrounded main service has not been supplied with a bonding path to ground. This could result in a shock hazard to persons and failure of overcurrent devices to operate. No ground fault indicating lights present. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Grounding_CT_Cabinet.png | file://x:/photopub/docs/0000000540/22378bdc-9430-4d45-a740-4dce4491fd01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c2878d7_d5b6_4e44_bd0e_3d4a38ace748
ELIN-732634-2017 | EL-419143-2016 | 1/6/2017 9:03:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Grounding_CT_Cabinet.png,Main_Switch.png A 480 volt 600 amp ungrounded main service has not been supplied with a bonding path to ground. This could result in a shock hazard to persons and failure of overcurrent devices to operate. No ground fault indicating lights present. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Main_Switch.png | file://x:/photopub/docs/0000000540/e1f0049a-f859-4d31-85fa-7177467b5d59.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c2878d7_d5b6_4e44_bd0e_3d4a38ace748
ELHE-759971-2017 | HE-502769-2017 | 2/20/2017 10:41:08 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cables and electrical equipment that are approved for dry locations use only, has become wet and is not approved for the use and has lost its insulation integrity and is not authorized for connection or use. | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors1.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors2.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors3.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors4.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors5.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors6.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors7.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors8.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors9.png,Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors10.png,Dry_location_type_elec | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Dry_location_type_electrical_equipment_is_wet_and_damaged_an_not_approved_for_the_use_outdoors5.png | file://x:/photopub/docs/0000000560/676cdf19-0e69-4f5f-b026-ae773b168c8c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33e33e58_a028_4b39_8220_81b3eac993b9
BPVIN-746409-2017 | BPV-495398-2017 | 1/26/2017 1:04:22 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP142 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | 3 | 2 | #No_thermometer_for_hot_water_storage_tank.png Upon assessment of potable hot water storage tank (Length-1.6m, Diameter-0.65m) with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Working Temperature (MAWT) of 210*Fahrenheit, it is determined that there is no thermometer at or near the outlet of storage tank. There is no way to detect and take subsequent corrective action in the event of water temperature above operating range or even MAWT, caused by mal-function of controls , which may lead to incident. | 3 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | No_thermometer_for_hot_water_storage_tank.png | file://x:/photopub/docs/0000000549/ae86799e-beff-4a6d-a34d-2434efec2dde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__432df07a_06d0_4baf_98f9_b5f4396042a3
ELIN-736485-2017 | EL-446850-2016 | 1/11/2017 11:50:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Main_Ground.png The grounding conductor for the 200 amp 120/240 service has been terminated to a bonding lug instead of the neutral bar. This could result in the overcurrent devices failing to operate as designed, and a shock hazard for persons. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Main_Ground.png | file://x:/photopub/docs/0000000542/946b0ce9-ec57-42fa-a7d1-6f999ab79989.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__114480a2_8027_4c8d_af65_5ba89442d195
GAHE-753225-2017 | HE-499111-2017 | 2/8/2017 12:56:04 PM | ASSESS: GA HE: Hazard Elimination | JPG | #asFound Uncapped gas line | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 3 | #Photo-2017-02-08-09-31-34_0267.JPG While assessing a hazard call i found an uncapped shut off valve serving a range. Should somebody bump open the valve, raw gas could be released into the living space. This gas could accumulate until it finds a source of ignition, leading to a fire or explosion. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Photo-2017-02-08-09-31-34_0267.JPG | file://x:/photopub/docs/0000000555/ae60851a-2479-4c22-ae0b-4b06e8a339ad.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53b57170_174e_4c86_84d8_ea2bde8c95db
ELHE-718033-2016 | HE-476430-2016 | 12/6/2016 5:10:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found high voltage overhead conductors 14.4 kv are located too close to trees and building and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | g.png | file://x:/photopub/docs/0000000527/b4e08a77-7521-479e-bb9e-dc42bf4c77f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f771f32c_d939_4618_87fa_79be663c160b
ELHE-718033-2016 | HE-476430-2016 | 12/6/2016 5:10:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found high voltage overhead conductors 14.4 kv are located too close to trees and building and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | e.png | file://x:/photopub/docs/0000000527/9e0f4bc0-d264-4317-b925-4ae281870575.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f771f32c_d939_4618_87fa_79be663c160b
ELHE-718033-2016 | HE-476430-2016 | 12/6/2016 5:10:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found high voltage overhead conductors 14.4 kv are located too close to trees and building and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | b.png | file://x:/photopub/docs/0000000527/f5f9f421-716a-49a7-bb42-44e3eee515e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f771f32c_d939_4618_87fa_79be663c160b
ELHE-726544-2016 | HE-478494-2016 | 12/12/2016 2:57:16 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cable has not been provided with mechanical protection and could be damaged in this location creating a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_in_kitchen_cabinet.png | file://x:/photopub/docs/0000000535/70c7bf50-064c-4d4a-8a56-e475b7a8cb65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b56bfd51_b9a5_4dcf_8587_5f4eefe40974
GAUP-744944-2017 | UW-494409-2017 | 1/24/2017 5:15:53 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound 4" venting connected to 6" vent stack | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Oversized_venting1.png Venting is oversized for appliance. Flue gases can cool down inside Vent quickly and fall back into home, causing possible CO poisoning to occupants | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Oversized_venting1.png | file://x:/photopub/docs/0000000547/b4afe07f-0f0b-459c-a630-84744d9a116d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea351c8e_b3ef_4e0b_8139_9c6a9f751e4d
GAIN-757584-2017 | GA-491013-2017 | 2/22/2017 1:34:33 PM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | #Liquid_level.png Liquefaction of propane can create a hazard. First-stage and integral two-stage propane vapour regulators that are not installed directly on a propane container can be subjected to liquid propane due to no-flow conditions and/or changes in ambient temperatures if they are installed below the liquid level of the supply container. Vapour service regulators are not designed to regulate propane liquid, and may be damaged by it, or may pass liquid leading to hazardous conditions downstream. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Liquid_level.png | file://x:/photopub/docs/0000000561/fed5760c-20ac-4333-93f0-bbda2007582c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2dde2284_c007_4073_8b41_8e80bcf15db6
GAWP-749223-2017 | GA-439589-2016 | 1/31/2017 2:29:43 PM | ASSESS: GA Work In Progress | png | #asFound 2 psi system pressure regulator | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #Meter_pressure_regulator.png Furnace installed without an appliance regulator on a 2psi supply line. The appliance will be over fired leading to excessive heat and premature failure of the heat exchanger. | 4 | Appliance regulator not installed, incorrect delivery pressure | Meter_pressure_regulator.png | file://x:/photopub/docs/0000000550/c54d34c6-737a-494b-bdea-3d895e1407c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e434028_4b36_4d89_93db_322e09a477e7
ELOP-721070-2016 | 1958 | 12/8/2016 8:38:16 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | A non GFCI protected outlet near a sink can result in a shock hazard for someone using an electrical appliance near water. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Recetacle_near_sink_not_GFCI_protected.png | file://x:/photopub/docs/0000000532/27904c98-1df4-48b5-963d-4417883247ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40d46ed8_0c92_4ef9_8ced_f82d8f177f8d
PROP-599987-2016 | 4246968 | 12/14/2016 4:15:50 PM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Shackle is improperly installed, won't take as much Load as intended. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Shackle_side_loaded.png | file://x:/photopub/docs/0000000533/5b7463cc-4fcb-43d1-8bc1-41774200adc6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1E002C03_A0A8_47D6_B5B4_C3F64B794DB8
PROP-598624-2016 | PR-065398-2013 | 12/19/2016 11:32:44 AM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Choke chain being used as a tag line. Could become unattached if tensioning winch were to fail, causing carriage to slam forward. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Choke_chain_taglline_.png | file://x:/photopub/docs/0000000533/ef79c25c-653d-4aa2-b2bd-fe2a7207691d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0F4C5495_038F_4B2A_8741_1DCEF42A7DE8
ELIN-737278-2017 | EL-489095-2017 | 1/12/2017 12:43:51 PM | ASSESS: EL: Service Connection | png | #asFound Bond strap not connected. | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Missing_coverplate1.png,Missing_coverplate2.png There was no cover plate installed on a 15 amp /120 volt receptacle. This could lead to a potential shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Missing_coverplate1.png | file://x:/photopub/docs/0000000542/3282c33f-2e3f-4473-bbf8-df36006ce1c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47eb68d5_99bb_4c29_978b_ad2d9b15d9e9
ELIN-737278-2017 | EL-489095-2017 | 1/12/2017 12:43:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Missing_coverplate1.png,Missing_coverplate2.png There was no cover plate installed on a 15 amp /120 volt receptacle. This could lead to a potential shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Missing_coverplate2.png | file://x:/photopub/docs/0000000542/92ad46aa-0a3d-4ebd-969a-97a65effe2a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47eb68d5_99bb_4c29_978b_ad2d9b15d9e9
ELIN-734870-2017 | EL-449786-2016 | 1/12/2017 2:03:09 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Openings_in_panel_.png There were openings in the panel exposing energized bus. This could lead to accidental contact causing shock or electrocution. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Openings_in_panel_.png | file://x:/photopub/docs/0000000542/dfbf5a55-cb31-45c8-a8a9-4f098e07853f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__669afee1_0a2e_441e_ad3d_8087144a1038
ELIN-729455-2016 | EL-446103-2016 | 12/28/2016 9:48:15 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Rough wire of new single family dwelling. No gas line bonding conductor has been installed. This conductor is required when the gas lines are metallic. Failure to install this bonding conductor can lead to shock or failure of overcurrent devices to operate if damaged cables come in contact with them. | 3 | Equipment Gas line, cast or water pipe has not been bonded | No_gas_bonding_conductor.png | file://x:/photopub/docs/0000000536/d1738053-b538-4281-8cff-421da55a1276.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__170b158e_f8fb_4f99_afa1_48c1fac2f612
ELIN-729455-2016 | EL-446103-2016 | 12/28/2016 9:48:15 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Rough wire of new single family dwelling. No gas line bonding conductor has been installed. This conductor is required when the gas lines are metallic. Failure to install this bonding conductor can lead to shock or failure of overcurrent devices to operate if damaged cables come in contact with them. | 3 | Equipment Gas line, cast or water pipe has not been bonded | No_gas_bond_leaving_panel.png | file://x:/photopub/docs/0000000536/43893a18-c6ce-4bc2-bdb1-a0b0a11f3c27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__170b158e_f8fb_4f99_afa1_48c1fac2f612
ELIN-757534-2017 | EL-501336-2017 | 2/16/2017 12:02:56 PM | ASSESS: EL: Final | png | #asFound Likely no junction box is installed for this luminaire, electrician to verify. | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #How___how_s_found_electrical_wiring_on_the_exterior_of_house1.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house2.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house3.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house4.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house5.png Electrical wiring is not approved for the purpose and is located on the exterior of the building, water penetration could cause the electrical equipment too short and cause a fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | How___how_s_found_electrical_wiring_on_the_exterior_of_house1.png | file://x:/photopub/docs/0000000558/9fa98574-4833-457d-8943-dc2043f5db41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45d710af_1ecc_495f_ac17_5b1e6e10c04d
ELIN-757534-2017 | EL-501336-2017 | 2/16/2017 12:02:56 PM | ASSESS: EL: Final | png | #asFound Electrician to verify likely no junction box used for the installation of this luminaire | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #How___how_s_found_electrical_wiring_on_the_exterior_of_house1.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house2.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house3.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house4.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house5.png Electrical wiring is not approved for the purpose and is located on the exterior of the building, water penetration could cause the electrical equipment too short and cause a fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | How___how_s_found_electrical_wiring_on_the_exterior_of_house2.png | file://x:/photopub/docs/0000000558/1f06a5ee-eeb6-4a25-a71e-0b32efee5989.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45d710af_1ecc_495f_ac17_5b1e6e10c04d
ELIN-757534-2017 | EL-501336-2017 | 2/16/2017 12:02:56 PM | ASSESS: EL: Final | png | #asFound Nonmetallic sheath cable and dry type equipment used in an outdoor location | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #How___how_s_found_electrical_wiring_on_the_exterior_of_house1.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house2.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house3.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house4.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house5.png Electrical wiring is not approved for the purpose and is located on the exterior of the building, water penetration could cause the electrical equipment too short and cause a fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | How___how_s_found_electrical_wiring_on_the_exterior_of_house4.png | file://x:/photopub/docs/0000000558/d8deb985-2e62-43e2-a80e-c06e68f539ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45d710af_1ecc_495f_ac17_5b1e6e10c04d
ELIN-757534-2017 | EL-501336-2017 | 2/16/2017 12:02:56 PM | ASSESS: EL: Final | png | #asFound Dry type enclosure used outdoors no strapping or securing of conduit | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #How___how_s_found_electrical_wiring_on_the_exterior_of_house1.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house2.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house3.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house4.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house5.png Electrical wiring is not approved for the purpose and is located on the exterior of the building, water penetration could cause the electrical equipment too short and cause a fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | How___how_s_found_electrical_wiring_on_the_exterior_of_house5.png | file://x:/photopub/docs/0000000558/727d6e74-852a-4394-83f3-15bb5b35b625.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45d710af_1ecc_495f_ac17_5b1e6e10c04d
ELIN-757534-2017 | EL-501336-2017 | 2/16/2017 12:02:56 PM | ASSESS: EL: Final | png | #asFound Nonmetallic sheath cable and type one enclosure used outdoors. | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #How___how_s_found_electrical_wiring_on_the_exterior_of_house1.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house2.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house3.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house4.png,How___how_s_found_electrical_wiring_on_the_exterior_of_house5.png Electrical wiring is not approved for the purpose and is located on the exterior of the building, water penetration could cause the electrical equipment too short and cause a fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | How___how_s_found_electrical_wiring_on_the_exterior_of_house3.png | file://x:/photopub/docs/0000000558/c91a24d9-a4f7-4e0d-a238-0c1392648f69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45d710af_1ecc_495f_ac17_5b1e6e10c04d
BPVIN-736746-2017 | BPV-474325-2016 | 1/13/2017 7:40:21 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound Discharge only 8 feet from ground and less than 25 ft from doorway. | BP105 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | 2 | 3 | #Safety___valve_Discharge_lines_distance_less_than_required__1.png,Safety___valve_Discharge_lines_distance_less_than_required__2.png Safety valve discharge line is required to be 15 feet above ground. In addition, this discharge line is less than 25 feet from the nearest doorway. This may contribute to an incident in the event that the refrigerant is discharged to atmosphere during an overpressure situation and a person is in close proximity to the discharged gases. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | Safety___valve_Discharge_lines_distance_less_than_required__1.png | file://x:/photopub/docs/0000000558/513549fd-a4ea-4e48-b6f8-95bb24aac27f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6816d711_0970_465c_b4af_5642fd7ca914
BPVIN-736746-2017 | BPV-474325-2016 | 1/13/2017 7:40:21 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP105 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | 2 | 3 | #Safety___valve_Discharge_lines_distance_less_than_required__1.png,Safety___valve_Discharge_lines_distance_less_than_required__2.png Safety valve discharge line is required to be 15 feet above ground. In addition, this discharge line is less than 25 feet from the nearest doorway. This may contribute to an incident in the event that the refrigerant is discharged to atmosphere during an overpressure situation and a person is in close proximity to the discharged gases. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | Safety___valve_Discharge_lines_distance_less_than_required__2.png | file://x:/photopub/docs/0000000558/953ecebe-becc-4013-b5b0-321fc3ea57be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6816d711_0970_465c_b4af_5642fd7ca914
GAIN-747921-2017 | GA-466654-2016 | 2/10/2017 4:26:35 PM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | #Cloke3.png Fuel leak on appliance connector joint at furnace located in crawl space. Possible fire risk if a source of ignition were present. Very minor leak(peach fuzz) but this could increase over time if not corrected. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Cloke3.png | file://x:/photopub/docs/0000000556/f1163a8a-c053-49a2-9cac-a2c50ed79b20.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01792e74_8c67_4b18_aa47_beebe5c2a933
ELIN-755981-2017 | EL-500561-2017 | 2/14/2017 11:32:30 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Bonding conductors not terminated correctly at time of installation. | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #Bonding_conductors_damaged_at_time_of_installation1.png,Bonding_conductors_damaged_at_time_of_installation2.png The connection of the bonding conductors to equipment must be secure. By damaging the bonding conductor upon installation there is risk of the conductor breaking and opening the bonding circuit thereby creating a potential shock hazard. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Bonding_conductors_damaged_at_time_of_installation1.png | file://x:/photopub/docs/0000000557/5e617986-0b32-4bd6-bb27-480d7f4f646b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e8eae0f_8ce8_425c_b176_607a687a9c46
ELOP-730114-2016 | 5549 | 12/28/2016 11:12:07 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Electrical operating permit assessment of public library. The main distribution panel has two openings in the breaker section that are exposing energized buss to inadvertent contact. Shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Open_energized_buss.png | file://x:/photopub/docs/0000000536/9038600d-2c2d-47af-a67f-a3931da4d964.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bb313ce_7dac_4cd8_8cef_08a8482cfe45
ELIN-729195-2016 | EL-483810-2016 | 12/28/2016 12:26:49 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Rough wire of new detached shop. Metallic gas line has not been bonded. This can cause overcurrent devices not to function if damaged cables come into contact with the gas line. Shock hazard. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Gas_lines_.png | file://x:/photopub/docs/0000000536/9aec1093-d4ff-4cf1-bb95-ba2c732cb57e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__880a263e_aebf_494b_872f_7bccfd9481e9
ELIN-722444-2016 | EL-477855-2016 | 12/15/2016 11:19:56 AM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | 100 amp service is not grounded. This is a hazard as protection devices will not operate properly and lightening could easily damage the ungrounded wiring. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | A.png | file://x:/photopub/docs/0000000533/f010dc17-c630-4af9-a23e-056f8f2c515f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26d42288_a280_4f80_8e93_e6c1718cbd38
ELOP-707861-2016 | 5434619 | 12/19/2016 1:02:54 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Load break switch handle not grounded. This is a shock hazard as an individual could be electrocuted while operating an ungrounded switch. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | F.png | file://x:/photopub/docs/0000000533/212bea03-d43d-42a5-b992-3580a482450b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e8bbcf1_f8d8_4950_b5f1_cc9e75e88fc8
ELIN-722444-2016 | EL-477855-2016 | 12/15/2016 11:19:56 AM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | 100 amp service is not grounded. This is a hazard as protection devices will not operate properly and lightening could easily damage the ungrounded wiring. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | B.png | file://x:/photopub/docs/0000000533/76445a3a-96b4-4d77-be2d-67989c3afb3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26d42288_a280_4f80_8e93_e6c1718cbd38
GAIN-748473-2017 | GA-486689-2017 | 2/2/2017 11:08:37 AM | ASSESS: GA: Final | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | #Water_heater.png A natural draft water heater was found installed in the same area where an exhaust fan was in operation creating a negative condition in the space that resulted in the products (Carbon Monoxide) of combustion entering into the occupied space. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Water_heater.png | file://x:/photopub/docs/0000000552/25da8bbb-46b5-4560-b2da-39be8d5203ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__208ce99c_96ec_4cda_a954_b8e37c731f9e
ELIN-732520-2017 | EL-351120-2016 | 1/5/2017 10:23:45 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | Ground Plate not buried to correct depth, In a fault conditions there could be a shock hazard | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_plate_not_covered.png | file://x:/photopub/docs/0000000539/6cb09506-cc26-4ce3-bf19-2d9f892e7b95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24185b58_af2d_4517_833e_6494f9926cae
EDIN-712289-2016 | ED-457946-2016 | 12/5/2016 8:01:50 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | The emergency 2-way emergency communication in the elevator is a means of communication to a 24 hours/day monitored station. During an acceptance inspection it was found the 2-way emergency communication was not functioning properly because the monitoring station was not able to tell us our location. Without a properly functioning 2-way emergency communication in the elevator it may be difficult to get help in case of an entrapment in the elevators. This may result in a serious situation if panic sets in or if a person had a medical emergency and was trapped in the elevator. This is a 4 top MRL traction elevator located in a newly constructed commercial building. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | Elevator_emergency_communication.png | file://x:/photopub/docs/0000000526/f9470d77-d248-46a8-96b2-4af4bcf7cb9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42bc9c8a_f804_4c6e_8ab5_9c463879f4d9
BPVIN-736746-2017 | BPV-474325-2016 | 1/13/2017 7:40:21 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP105 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | 2 | 3 | #Safety___valve_Discharge_lines_distance_less_than_required__1.png,Safety___valve_Discharge_lines_distance_less_than_required__2.png Safety valve discharge line is required to be 15 feet above ground. In addition, this discharge line is less than 25 feet from the nearest doorway. This may contribute to an incident in the event that the refrigerant is discharged to atmosphere during an overpressure situation and a person is in close proximity to the discharged gases. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | Safety___valve_Discharge_lines_distance_less_than_required__2.png | file://x:/photopub/docs/0000000558/21d373f3-bcac-4df1-973e-cd26fa70c55e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6816d711_0970_465c_b4af_5642fd7ca914
BPVIN-736746-2017 | BPV-474325-2016 | 1/13/2017 7:40:21 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP105 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | 2 | 3 | #Safety___valve_Discharge_lines_distance_less_than_required__1.png,Safety___valve_Discharge_lines_distance_less_than_required__2.png Safety valve discharge line is required to be 15 feet above ground. In addition, this discharge line is less than 25 feet from the nearest doorway. This may contribute to an incident in the event that the refrigerant is discharged to atmosphere during an overpressure situation and a person is in close proximity to the discharged gases. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | Safety___valve_Discharge_lines_distance_less_than_required__1.png | file://x:/photopub/docs/0000000558/0d29b966-80cd-4ed5-ba1b-ac68df3bdce8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6816d711_0970_465c_b4af_5642fd7ca914
ELIN-738260-2017 | EL-337894-2016 | 1/16/2017 9:57:22 AM | ASSESS: EL: Service Connection | png | #asFound Grounding conductor with no electrode attached | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | #Ground_conductor_with_no_electrode_.png No ground Ã©lectrode installed With an incomplete system ground there is a danger of a shock during an electrical fault on the system | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_conductor_with_no_electrode_.png | file://x:/photopub/docs/0000000543/758e6ba9-07db-4e0b-9ce0-655ad4f4f36d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e9a4d56_f7a6_4b10_b295_194cceb80fd6
ELIN-738320-2017 | EL-351115-2016 | 1/16/2017 10:56:17 AM | ASSESS: EL: Service Connection | png | #asFound Ground plate not covered | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | #Ground_plate.png Ground plate not covered Could be a shock hazard during and electrical fault | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_plate.png | file://x:/photopub/docs/0000000543/87859104-a76f-46ec-91dd-a4c8940b67f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45592a90_d802_4d64_bc00_cbdac809619f
ELIN-713649-2016 | EL-388225-2016 | 11/30/2016 1:39:39 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL082 | Continuity Multiple grounded systems are not interconnected. | 3 | 3 | -two ground electrodes have been installed at the building but have not been interconnected which may cause ground loops to occur across the grounding and bonding systems. | 3 | Continuity Multiple grounded systems are not interconnected. | -pic_1.png | file://x:/photopub/docs/0000000525/3fb36e4a-070e-41e0-b06a-4a4ae36bd26e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be8459e5_d671_4e25_a1c6_b76a493df9cc
ELIN-713649-2016 | EL-388225-2016 | 11/30/2016 1:39:39 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL082 | Continuity Multiple grounded systems are not interconnected. | 3 | 3 | -two ground electrodes have been installed at the building but have not been interconnected which may cause ground loops to occur across the grounding and bonding systems. | 3 | Continuity Multiple grounded systems are not interconnected. | Pic_2.png | file://x:/photopub/docs/0000000525/ef9ce76e-1c97-419f-acb1-c3089bacf13c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be8459e5_d671_4e25_a1c6_b76a493df9cc
ELIN-755981-2017 | EL-500561-2017 | 2/14/2017 11:32:30 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #Bonding_conductors_damaged_at_time_of_installation1.png,Bonding_conductors_damaged_at_time_of_installation2.png The connection of the bonding conductors to equipment must be secure. By damaging the bonding conductor upon installation there is risk of the conductor breaking and opening the bonding circuit thereby creating a potential shock hazard. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Bonding_conductors_damaged_at_time_of_installation2.png | file://x:/photopub/docs/0000000557/ddb89d84-16cb-4bdb-bbd4-8a6943891fab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e8eae0f_8ce8_425c_b176_607a687a9c46
ELHE-757589-2017 | HE-501366-2017 | 2/15/2017 2:09:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 4 | #Service1.png,Service2.png Service attachment point and service conduit gas been removed from building. High fault current is available on BC Hydro line leaving hazard of shock or fire. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service1.png | file://x:/photopub/docs/0000000557/1963eaac-bc46-49fa-9f8f-7843982e33b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__234ea86f_d019_4cf0_b2be_5136000e83a6
ELHE-757589-2017 | HE-501366-2017 | 2/15/2017 2:09:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 4 | #Service1.png,Service2.png Service attachment point and service conduit gas been removed from building. High fault current is available on BC Hydro line leaving hazard of shock or fire. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service2.png | file://x:/photopub/docs/0000000557/dd2fb686-5f58-4d4a-9e02-bde58a2309b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__234ea86f_d019_4cf0_b2be_5136000e83a6
ELIN-757593-2017 | EL-483001-2016 | 2/15/2017 2:21:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Neutral_conductors1.png,Neutral_conductors2.png,Neutral_conductors3.png Neutral not identified. Possibility to be energized as a line conductor creating a shock hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Neutral_conductors1.png | file://x:/photopub/docs/0000000557/358ad628-0242-4016-a3e3-5f167d0330ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acf79f4f_a993_4ecc_8dee_b8c4b56b143a
ELIN-757593-2017 | EL-483001-2016 | 2/15/2017 2:21:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Neutral_conductors1.png,Neutral_conductors2.png,Neutral_conductors3.png Neutral not identified. Possibility to be energized as a line conductor creating a shock hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Neutral_conductors2.png | file://x:/photopub/docs/0000000557/e32a4463-8aed-411f-9b00-10acadfc2a1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acf79f4f_a993_4ecc_8dee_b8c4b56b143a
ELIN-757593-2017 | EL-483001-2016 | 2/15/2017 2:21:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Neutral_conductors1.png,Neutral_conductors2.png,Neutral_conductors3.png Neutral not identified. Possibility to be energized as a line conductor creating a shock hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Neutral_conductors3.png | file://x:/photopub/docs/0000000557/5a86e6fc-034a-4efd-a32e-e1962b166b5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acf79f4f_a993_4ecc_8dee_b8c4b56b143a
BPVIN-730671-2016 | BPV-399016-2016 | 12/29/2016 5:59:24 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | Upon assessment it is determined that high temperature safety cutout with manual reset is installed down stream of boiler outlet shutoff valve. Inadvertent closing of outlet shutoff valve will isolate high temperature cutout device and can lead to dangerous situation if other safety devices fail to protect boiler. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Hi-temperature_safety_cutout_not_installed_properly.png | file://x:/photopub/docs/0000000536/02db2ee5-64ed-4eed-85dd-77373b3d04db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e24e42e7_bbf5_41f7_8111_4cdd54e2e2a5
GAHE-758779-2017 | HE-502070-2017 | 2/16/2017 11:39:20 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 4 | #Gas1.png,Gas2.png Found propane tank in mobile home park that was not connected to any building anymore, found copper piping open, no cap and when looked at tank found the service valve in the open position. Propane tanks when not in use should be removed from site or capped to prevent the release of propane which could catch fire or create an explosion. | 5 | Open gas line connected to fuel supply (no cap/plug) | Gas1.png | file://x:/photopub/docs/0000000559/43d35311-e846-4aaa-afe5-96f04e9b8347.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1c01186_e74c_439a_86cf_c389280f00a1
GAHE-758779-2017 | HE-502070-2017 | 2/16/2017 11:39:20 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 4 | #Gas1.png,Gas2.png Found propane tank in mobile home park that was not connected to any building anymore, found copper piping open, no cap and when looked at tank found the service valve in the open position. Propane tanks when not in use should be removed from site or capped to prevent the release of propane which could catch fire or create an explosion. | 5 | Open gas line connected to fuel supply (no cap/plug) | Gas2.png | file://x:/photopub/docs/0000000559/75270bb4-fc0a-4b33-814c-5a2159d81003.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1c01186_e74c_439a_86cf_c389280f00a1
BPVOP-739984-2017 | 2252773 | 1/17/2017 9:11:58 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 | #Int.png | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | Int.png | file://x:/photopub/docs/0000000544/bd7fdec7-0580-4b46-8984-e0e8343cf2f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f97961af_c417_45d9_afef_78f5c75a22b3
GAIN-729545-2016 | GA-371814-2016 | 1/5/2017 12:58:07 PM | ASSESS: GA: Rough-In | png | #asFound | GA080 | Line pressure regulator without required overpressure protection in place | 3 | 3 | The hazard is that the inlet gas pressure is too high for the rating of the gas regulator serving a temporary heater. This could result in dangerous operation of the appliance, poor combustion and release of harmful emmissions | 3 | Line pressure regulator without required overpressure protection in place | Temporary_heater.png | file://x:/photopub/docs/0000000539/1d472648-a9b5-4178-9cea-aff10e0a941f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc4b8c03_2b34_4357_aa6d_d74e5801be14
GAIN-729036-2016 | GA-484650-2016 | 1/5/2017 2:43:37 PM | ASSESS: GA: Final | png | #asFound | GA064 | Gas leak readily detectable, able to pinpoint and isolate at source | 4 | 4 | When pulled commercial range out for inspection, strong gas odour, able to pin point by smell and then checked with soap and water. Bubbles at street 90 and appliance regulator. Gas leak could cause a fire or explosion as open pilot lights on range. | 4 | Gas leak readily detectable, able to pinpoint and isolate at source | Farrier_2.png | file://x:/photopub/docs/0000000539/eb140838-077f-4713-995d-87d570a1ec66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3988f1c5_3262_488b_b7cf_d535bc3f293a
GAIN-729036-2016 | GA-484650-2016 | 1/5/2017 2:43:37 PM | ASSESS: GA: Final | png | #asFound | GA064 | Gas leak readily detectable, able to pinpoint and isolate at source | 4 | 4 | When pulled commercial range out for inspection, strong gas odour, able to pin point by smell and then checked with soap and water. Bubbles at street 90 and appliance regulator. Gas leak could cause a fire or explosion as open pilot lights on range. | 4 | Gas leak readily detectable, able to pinpoint and isolate at source | Farrier1.png | file://x:/photopub/docs/0000000539/11e31b10-2625-4155-8694-ed004b5296b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3988f1c5_3262_488b_b7cf_d535bc3f293a
PRIN-732237-2017 | PR-459184-2016 | 1/4/2017 8:22:57 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR031 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | 1 | 1 |  | 1 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | Newly_installed_safety_gate.png | file://x:/photopub/docs/0000000539/31f18df3-374b-4c3f-a9a5-93e674a4b764.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cc6078c_7e0b_48f7_9236_a3dbce32abf0
PRIN-732237-2017 | PR-459184-2016 | 1/4/2017 8:22:57 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR031 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | 1 | 1 |  | 1 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | Load_test.png | file://x:/photopub/docs/0000000539/f9f755c6-4042-4e6f-87ab-dde05337d959.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cc6078c_7e0b_48f7_9236_a3dbce32abf0
GAIN-753361-2017 | GA-499169-2017 | 2/16/2017 1:53:02 PM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Furnace.png The as-found-condition is that insufficient combustion air supply was provided to a high efficiency furnace. The potential hazard is that the furnace could become starved for air, resulting in improper combustion characteristics and the release of harmful emissions such as CO. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Furnace.png | file://x:/photopub/docs/0000000558/fe052e86-87d7-4274-b6d7-e4af9f3b7374.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ccde074f_80f3_4b57_96fe_c92fe730dea5
GAIN-744143-2017 | GA-395497-2016 | 2/17/2017 11:08:40 AM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Comb_air_crawl_space.png,Comb_air_crawl_space2.png Combustion air is being pulled from Crawl space. Crawl space does not have any air returning to crawl space. Combustion of appliances will look elsewhere for air, flame roll out may occur | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Comb_air_crawl_space2.png | file://x:/photopub/docs/0000000558/24fcd0ec-3424-499e-8a89-4cf7c8bc594d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbcbc0d0_b64b_42ef_a36b_99241677ddec
GAIN-744143-2017 | GA-395497-2016 | 2/17/2017 11:08:40 AM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Comb_air_crawl_space.png,Comb_air_crawl_space2.png Combustion air is being pulled from Crawl space. Crawl space does not have any air returning to crawl space. Combustion of appliances will look elsewhere for air, flame roll out may occur | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Comb_air_crawl_space.png | file://x:/photopub/docs/0000000558/9525c399-d3b4-4b35-b0d8-9d62b9489e37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbcbc0d0_b64b_42ef_a36b_99241677ddec
GAWP-743787-2017 | GA-442443-2016 | 2/21/2017 9:13:52 AM | ASSESS: GA Work In Progress | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Maple_bay_2.png Open gas line with valve in closed position. If valve were to be opened unintentionally ,uncontrolled release of fuel would occur. Explosion and fire hazard risk | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Maple_bay_2.png | file://x:/photopub/docs/0000000560/81594044-ec47-4581-bf53-ec5ffc091f99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9442ef2_4f22_40e4_a36b_a3ed39fef486
ELIN-730275-2016 | EL-477162-2016 | 1/3/2017 12:18:07 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | DB2 conduit for service conductors has been installed above ground. Conduit is built with a thinner wall and not meant to be located above ground, this conduit also does not have the mechanical and ultraviolet strength of rigid PVC conduit and is meant for underground use only. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | DB2_conduit__DB2_conduit_above_ground.png | file://x:/photopub/docs/0000000537/5eb5b17a-82a9-4f6a-b055-0f9a40cc0b27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1317305_0438_42f5_9a32_e564a8515b3d
ELHE-727348-2016 | HE-483669-2016 | 12/20/2016 2:43:53 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Main service panel is found without cover with exposed energized main wires without insulation before the main 100A-2 pole breaker. Fault current in the event of accidental short between line 1 and line 2, before the main breaker could cause an arc flash condition which could cause shock, serious body burns, fire and even death. Accidental contact to other energized exposed parts in of the panel can also cause serious injury or death. | 4 | Conductors, Misuse of flexible cords. | 6.png | file://x:/photopub/docs/0000000534/e7223a72-ff0b-4521-88e9-acfc861e8869.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__089ddcb7_1411_48c0_99f5_f3f47d0564e4
ELHE-727348-2016 | HE-483669-2016 | 12/20/2016 2:43:53 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Main service panel is found without cover with exposed energized main wires without insulation before the main 100A-2 pole breaker. Fault current in the event of accidental short between line 1 and line 2, before the main breaker could cause an arc flash condition which could cause shock, serious body burns, fire and even death. Accidental contact to other energized exposed parts in of the panel can also cause serious injury or death. | 4 | Conductors, Misuse of flexible cords. | 3.png | file://x:/photopub/docs/0000000534/c73870b9-975f-4e98-a92e-63e473fa7d16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__089ddcb7_1411_48c0_99f5_f3f47d0564e4
ELHE-727348-2016 | HE-483669-2016 | 12/20/2016 2:43:53 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Main service panel is found without cover with exposed energized main wires without insulation before the main 100A-2 pole breaker. Fault current in the event of accidental short between line 1 and line 2, before the main breaker could cause an arc flash condition which could cause shock, serious body burns, fire and even death. Accidental contact to other energized exposed parts in of the panel can also cause serious injury or death. | 4 | Conductors, Misuse of flexible cords. | 5.png | file://x:/photopub/docs/0000000534/470a9ca3-ffe3-42b6-b242-a4f9719e5d82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__089ddcb7_1411_48c0_99f5_f3f47d0564e4
ELHE-727348-2016 | HE-483669-2016 | 12/20/2016 2:43:53 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Main service panel is found without cover with exposed energized main wires without insulation before the main 100A-2 pole breaker. Fault current in the event of accidental short between line 1 and line 2, before the main breaker could cause an arc flash condition which could cause shock, serious body burns, fire and even death. Accidental contact to other energized exposed parts in of the panel can also cause serious injury or death. | 4 | Conductors, Misuse of flexible cords. | 1.png | file://x:/photopub/docs/0000000534/fc4b965a-09f4-4800-9e65-22d08b3b9459.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__089ddcb7_1411_48c0_99f5_f3f47d0564e4
ELHE-727348-2016 | HE-483669-2016 | 12/20/2016 2:43:53 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Main service panel is found without cover with exposed energized main wires without insulation before the main 100A-2 pole breaker. Fault current in the event of accidental short between line 1 and line 2, before the main breaker could cause an arc flash condition which could cause shock, serious body burns, fire and even death. Accidental contact to other energized exposed parts in of the panel can also cause serious injury or death. | 4 | Conductors, Misuse of flexible cords. | 4.png | file://x:/photopub/docs/0000000534/f3eff367-7496-4661-995e-aecb7694d192.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__089ddcb7_1411_48c0_99f5_f3f47d0564e4
ELHE-727348-2016 | HE-483669-2016 | 12/20/2016 2:43:53 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Main service panel is found without cover with exposed energized main wires without insulation before the main 100A-2 pole breaker. Fault current in the event of accidental short between line 1 and line 2, before the main breaker could cause an arc flash condition which could cause shock, serious body burns, fire and even death. Accidental contact to other energized exposed parts in of the panel can also cause serious injury or death. | 4 | Conductors, Misuse of flexible cords. | 2.png | file://x:/photopub/docs/0000000534/ab7b4bac-09d4-48b2-820c-a93a7da7a390.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__089ddcb7_1411_48c0_99f5_f3f47d0564e4
ELIN-710997-2016 | EL-415179-2016 | 12/5/2016 11:56:58 AM | ASSESS: EL: Final | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 | The number of circuits entered into the distribution panel exceed the number of spaces available for breakers to protect the circuits. These circuits can not be supplied from this panel. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 113_Whiteshield_panel.png | file://x:/photopub/docs/0000000539/6982316f-1aba-48a2-ab53-36e9901d2a34.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0970ac5c_b2c9_4713_b75f_c352d32abb28
BPVOP-749242-2017 | BPV-283420-2015 | 1/31/2017 4:31:57 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound BCSA CRN Acceptance Letter | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 4 | #Photo-2017-01-31-08-51-45_3837.JPG,Photo-2017-01-31-19-05-02_3905.JPG,Photo-2017-01-31-19-05-17_3906.JPG,Photo-2017-01-31-19-06-05_3907.JPG The January 30, 2017 ultrasonic inspection report for the boiler tubes indicates that of the 56 out of 175 boiler tubes sampled 16 tubes are below the nominal thickness of 0.105" as documented on the manufacturer's data report. Readings below 0.105" ranged from 0.102" to the lowest reading sample measured of 0.070" or up to 33% tube wall loss due to corrosion. This may contribute to an incident. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Photo-2017-01-31-19-06-05_3907.JPG | file://x:/photopub/docs/0000000550/e5c18c3d-6b1d-4ef5-b77e-24f2f7213e26.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__662fd9db_c60d_4176_817d_8f3a2db99bb8
BPVOP-749242-2017 | BPV-283420-2015 | 1/31/2017 4:31:57 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound View from boiler top man-way. | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 4 | #Photo-2017-01-31-08-51-45_3837.JPG,Photo-2017-01-31-19-05-02_3905.JPG,Photo-2017-01-31-19-05-17_3906.JPG,Photo-2017-01-31-19-06-05_3907.JPG The January 30, 2017 ultrasonic inspection report for the boiler tubes indicates that of the 56 out of 175 boiler tubes sampled 16 tubes are below the nominal thickness of 0.105" as documented on the manufacturer's data report. Readings below 0.105" ranged from 0.102" to the lowest reading sample measured of 0.070" or up to 33% tube wall loss due to corrosion. This may contribute to an incident. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Photo-2017-01-31-08-51-45_3837.JPG | file://x:/photopub/docs/0000000550/e259260b-e45e-496d-9c42-7f2614cbf2d9.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__662fd9db_c60d_4176_817d_8f3a2db99bb8
BPVOP-749242-2017 | BPV-283420-2015 | 1/31/2017 4:31:57 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound MDR page 2 | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 4 | #Photo-2017-01-31-08-51-45_3837.JPG,Photo-2017-01-31-19-05-02_3905.JPG,Photo-2017-01-31-19-05-17_3906.JPG,Photo-2017-01-31-19-06-05_3907.JPG The January 30, 2017 ultrasonic inspection report for the boiler tubes indicates that of the 56 out of 175 boiler tubes sampled 16 tubes are below the nominal thickness of 0.105" as documented on the manufacturer's data report. Readings below 0.105" ranged from 0.102" to the lowest reading sample measured of 0.070" or up to 33% tube wall loss due to corrosion. This may contribute to an incident. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Photo-2017-01-31-19-05-17_3906.JPG | file://x:/photopub/docs/0000000550/1155be30-a055-4c94-80f8-5998530a6ed0.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__662fd9db_c60d_4176_817d_8f3a2db99bb8
BPVOP-749242-2017 | BPV-283420-2015 | 1/31/2017 4:31:57 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound MDR page 1 | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 4 | #Photo-2017-01-31-08-51-45_3837.JPG,Photo-2017-01-31-19-05-02_3905.JPG,Photo-2017-01-31-19-05-17_3906.JPG,Photo-2017-01-31-19-06-05_3907.JPG The January 30, 2017 ultrasonic inspection report for the boiler tubes indicates that of the 56 out of 175 boiler tubes sampled 16 tubes are below the nominal thickness of 0.105" as documented on the manufacturer's data report. Readings below 0.105" ranged from 0.102" to the lowest reading sample measured of 0.070" or up to 33% tube wall loss due to corrosion. This may contribute to an incident. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Photo-2017-01-31-19-05-02_3905.JPG | file://x:/photopub/docs/0000000550/6161aefb-059d-4106-a43c-6fce7e990e04.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__662fd9db_c60d_4176_817d_8f3a2db99bb8
PROP-741434-2017 | PR-492475-2017 | 1/19/2017 2:02:50 AM | ASSESS: PR OP: Annual | png | #asFound Section of shirting missing at unload area | PR025 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Section_of_skirting_missing.png Passenger conveyors are to be provided with skirting along the full length of the conveyor. It was observed that a short section of skirting was missing (approximately.5m length). The cavern below the edge of the conveyor results in an entrapment hazard. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Section_of_skirting_missing.png | file://x:/photopub/docs/0000000545/68114b52-9ae6-421b-a70f-9c259fc2c8e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__80b9c9b0_d0f1_47bc_b369_817e18c2d041
ELIN-730462-2016 | EL-390421-2016 | 12/30/2016 6:47:32 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Light fixtures above showers are required to be approved for wet or damp locations. This is to protect moisture from entering the fixture and causing corrosion on live parts or making contact with a hot lamp. In this installation in a single family dwelling, a recessed light was installed over a shower without an approved trim for wet or damp locations. The open style recessed fixture could allow moisture to make contact with the hot incandescent lamp which could cause the lamp to shatter and hot glass to fall into the shower. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Shower_fixture.png | file://x:/photopub/docs/0000000536/6b44b8d8-5fae-4b40-91cf-eadd43f6749a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__913c037d_3b5c_4909_9ca3_67c20d531aa6
ELIN-733026-2017 | EL-453265-2016 | 1/17/2017 1:27:34 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #No_outlet_on_AC90.png 15 amp, 120 volt AC90 installed for future electrical equipment not installed in outlet box. This is a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | No_outlet_on_AC90.png | file://x:/photopub/docs/0000000546/d70deffc-f0be-4db6-aee9-1c3b90354d89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01819c8e_e338_4bc0_896f_0f30ef40ec84
ELIN-722861-2016 | EL-480072-2016 | 12/19/2016 1:00:54 PM | ASSESS: EL: Final | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 3 | 120/240 volt branch circuit wiring installed in main distribution not installed with connectors. This is a thermal issue. | 3 | Conductors, No expansion joint or not installed correctly. | No_connectors.png | file://x:/photopub/docs/0000000533/11f56460-5991-4932-9048-66a63bdc4a5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__568590ba_93fc_49b6_816a_1768daa1c578
GAIN-760242-2017 | GA-386668-2016 | 2/22/2017 9:30:58 AM | ASSESS: GA: Rough-In | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Combustion_air_grille1.png,Combustion_air_grille2.png Combustion air grille is not big enough to provide air requirements for two make up air units, could produce improper combustion and create a hazardous environment | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Combustion_air_grille2.png | file://x:/photopub/docs/0000000561/acc3c4c3-d141-44e2-be29-f83331e7f6c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13b64d9d_d9c6_4534_94a4_c90a01e6ea0a
GAIN-760242-2017 | GA-386668-2016 | 2/22/2017 9:30:58 AM | ASSESS: GA: Rough-In | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Combustion_air_grille1.png,Combustion_air_grille2.png Combustion air grille is not big enough to provide air requirements for two make up air units, could produce improper combustion and create a hazardous environment | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Combustion_air_grille1.png | file://x:/photopub/docs/0000000561/49ce7f89-346d-4869-9ac7-8fabef6e373e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13b64d9d_d9c6_4534_94a4_c90a01e6ea0a
ELIN-748484-2017 | EL-491123-2017 | 1/31/2017 8:12:03 AM | ASSESS: EL: Service Connection | png | #asFound Service ground entering the meter base. | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #N7.png Service grounding is terminated in the service equipment before the main disconnect device on the supply side. Although there is grounding protection through the meter bonded to the service equipment but installation does not meet code requirements. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | N7.png | file://x:/photopub/docs/0000000552/f559a67c-7289-46cf-975b-f3932745a591.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b68efcbf_1ac1_47f6_a2bd_d079d8caa07e
ELHE-718033-2016 | HE-476430-2016 | 12/6/2016 5:10:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found high voltage overhead conductors 14.4 kv are located too close to trees and building and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | d.png | file://x:/photopub/docs/0000000527/b4b6fe4a-3543-480f-970b-9bcafd292a8e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f771f32c_d939_4618_87fa_79be663c160b
ELHE-718033-2016 | HE-476430-2016 | 12/6/2016 5:10:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found high voltage overhead conductors 14.4 kv are located too close to trees and building and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | i.png | file://x:/photopub/docs/0000000527/e2ba6e38-d20c-414b-a7ba-14ba369ff8e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f771f32c_d939_4618_87fa_79be663c160b
ELHE-718033-2016 | HE-476430-2016 | 12/6/2016 5:10:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found high voltage overhead conductors 14.4 kv are located too close to trees and building and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | f.png | file://x:/photopub/docs/0000000527/547fbed6-42e2-4957-9b6a-c7c396142299.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f771f32c_d939_4618_87fa_79be663c160b
BPVIN-412750-2015 | BPV-254314-2015 | 1/31/2017 10:40:39 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Disconnect_switch__.png,Boiler_switch_.png A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected when required. I found that there was no lockout system provided on the disconnect switches. Potential exists for an incident due to system becoming energized while work is being carried out. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Disconnect_switch__.png | file://x:/photopub/docs/0000000553/74358c3b-eba4-4092-8481-e21d1aa2e01b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7712e2ae_5542_4078_bef6_19fa4575be4e
BPVIN-412750-2015 | BPV-254314-2015 | 1/31/2017 10:40:39 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Disconnect_switch__.png,Boiler_switch_.png A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected when required. I found that there was no lockout system provided on the disconnect switches. Potential exists for an incident due to system becoming energized while work is being carried out. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_switch_.png | file://x:/photopub/docs/0000000553/7c45c8c8-ff86-45e0-9f68-fda0dd8d78ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7712e2ae_5542_4078_bef6_19fa4575be4e
ELHE-720161-2016 | HE-478069-2016 | 12/12/2016 10:46:54 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Feeder overcurrent protection for mobile home unit # 29 is undersized for load demand. This could be hazard if the overcurrent protection keeps on tripping due to the demand load exceeding the overcurrent protection limits. If the overcurrent protection gets reset over and over this could wear out the trip mechanism and eventually cause the overcurrent protection to fail. This could result in possible fire if the load exceeds the rating of the feeder cable. | 0 | No Created Hazard Identified | 60_amp_overcurrent_protection.png | file://x:/photopub/docs/0000000530/c4d5ced2-2deb-4b89-9d21-5f463ebc53e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ee9ade3_b299_4358_959e_2018703d9551
BPVOP-729592-2016 | 2256013 | 1/4/2017 1:52:32 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided for hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_remote_shutdown_switch.png | file://x:/photopub/docs/0000000538/48e34efb-ded4-4270-bcac-ca3469122e8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29c2d80d_ce39_4264_85eb_7d06da7ad823
EDIN-743970-2017 | ED-430926-2016 | 2/7/2017 | ASSESS: ED IN: Acceptance | png | #asFound | ED057 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 2 | 2 | #Floor_opening_beside_cartveyor2.png Opening in the floor beside the cartveyor. | 2 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | Floor_opening_beside_cartveyor2.png | file://x:/photopub/docs/0000000554/649f0087-6a8b-4f33-83b8-f8af4d7d0e34.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4260f538_4abf_4981_87be_ad7bf8dbf6ab
EDIN-743972-2017 | ED-430916-2016 | 2/7/2017 | ASSESS: ED IN: Acceptance | png | #asFound | ED057 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 2 | 2 | #Floor_opening_beside_down_cartveyor.png Opening in the floor beside the cartveyor. | 2 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | Floor_opening_beside_down_cartveyor.png | file://x:/photopub/docs/0000000554/1f5f82ba-f79f-4fee-891e-05c84123c607.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4b18e3a_cfdc_44d4_add8_8b7007c1b269
ELHE-718033-2016 | HE-476430-2016 | 12/6/2016 5:10:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found high voltage overhead conductors 14.4 kv are located too close to trees and building and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | a.png | file://x:/photopub/docs/0000000527/91f02578-208c-46a2-87d0-fa46ad60d159.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f771f32c_d939_4618_87fa_79be663c160b
ELHE-718033-2016 | HE-476430-2016 | 12/6/2016 5:10:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found high voltage overhead conductors 14.4 kv are located too close to trees and building and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | k.png | file://x:/photopub/docs/0000000527/7fabb38d-f47e-44b8-b778-f1f7eaca741b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f771f32c_d939_4618_87fa_79be663c160b
ELHE-718033-2016 | HE-476430-2016 | 12/6/2016 5:10:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found high voltage overhead conductors 14.4 kv are located too close to trees and building and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | c.png | file://x:/photopub/docs/0000000527/965f1fef-f4ea-4bce-b1e4-3b3c4eb4c47c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f771f32c_d939_4618_87fa_79be663c160b
ELHE-718033-2016 | HE-476430-2016 | 12/6/2016 5:10:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found high voltage overhead conductors 14.4 kv are located too close to trees and building and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | j.png | file://x:/photopub/docs/0000000527/86d42a64-1d41-43af-a77c-03d12a9bd988.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f771f32c_d939_4618_87fa_79be663c160b
ELIN-724784-2016 | EL-454146-2016 | 12/20/2016 1:54:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | Improper, additional neutral â€“ ground bonds not only create shock hazards for operating personnel, but can also degrade the performance of electronic equipment. | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | Xo_ground_conductor_bonded_to_equipment.png | file://x:/photopub/docs/0000000534/2eba61c7-ad60-4edb-b635-37cb1bf4adf1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__508d03c9_f75e_4d83_822a_78040e0a168c
ELIN-753197-2017 | EL-456569-2016 | 2/11/2017 9:25:09 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL274 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | 3 | 3 | #Shower.png This assessment found the wall switch for a bathroom light located less than the required 1m of a shower enclosure. At this distance a person in the shower is able to operate the light switch, presenting a shock hazard. | 3 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | Shower.png | file://x:/photopub/docs/0000000556/78adf7ef-b3d0-4534-9060-0c4f6bf7aaec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a62c38eb_c071_40d2_84c7_3a7a98fec840
ELIN-738196-2017 | UW-490187-2017 | 1/16/2017 10:10:45 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | #A1.png,A2.png Unused openings in panel. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | A2.png | file://x:/photopub/docs/0000000544/aa11ab1d-49c2-403e-8646-36673e47c594.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e87d91ee_0451_445f_8d9f_52ca95242e94
ELIN-738196-2017 | UW-490187-2017 | 1/16/2017 10:10:45 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | #A1.png,A2.png Unused openings in panel. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | A1.png | file://x:/photopub/docs/0000000544/4f583739-535d-44ae-8ce5-c16f1f1c7f92.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e87d91ee_0451_445f_8d9f_52ca95242e94
BPVOP-751307-2017 | 2302780 | 2/3/2017 1:11:49 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Prd.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 3 years as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Prd.png | file://x:/photopub/docs/0000000553/c4febb7c-4a30-44ee-adb6-27b15e28deff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6cdebcb_291e_4a4e_946c_0c4d91184e7f
ELHE-718033-2016 | HE-476430-2016 | 12/6/2016 5:10:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found high voltage overhead conductors 14.4 kv are located too close to trees and building and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | l.png | file://x:/photopub/docs/0000000527/d5b4e0c3-8763-4814-98bf-1730661c5cad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f771f32c_d939_4618_87fa_79be663c160b
ELHE-718033-2016 | HE-476430-2016 | 12/6/2016 5:10:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found high voltage overhead conductors 14.4 kv are located too close to trees and building and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | h.png | file://x:/photopub/docs/0000000527/d05237c3-04e2-46b1-934d-8e40be994c3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f771f32c_d939_4618_87fa_79be663c160b
ELIN-737570-2017 | EL-489407-2017 | 1/13/2017 12:50:47 PM | ASSESS: EL: Service Connection | png | #asFound System grounding conductor has been terminated on a lug on the panel casing and not on the neutral buss. | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | #Grounding_connection.png Service connection for new single family dwelling. The system grounding conductor has not been properly terminated in the service entrance panel. It has been terminated in the wrong place. It may not therefore, quickly clear any fault that occurs inside the dwelling possibly leading to equipment damage or failure of overcurrent devices to function. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_connection.png | file://x:/photopub/docs/0000000543/ae5f8162-4433-4d37-8a2f-3604005ba13c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc34f011_124c_4f96_bfd2_84bbf1a73e63
GAIN-738470-2017 | GA-280003-2015 | 2/20/2017 9:25:25 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Intake2.png,Intake3.png Second stage regulator 10 psi to 2 psi at building installed 2 feet away from mechanical air intake for HRV, boiler and air handler in mechanical room. In the event of over presurization of regulator gas could be introduced into the building or appliance causing a fire or explosion. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Intake2.png | file://x:/photopub/docs/0000000560/2cd359d3-be76-414d-a66e-30fe52c94691.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44f33453_3c23_4eb3_b088_8464836a3e84
GAIN-738470-2017 | GA-280003-2015 | 2/20/2017 9:25:25 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Intake2.png,Intake3.png Second stage regulator 10 psi to 2 psi at building installed 2 feet away from mechanical air intake for HRV, boiler and air handler in mechanical room. In the event of over presurization of regulator gas could be introduced into the building or appliance causing a fire or explosion. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Intake3.png | file://x:/photopub/docs/0000000560/d4ecfefd-bc2e-48c6-ac10-dda589e34aa0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44f33453_3c23_4eb3_b088_8464836a3e84
ELIN-758068-2017 | EL-477273-2016 | 2/20/2017 8:33:01 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Outdoor_receptacle.png Outdoor receptacle is exposed to weather. Cover plate is not approved to be exposed to weather. This could be a hazard over time due to water causing excessive tripping of the ground fault circuit interruptor. Over time the (GFCI) could become over used and will not function properly causing injury to person(s) or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Outdoor_receptacle.png | file://x:/photopub/docs/0000000560/0b43d918-b500-4e08-9883-ad92a636785f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd931780_16aa_479e_88f9_e5829b66d51d
ELOP-656834-2016 | 5399169 | 2/8/2017 2:21:13 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL296 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Panel_g2.png Open breaker spaces on energized panel leaving exposed electrical parts and a potential shock hazard. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Panel_g2.png | file://x:/photopub/docs/0000000555/746e350e-bf97-480f-8e2b-b008a1d1341f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__E4513131_2083_448D_BA0E_AA47D73B2153
GAIN-705974-2016 | GA-459156-2016 | 12/9/2016 2:12:46 PM | ASSESS: GA: Final | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | The distance required for a direct vent two pipe system for this furnace is not met (10ft requirement) if there was a overpressure situation inside the utilities gas pipe system, this relief vent could potentially release raw gas into the atmosphere, thus the intake piping for the furnace could potentially draw this gas inside and cause a explosion, leading to injury or property damage. | 3 | insufficient mechanical air intake clearance to gas regulator relief | Clearances.png | file://x:/photopub/docs/0000000529/4337cd9f-5695-43be-9027-a0a0e322f004.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0dcb5846_0fa5_4e05_adcf_9f230bc9e64e
GAIN-705974-2016 | GA-459156-2016 | 12/9/2016 2:12:46 PM | ASSESS: GA: Final | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | The distance required for a direct vent two pipe system for this furnace is not met (10ft requirement) if there was a overpressure situation inside the utilities gas pipe system, this relief vent could potentially release raw gas into the atmosphere, thus the intake piping for the furnace could potentially draw this gas inside and cause a explosion, leading to injury or property damage. | 3 | insufficient mechanical air intake clearance to gas regulator relief | Air_intake_clearance.png | file://x:/photopub/docs/0000000529/1091a145-ba3f-49b4-83b7-ace8168600de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0dcb5846_0fa5_4e05_adcf_9f230bc9e64e
EDIN-728394-2016 | ED-471366-2016 | 12/22/2016 5:21:43 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | The burst rating of a oil supply line of a hydraulic material lift is to have a safety factor of 10 times. It was found during a final acceptance inspection that the burst rating safety factor was not 10 times the operating pressure for full load. Not meeting the required safety will compromise the safety and integrity of material lift. This 2 stop hydraulic material lift is installed in a newly constructed cement/grout manufacturing plant. | 3 | Defects that are: Not detected by maintenance program Likely to progress | Pic_of_Underated_oil_supply_hose.png | file://x:/photopub/docs/0000000535/e2fa2f95-aa6d-463e-af0f-03974e71b527.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6b99cdf_2eee_4b0d_8165_4deeb665d844
ELIN-740354-2017 | EL-472493-2016 | 1/20/2017 6:57:18 AM | ASSESS: EL: Service Connection | png | #asFound Water present on main distribution equipment | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #detail01_main_distribution.png Permanently installed main distribution equipment for use during construction phase of installation is not protected from effects of weather. This poses a serious risk of personal injury (shock) or property damage (thermal event) due to corrosion damage and/or failure of equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | detail01_main_distribution.png | file://x:/photopub/docs/0000000545/a9b957f9-a11b-44ac-97bd-52bc60c4cb66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__859896de_6b45_4d7e_96cb_4d06c503f1c8
BPVOP-757561-2017 | UW-493640-2017 | 2/15/2017 | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_valve-2.png BP131 All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve(s). Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve-2.png | file://x:/photopub/docs/0000000557/b6a74e9e-7aca-473c-a1e0-4c2602787f9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c62ed1d_efbc_4c69_9dc2_a25f4e6596e0
ELIN-756163-2017 | EL-498729-2017 | 2/15/2017 10:55:05 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Not_weatherproofed.png Equipment is type 1 and is exposed to weather. Possibility for water egress creating shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Not_weatherproofed.png | file://x:/photopub/docs/0000000557/0bd835e6-3d7c-4cbf-a836-9adafe4935c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a8a8209_3f38_4f64_9595_30d01701cc1e
ELHE-721478-2016 | HE-478944-2016 | 11/24/2016 1:14:02 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Energized electrical panels are required to have the covers installed to guard against accidental contact of the bare, energized parts. At a new subdivision where several new dwellings where under construction by the same general contractor, electrical panel covers had been removed by non-qualified persons on energized electrical panels. At one dwelling the panel cover was partially reinstalled and at a second dwelling the panel cover was sitting on the floor. Both panels where located in garages of dwellings that did not have the doors installed and where accessible by the public. No persons where on site at the time of the assessment. The exposed buss bars of these electrical panels are a potential shock hazard for any person that comes in contact. The exposed buss bars could also create an arc flash hazard if conductive materials where to come in contact with the buss bars. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 3501_Panel_.png | file://x:/photopub/docs/0000000529/b18436dc-5464-41ae-9bb8-3f4592635ec8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad8a91dc_37cf_4cad_b51e_1adbb84d2f84
ELHE-721478-2016 | HE-478944-2016 | 11/24/2016 1:14:02 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Energized electrical panels are required to have the covers installed to guard against accidental contact of the bare, energized parts. At a new subdivision where several new dwellings where under construction by the same general contractor, electrical panel covers had been removed by non-qualified persons on energized electrical panels. At one dwelling the panel cover was partially reinstalled and at a second dwelling the panel cover was sitting on the floor. Both panels where located in garages of dwellings that did not have the doors installed and where accessible by the public. No persons where on site at the time of the assessment. The exposed buss bars of these electrical panels are a potential shock hazard for any person that comes in contact. The exposed buss bars could also create an arc flash hazard if conductive materials where to come in contact with the buss bars. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 3477_Panel_.png | file://x:/photopub/docs/0000000529/b5eb317a-4e2a-435b-abd2-2ed9e206fdbd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad8a91dc_37cf_4cad_b51e_1adbb84d2f84
ELHE-721478-2016 | HE-478944-2016 | 11/24/2016 1:14:02 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Energized electrical panels are required to have the covers installed to guard against accidental contact of the bare, energized parts. At a new subdivision where several new dwellings where under construction by the same general contractor, electrical panel covers had been removed by non-qualified persons on energized electrical panels. At one dwelling the panel cover was partially reinstalled and at a second dwelling the panel cover was sitting on the floor. Both panels where located in garages of dwellings that did not have the doors installed and where accessible by the public. No persons where on site at the time of the assessment. The exposed buss bars of these electrical panels are a potential shock hazard for any person that comes in contact. The exposed buss bars could also create an arc flash hazard if conductive materials where to come in contact with the buss bars. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 3501_Energized_Panel.png | file://x:/photopub/docs/0000000529/68772969-4f71-4a55-9e0b-800e5624e4d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad8a91dc_37cf_4cad_b51e_1adbb84d2f84
ELHE-721478-2016 | HE-478944-2016 | 11/24/2016 1:14:02 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Energized electrical panels are required to have the covers installed to guard against accidental contact of the bare, energized parts. At a new subdivision where several new dwellings where under construction by the same general contractor, electrical panel covers had been removed by non-qualified persons on energized electrical panels. At one dwelling the panel cover was partially reinstalled and at a second dwelling the panel cover was sitting on the floor. Both panels where located in garages of dwellings that did not have the doors installed and where accessible by the public. No persons where on site at the time of the assessment. The exposed buss bars of these electrical panels are a potential shock hazard for any person that comes in contact. The exposed buss bars could also create an arc flash hazard if conductive materials where to come in contact with the buss bars. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 3501_Dwelling.png | file://x:/photopub/docs/0000000529/27100622-555f-4d46-80d3-4e0e46515f81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad8a91dc_37cf_4cad_b51e_1adbb84d2f84
ELHE-721478-2016 | HE-478944-2016 | 11/24/2016 1:14:02 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Energized electrical panels are required to have the covers installed to guard against accidental contact of the bare, energized parts. At a new subdivision where several new dwellings where under construction by the same general contractor, electrical panel covers had been removed by non-qualified persons on energized electrical panels. At one dwelling the panel cover was partially reinstalled and at a second dwelling the panel cover was sitting on the floor. Both panels where located in garages of dwellings that did not have the doors installed and where accessible by the public. No persons where on site at the time of the assessment. The exposed buss bars of these electrical panels are a potential shock hazard for any person that comes in contact. The exposed buss bars could also create an arc flash hazard if conductive materials where to come in contact with the buss bars. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 3477_Front_of_Dwelling.png | file://x:/photopub/docs/0000000529/9ff733e3-cbdd-4ff1-852f-42904a68c7e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad8a91dc_37cf_4cad_b51e_1adbb84d2f84
ELIN-716341-2016 | EL-342230-2016 | 12/9/2016 11:56:37 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL152 | Installation of electrical equipment, Equipment is approved, and installation instructions have not been satisfied. | 2 | 2 |  | 2 | Installation of electrical equipment, Equipment is approved, and installation instructions have not been satisfied. | Backfed_breaker.png | file://x:/photopub/docs/0000000529/cfca3796-7e6d-497b-87d7-22b8609b8035.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a24021f4_e66a_4d40_b623_b504a37c9eb0
ELIN-716341-2016 | EL-342230-2016 | 12/9/2016 11:56:37 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL152 | Installation of electrical equipment, Equipment is approved, and installation instructions have not been satisfied. | 2 | 2 |  | 2 | Installation of electrical equipment, Equipment is approved, and installation instructions have not been satisfied. | Temp_feeder.png | file://x:/photopub/docs/0000000529/dc1d3361-61b5-4a5c-800a-73fccda2450f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a24021f4_e66a_4d40_b623_b504a37c9eb0
ELIN-716341-2016 | EL-342230-2016 | 12/9/2016 11:56:37 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL152 | Installation of electrical equipment, Equipment is approved, and installation instructions have not been satisfied. | 2 | 2 |  | 2 | Installation of electrical equipment, Equipment is approved, and installation instructions have not been satisfied. | Switchgear.png | file://x:/photopub/docs/0000000529/683128b4-0122-41fb-b4da-ee0771a20f6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a24021f4_e66a_4d40_b623_b504a37c9eb0
ELOP-725979-2016 | 4793775 | 12/19/2016 1:47:58 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | NMD 90 located in basement area is not installed in junction box. This could be a shock hazard to person(s) if they were to touch the live/hot conductor. | 0 | No Created Hazard Identified | NMD_.png | file://x:/photopub/docs/0000000533/a19574ad-8fb8-4b61-b4db-94a5e6d54898.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__19339bd8_6f91_45d1_aa37_48254b0c6eee
ELIN-735175-2017 | UW-487927-2017 | 1/6/2017 12:27:14 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Missing_panel_cover_.png The panel cover for the main section of the panel was not installed. This could result in a potential shock or fire hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Missing_panel_cover_.png | file://x:/photopub/docs/0000000540/3a25ab61-8a65-4254-919d-fcd2b7cdf277.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3c38c91_f8be_4016_8af9_a4b55a037c2a
ELIN-736540-2017 | EL-420413-2016 | 1/11/2017 2:18:04 PM | ASSESS: EL: Final | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #Energized_panel.png The panel cover of a 120/240 V panel is missing this is a possible shock hazard | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_panel.png | file://x:/photopub/docs/0000000541/a6445e5a-50f0-4650-bf9e-d38b8c0c2d6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96990fba_7419_4dcf_8857_5abcf0a137ed
ELIN-735082-2017 | EL-486612-2017 | 1/11/2017 1:27:40 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #H1.png,H2.png BX connectors inched down on nmd90. This connector is not rated for non metallic sheathed cable and over-tightening could damage the conductors and cause a fire. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | H2.png | file://x:/photopub/docs/0000000542/148b2114-ee95-4c45-b077-7950bc6d2fa2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6abed17d_b762_4e99_82b9_e71b31e09128
ELIN-735082-2017 | EL-486612-2017 | 1/11/2017 1:27:40 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #H1.png,H2.png BX connectors inched down on nmd90. This connector is not rated for non metallic sheathed cable and over-tightening could damage the conductors and cause a fire. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | H1.png | file://x:/photopub/docs/0000000542/efbafeec-aa8f-4f3d-ac00-96f2bd588c0a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6abed17d_b762_4e99_82b9_e71b31e09128
ELIN-732382-2017 | EL-478450-2016 | 1/9/2017 12:58:09 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | #Ground_plate_not_buried.png Plate type ground electrodes are required to be covered prior to connecting the service to the utility supply. This is required because in order for the ground plate to be effective at keeping electrical equipment and the ground around it at an equipotential plane the plate needs to be buried in exterior soil at a depth of 600mm. This is to intended to have sufficient moisture content and the weight of 600mm of earth on it to provide the equipotential desired. This installation of a new 125A 120/240V service for a new house under construction has the ground plate laying on top of the ground. The service is energized. Left uncorrected if an electrical fault or lightening strike occurs the electrical equipment and the ground surrounding it may be at different potentials which presents a shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_plate_not_buried.png | file://x:/photopub/docs/0000000540/87248fcd-db68-4626-91a6-ce986af695c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5779709_a61c_4be8_9b33_4d4d84763436
ELIN-726662-2016 | EL-387969-2016 | 1/9/2017 2:24:06 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | #Spare_cable_not_terminated_into_a_box_with_a_cover_.png Cables that are installed for spare branch circuits in the future must be terminated into junction boxes with covers. This is required so that the cable is safe from accidental contact if it gets energized. This installation at a new residential unit has a 2c#10 nmd90 cable in the furnace room that is not terminated into a junction boxes with a cover. The cable enters the panel but conductors are not terminated to a breaker. The other end of the cable has the conductors uncapped. Also a gas fireplace has a cable entered into a box but the box has no cover installed on it. Left uncorrected this is a potential shock and fire hazard if the conductors become energized and are contacted by persons or objects. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Spare_cable_not_terminated_into_a_box_with_a_cover_.png | file://x:/photopub/docs/0000000540/18659cd5-7c9c-4229-809a-c157daa0cf2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf0a5f14_0ff9_468b_8767_edc8e9efdd1c
ELIN-760916-2017 | EL-461723-2016 | 2/21/2017 11:31:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png Energized circuits without covers. This is a shock hazard. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | A4.png | file://x:/photopub/docs/0000000560/e158badc-d1fa-421f-90c6-3bf77c060b75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__100748d9_38c1_41e4_b7ee_8acaa6ec5d2a
ELIN-760916-2017 | EL-461723-2016 | 2/21/2017 11:31:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png Energized circuits without covers. This is a shock hazard. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | A5.png | file://x:/photopub/docs/0000000560/177f50d1-cae3-4666-8bf9-b1aa075362c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__100748d9_38c1_41e4_b7ee_8acaa6ec5d2a
ELIN-760916-2017 | EL-461723-2016 | 2/21/2017 11:31:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png Energized circuits without covers. This is a shock hazard. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | A3.png | file://x:/photopub/docs/0000000560/158841f5-27c0-468d-8d9a-8c06f3d3efec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__100748d9_38c1_41e4_b7ee_8acaa6ec5d2a
ELIN-760916-2017 | EL-461723-2016 | 2/21/2017 11:31:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png Energized circuits without covers. This is a shock hazard. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | A2.png | file://x:/photopub/docs/0000000560/9ad7f825-b2cd-40e0-b1d1-2c9ea574eecf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__100748d9_38c1_41e4_b7ee_8acaa6ec5d2a
ELIN-760916-2017 | EL-461723-2016 | 2/21/2017 11:31:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png Energized circuits without covers. This is a shock hazard. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | A6.png | file://x:/photopub/docs/0000000560/253eab17-af7b-498a-9d64-b22763d9e081.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__100748d9_38c1_41e4_b7ee_8acaa6ec5d2a
ELIN-760916-2017 | EL-461723-2016 | 2/21/2017 11:31:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png Energized circuits without covers. This is a shock hazard. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | A1.png | file://x:/photopub/docs/0000000560/e5ad3c6a-7c21-4c6b-b4a8-fe40216f8d4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__100748d9_38c1_41e4_b7ee_8acaa6ec5d2a
BPVIN-733699-2017 | UW-487204-2017 | 1/5/2017 4:06:34 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided for hot water boilers. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Remote_ESD_not_provided.png | file://x:/photopub/docs/0000000539/f31a8bf6-8680-41bd-aef4-f8ee4be71ca2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5cf95f7_9df1_49f6_8f21_727976892a66
ELIN-728681-2016 | EL-476773-2016 | 1/5/2017 2:18:55 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | AFCI breaker has not been installed for new receptacles . AFCI protection protects people and assets from a fire hazard, with out AFCI protection in place the risk is increased. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Incomplete_circuit.png | file://x:/photopub/docs/0000000539/f4179344-007e-41cf-908b-e708c2c4cae8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e86501b3_16c8_41ba_a884_9733b79d90ed
ELIN-700790-2016 | EL-465349-2016 | 1/5/2017 11:12:58 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeder terminates in a box that is located out side the trailer envelope. NMD is buried at ground surface exposing outer cable. The Cable is subject to environmental and mechanical damage. This would cause a shock hazard when break down of cable occurs. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Pre_existing_ground_rod_no_connection_.png | file://x:/photopub/docs/0000000539/ebc6dd3b-b1c9-429b-a9b1-89b486f43bd1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__539e97e1_b31f_43b0_914d_d69cb993825d
ELIN-700790-2016 | EL-465349-2016 | 1/5/2017 11:12:58 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeder terminates in a box that is located out side the trailer envelope. NMD is buried at ground surface exposing outer cable. The Cable is subject to environmental and mechanical damage. This would cause a shock hazard when break down of cable occurs. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | NMD_feeder_outside_.png | file://x:/photopub/docs/0000000539/146fce21-2f2e-407f-b7a9-dc3186b0fea5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__539e97e1_b31f_43b0_914d_d69cb993825d
ELIN-700790-2016 | EL-465349-2016 | 1/5/2017 11:12:58 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeder terminates in a box that is located out side the trailer envelope. NMD is buried at ground surface exposing outer cable. The Cable is subject to environmental and mechanical damage. This would cause a shock hazard when break down of cable occurs. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Exterior_door_with_out_luminaire.png | file://x:/photopub/docs/0000000539/e7526d47-ea56-4c32-9097-91d1c78d3cdc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__539e97e1_b31f_43b0_914d_d69cb993825d
BPVIN-412750-2015 | BPV-254314-2015 | 1/31/2017 10:40:39 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Disconnect_switch__.png,Boiler_switch_.png A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected when required. I found that there was no lockout system provided on the disconnect switches. Potential exists for an incident due to system becoming energized while work is being carried out. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Disconnect_switch__.png | file://x:/photopub/docs/0000000550/584a02b4-76a1-42bf-9bb3-7405843a8245.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7712e2ae_5542_4078_bef6_19fa4575be4e
GAIN-754657-2017 | GA-384765-2016 | 2/14/2017 10:27:44 AM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | #Sent3.png Fuel leak on fitting supplying on demand water heater. Risk of fire if a source of ignition was present. Fire and or explosion hazard under ideal conditions. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Sent3.png | file://x:/photopub/docs/0000000557/7cf38323-1d4e-41fb-832a-998ce50ae8d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8207f1f_2558_48f4_936a_4e4e25131e6f
ELIN-726719-2016 | UW-483302-2016 | 12/19/2016 12:56:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Devices such as receptacles and switches are required to have device covers plates to protect against accidental contact of the energized terminals of the devices. In the basement of an existing hotel, in the mechanical and electrical rooms, several of the devices and oulet boxes did not have cover plates. The exposed terminals on the devices are a potential shock hazard for any persons that may come in contact with the energized equipment. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outlets.png | file://x:/photopub/docs/0000000533/213b7814-6808-4afc-8602-aaa714632084.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e657dd1_cc4b_4593_be64_2d6440352b71
ELIN-726719-2016 | UW-483302-2016 | 12/19/2016 12:56:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Devices such as receptacles and switches are required to have device covers plates to protect against accidental contact of the energized terminals of the devices. In the basement of an existing hotel, in the mechanical and electrical rooms, several of the devices and oulet boxes did not have cover plates. The exposed terminals on the devices are a potential shock hazard for any persons that may come in contact with the energized equipment. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Switch.png | file://x:/photopub/docs/0000000533/d0fa7013-630d-487f-a12f-1564b67fecc2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e657dd1_cc4b_4593_be64_2d6440352b71
ELIN-726719-2016 | UW-483302-2016 | 12/19/2016 12:56:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Devices such as receptacles and switches are required to have device covers plates to protect against accidental contact of the energized terminals of the devices. In the basement of an existing hotel, in the mechanical and electrical rooms, several of the devices and oulet boxes did not have cover plates. The exposed terminals on the devices are a potential shock hazard for any persons that may come in contact with the energized equipment. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_switch_box_.png | file://x:/photopub/docs/0000000533/f4d4947c-182b-4e7c-b656-753f05ef8bb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e657dd1_cc4b_4593_be64_2d6440352b71
ELIN-726719-2016 | UW-483302-2016 | 12/19/2016 12:56:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Devices such as receptacles and switches are required to have device covers plates to protect against accidental contact of the energized terminals of the devices. In the basement of an existing hotel, in the mechanical and electrical rooms, several of the devices and oulet boxes did not have cover plates. The exposed terminals on the devices are a potential shock hazard for any persons that may come in contact with the energized equipment. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Junction_box.png | file://x:/photopub/docs/0000000533/b34a2a5b-4769-41a2-9320-c7bcb04a5c1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e657dd1_cc4b_4593_be64_2d6440352b71
BPOP-670524-2016 | BPV-405839-2015 | 12/12/2016 10:42:43 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Overgrown vegetation surrounding tank preventing proper inspection of outer shell, fire hazard as well, in event of fire readily combustible materials around tank and relief valve | 3 | Clearance to combustibles not maintained | Jameson.png | file://x:/photopub/docs/0000000534/98197ac3-8170-477d-89b6-1d84a644b186.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79dfb8da_8cd0_45fd_a6c0_54530257fdec
BPOP-670524-2016 | BPV-405839-2015 | 12/12/2016 10:42:43 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Overgrown vegetation surrounding tank preventing proper inspection of outer shell, fire hazard as well, in event of fire readily combustible materials around tank and relief valve | 3 | Clearance to combustibles not maintained | Jameson2.png | file://x:/photopub/docs/0000000534/47df3173-d1e6-48c4-8c9b-6bb820ef5c12.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79dfb8da_8cd0_45fd_a6c0_54530257fdec
BPVIN-716504-2016 | BPV-416170-2016 | 12/2/2016 10:06:39 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Hot Water Supply Boiler with Heating Surface (HS) of 5.5 square meters, Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_room_without_emergency_shutdown_switch_at_boiler_room_door.png | file://x:/photopub/docs/0000000529/d7b9f6a1-fcd5-4d64-8b0e-541ffc07a274.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6a8ec6b_8150_40f8_bdc2_df6841c42aa6
ELHE-730319-2016 | HE-485228-2016 | 12/29/2016 9:12:13 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | The 200 amp 120/240 volt distribution panel located in the bed and breakfast living room area is missing a breaker filler plate exposing possible contact by unauthorized persons, this is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Main_distribution_panel.png | file://x:/photopub/docs/0000000536/b60260f1-14a4-4ba1-a546-d78d45069478.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a493f94_4eaf_4760_9c5f_afdceaff8a47
PROP-599993-2016 | PR-323701-2015 | 12/14/2016 5:04:16 PM | ASSESS: PR OP: RAP | png | #asFound | PR040 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Loose wires at tail of splice, cutting hazard if not removed or protected | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Splice_wires_exposed.png | file://x:/photopub/docs/0000000533/7d437919-0884-41d6-8e5c-71dbe1a2f5db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__CD07ED3F_EA8C_45F3_BB2E_A319AEF8CDFE
ELIN-728681-2016 | EL-476773-2016 | 1/5/2017 2:18:55 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | AFCI breaker has not been installed for new receptacles . AFCI protection protects people and assets from a fire hazard, with out AFCI protection in place the risk is increased. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Exterior_device_incomplete_.png | file://x:/photopub/docs/0000000539/2c312182-09f9-4bed-93b6-df33127ce0b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e86501b3_16c8_41ba_a884_9733b79d90ed
ELIN-700790-2016 | EL-465349-2016 | 1/5/2017 11:12:58 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeder terminates in a box that is located out side the trailer envelope. NMD is buried at ground surface exposing outer cable. The Cable is subject to environmental and mechanical damage. This would cause a shock hazard when break down of cable occurs. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Unsupported_feeder.png | file://x:/photopub/docs/0000000539/673a1705-1df7-4608-a869-f879da0d1d59.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__539e97e1_b31f_43b0_914d_d69cb993825d
ELIN-700790-2016 | EL-465349-2016 | 1/5/2017 11:12:58 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeder terminates in a box that is located out side the trailer envelope. NMD is buried at ground surface exposing outer cable. The Cable is subject to environmental and mechanical damage. This would cause a shock hazard when break down of cable occurs. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Box_with_broken_hinge_.png | file://x:/photopub/docs/0000000539/b53b6768-1cc6-453b-aed8-516953a5fabc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__539e97e1_b31f_43b0_914d_d69cb993825d
ELIN-728681-2016 | EL-476773-2016 | 1/5/2017 2:18:55 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | AFCI breaker has not been installed for new receptacles . AFCI protection protects people and assets from a fire hazard, with out AFCI protection in place the risk is increased. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | AFCI_required.png | file://x:/photopub/docs/0000000539/a9ba0ca3-d863-4774-bf27-b7a81d070f19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e86501b3_16c8_41ba_a884_9733b79d90ed
GAIN-732511-2017 | GA-392847-2016 | 1/5/2017 1:05:12 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | Furnace manufactures instructions indicate the ductwork must extend out of the furnace room to protect Furnace from negative pressure. During operation when the Furnace is subject to negative pressure the potential for products of combustion to be circulated into the occupied space can occur if this happens the occupants would be breathing products of combustion and could become ill. | 3 | Appliance not installed according to installation instructions | 26055_0_ave_.png | file://x:/photopub/docs/0000000539/1370e9e3-353a-49e6-8251-2816fc00b4b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c50cc70_19f7_40f8_9726_bc498fbfa046
ELIN-756669-2017 | EL-500001-2017 | 2/22/2017 3:22:15 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Doors locked, keys turned over to general contractor. | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_panel_with_no_interior_cover_1.png,Energized_panel_with_no_interior_cover_2.png,Energized_panel_with_no_interior_cover_3.png,Energized_panel_with_no_interior_cover_4.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. During an assessment of a commercial building undergoing a tenant improvement, an energized 200 amp 120/208 volt electrical panel was found with the hinged panel door unlocked and no interior cover over the breakers. No qualified workers where on site at the time of the assessment. With the panel door open, there is a potential shock hazard for any person that makes accidental contact with with the energized bus bars or exposed energized conductors inside the panel. There is also a potential arc fault hazard if metal was to come in accidental contact with the energized bus bars or conductors inside the panel. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_panel_with_no_interior_cover_4.png | file://x:/photopub/docs/0000000561/e54c9841-ac2a-45a0-acd6-743068d93c14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfef69bb_38dc_49ee_a321_679e87d547d3
ELIN-754312-2017 | EL-484679-2016 | 2/22/2017 11:42:02 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_GFCI_receptacles1.png,No_GFCI_receptacles2.png Ground-fault circuit interrupters (GFCI's) are required to be installed for outlets within 1.5m of a sink. GFCI's monitor the current flowing in a circuit and will open the circuit if the GFCI senses a difference of 5 mA. This prevents dangerous levels of current from flowing through a person if they where holding a faulty appliance and made contact with water in a sink. In this installation at a duplex family dwelling, GFCI protection was not provided for the receptacles in the basement washroom and laundry room that are within 1.5m of the sinks. This is a potential shock hazard for persons working with cord connected equipment near these sinks in this residence. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | No_GFCI_receptacles2.png | file://x:/photopub/docs/0000000561/f18f5a6f-d38c-4374-b76f-5f7de3807507.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ea80877_e662_4012_a7d8_5e2fc6763dc9
ELIN-761487-2017 | UW-469753-2016 | 2/22/2017 10:36:32 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_GFCI_Receptacles1.png,No_GFCI_Receptacles2.png Ground-fault circuit interrupters (GFCI's) are required to be installed for outlets within 1.5m of a sink. GFCI's monitor the current flowing in a circuit and will open the circuit if the GFCI senses a difference of 5 mA. This prevents dangerous levels of current from flowing through a person if they where holding a faulty appliance and made contact with water in a sink. In this installation at a duplex family dwelling, GFCI protection was not provided for the receptacles in the basement washroom and laundry room that are within 1.5m of the sinks. This is a potential shock hazard for persons working with cord connected equipment near these sinks in this residence. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | No_GFCI_Receptacles1.png | file://x:/photopub/docs/0000000561/3eefed23-0c99-4ad5-9413-5b14362650e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07eba72c_584f_4b27_a65e_1f18fc6a3fc3
ELIN-756669-2017 | EL-500001-2017 | 2/22/2017 3:22:15 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_panel_with_no_interior_cover_1.png,Energized_panel_with_no_interior_cover_2.png,Energized_panel_with_no_interior_cover_3.png,Energized_panel_with_no_interior_cover_4.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. During an assessment of a commercial building undergoing a tenant improvement, an energized 200 amp 120/208 volt electrical panel was found with the hinged panel door unlocked and no interior cover over the breakers. No qualified workers where on site at the time of the assessment. With the panel door open, there is a potential shock hazard for any person that makes accidental contact with with the energized bus bars or exposed energized conductors inside the panel. There is also a potential arc fault hazard if metal was to come in accidental contact with the energized bus bars or conductors inside the panel. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_panel_with_no_interior_cover_1.png | file://x:/photopub/docs/0000000561/9612f0b8-bc20-4a92-a12f-5aa50124ee8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfef69bb_38dc_49ee_a321_679e87d547d3
ELIN-761487-2017 | UW-469753-2016 | 2/22/2017 10:36:32 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_GFCI_Receptacles1.png,No_GFCI_Receptacles2.png Ground-fault circuit interrupters (GFCI's) are required to be installed for outlets within 1.5m of a sink. GFCI's monitor the current flowing in a circuit and will open the circuit if the GFCI senses a difference of 5 mA. This prevents dangerous levels of current from flowing through a person if they where holding a faulty appliance and made contact with water in a sink. In this installation at a duplex family dwelling, GFCI protection was not provided for the receptacles in the basement washroom and laundry room that are within 1.5m of the sinks. This is a potential shock hazard for persons working with cord connected equipment near these sinks in this residence. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | No_GFCI_Receptacles2.png | file://x:/photopub/docs/0000000561/2284ce37-b4d3-4b87-aa9d-4080873ced11.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07eba72c_584f_4b27_a65e_1f18fc6a3fc3
ELIN-756669-2017 | EL-500001-2017 | 2/22/2017 3:22:15 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_panel_with_no_interior_cover_1.png,Energized_panel_with_no_interior_cover_2.png,Energized_panel_with_no_interior_cover_3.png,Energized_panel_with_no_interior_cover_4.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. During an assessment of a commercial building undergoing a tenant improvement, an energized 200 amp 120/208 volt electrical panel was found with the hinged panel door unlocked and no interior cover over the breakers. No qualified workers where on site at the time of the assessment. With the panel door open, there is a potential shock hazard for any person that makes accidental contact with with the energized bus bars or exposed energized conductors inside the panel. There is also a potential arc fault hazard if metal was to come in accidental contact with the energized bus bars or conductors inside the panel. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_panel_with_no_interior_cover_3.png | file://x:/photopub/docs/0000000561/b287ae12-d718-45bb-9105-85bfbc98131a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfef69bb_38dc_49ee_a321_679e87d547d3
BPVIN-681972-2016 | BPV-385115-2016 | 1/13/2017 8:29:30 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP001 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | 5 | 5 | #Safety_Valve.png The pressure relief valve installed on each boiler is set to relieve at a pressure that is "higher" than the maximum allowable working pressure of the boiler. The boiler maybe subjected to over pressurization and lead to a serious failure. The installed safety valve is set at 45 psi and the boiler maximum allowable working pressure is 30 psi. | 5 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | Safety_Valve.png | file://x:/photopub/docs/0000000543/cb6ea935-fc90-4356-91b4-e36ccba27796.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23e77498_89a3_4799_9994_2c0bccb387b0
GAIN-744059-2017 | GA-482821-2016 | 1/24/2017 11:18:55 AM | ASSESS: GA: Final | png | #asFound | GA147 | Incorrect use of safety controls (Example: bypass limit) | 4 | 4 | #By-passed_air_switch.png The as found hazard is a by-passed air pressure safety switch within the air handling unit. This creates a hazard as the system can no longer shut down when the air characteristics change which can lead to poor combustion and create harmful products of combustion being introduced into an occupied space. | 4 | Incorrect use of safety controls (Example: bypass limit) | By-passed_air_switch.png | file://x:/photopub/docs/0000000547/7a7e4b7e-d7af-4872-b0ce-8300427f0680.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c40810f_ec4b_49c6_927d_445d3d061488
ELIN-733513-2017 | EL-474089-2016 | 1/5/2017 2:30:57 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Unapproved pole for permanent service to dwelling unit | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 6x6_post.png | file://x:/photopub/docs/0000000539/0c89e576-f970-4647-9c2e-1035f0ef2985.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1743f090_350d_4062_8c02_1882077cb1c8
ELIN-754312-2017 | EL-484679-2016 | 2/22/2017 11:42:02 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_GFCI_receptacles1.png,No_GFCI_receptacles2.png Ground-fault circuit interrupters (GFCI's) are required to be installed for outlets within 1.5m of a sink. GFCI's monitor the current flowing in a circuit and will open the circuit if the GFCI senses a difference of 5 mA. This prevents dangerous levels of current from flowing through a person if they where holding a faulty appliance and made contact with water in a sink. In this installation at a duplex family dwelling, GFCI protection was not provided for the receptacles in the basement washroom and laundry room that are within 1.5m of the sinks. This is a potential shock hazard for persons working with cord connected equipment near these sinks in this residence. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | No_GFCI_receptacles1.png | file://x:/photopub/docs/0000000561/71ffcc46-59f0-486e-a9bd-7ea0ce08dcd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ea80877_e662_4012_a7d8_5e2fc6763dc9
ELIN-756669-2017 | EL-500001-2017 | 2/22/2017 3:22:15 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_panel_with_no_interior_cover_1.png,Energized_panel_with_no_interior_cover_2.png,Energized_panel_with_no_interior_cover_3.png,Energized_panel_with_no_interior_cover_4.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. During an assessment of a commercial building undergoing a tenant improvement, an energized 200 amp 120/208 volt electrical panel was found with the hinged panel door unlocked and no interior cover over the breakers. No qualified workers where on site at the time of the assessment. With the panel door open, there is a potential shock hazard for any person that makes accidental contact with with the energized bus bars or exposed energized conductors inside the panel. There is also a potential arc fault hazard if metal was to come in accidental contact with the energized bus bars or conductors inside the panel. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_panel_with_no_interior_cover_2.png | file://x:/photopub/docs/0000000561/3124ffed-d23f-4a61-ab6f-4a980855ba9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfef69bb_38dc_49ee_a321_679e87d547d3
ELIN-722345-2016 | EL-479904-2016 | 12/14/2016 1:25:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Bubble covers on temporary construction receptacles have fallen off. Likelihood of water and snow penetrating electrical equipment add shorting the circuit to ground. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Bubble_covers__bubble_covers_missing_from_temporary_construction_receptacles.png | file://x:/photopub/docs/0000000531/febbe749-98b8-4384-a294-6e4806be5b27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c57b8624_53c6_4596_9b44_a990f6d98ff4
ELIN-725550-2016 | EL-482228-2016 | 12/20/2016 1:16:37 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | No ground bushing on service raceway. This is a fire hazard as lock rings have been found to over heat during ground fault conditions. | 3 | Continuity Bonding; method for equipment is not adequate. | 2.png | file://x:/photopub/docs/0000000533/b9e21120-5e0e-41d4-9952-aa38cb698d9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6d289de_a155_4daf_a382_7233683ab6f7
ELIN-725186-2016 | EL-190775-2014 | 12/20/2016 2:22:25 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Missing cover plate on 240 volt receptacle. This is a shock hazard as an individual could come into contact with the energized parts of the receptacle. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 8.png | file://x:/photopub/docs/0000000533/55d2469e-4d1c-4914-ab96-3bbfa045ce04.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30af6d29_d2e9_4636_9780_00893ba3be40
ELIN-725550-2016 | EL-482228-2016 | 12/20/2016 1:16:37 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | No ground bushing on service raceway. This is a fire hazard as lock rings have been found to over heat during ground fault conditions. | 3 | Continuity Bonding; method for equipment is not adequate. | 3.png | file://x:/photopub/docs/0000000533/f4d87f38-7324-4f2a-b03a-126e4f6532b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6d289de_a155_4daf_a382_7233683ab6f7
ELIN-725186-2016 | EL-190775-2014 | 12/20/2016 2:22:25 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Missing cover plate on 240 volt receptacle. This is a shock hazard as an individual could come into contact with the energized parts of the receptacle. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 5.png | file://x:/photopub/docs/0000000533/6040a43e-032f-45ed-aee5-bc8bacc80243.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30af6d29_d2e9_4636_9780_00893ba3be40
ELIN-725186-2016 | EL-190775-2014 | 12/20/2016 2:22:25 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Missing cover plate on 240 volt receptacle. This is a shock hazard as an individual could come into contact with the energized parts of the receptacle. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 9.png | file://x:/photopub/docs/0000000533/39f989d5-fcaa-4e6c-98e1-395e80f60b5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30af6d29_d2e9_4636_9780_00893ba3be40
ELIN-725186-2016 | EL-190775-2014 | 12/20/2016 2:22:25 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Missing cover plate on 240 volt receptacle. This is a shock hazard as an individual could come into contact with the energized parts of the receptacle. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 10.png | file://x:/photopub/docs/0000000533/6903ee22-7a07-456f-801a-9863df3e4323.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30af6d29_d2e9_4636_9780_00893ba3be40
ELIN-725550-2016 | EL-482228-2016 | 12/20/2016 1:16:37 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | No ground bushing on service raceway. This is a fire hazard as lock rings have been found to over heat during ground fault conditions. | 3 | Continuity Bonding; method for equipment is not adequate. | 1.png | file://x:/photopub/docs/0000000533/a9a4767a-fba0-4bfc-a845-9e69a0216738.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6d289de_a155_4daf_a382_7233683ab6f7
ELIN-725186-2016 | EL-190775-2014 | 12/20/2016 2:22:25 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Missing cover plate on 240 volt receptacle. This is a shock hazard as an individual could come into contact with the energized parts of the receptacle. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 6.png | file://x:/photopub/docs/0000000533/5911e251-30bd-4759-9018-984493a96309.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30af6d29_d2e9_4636_9780_00893ba3be40
ELIN-726138-2016 | EL-431111-2016 | 12/20/2016 3:13:15 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacle outlet installed above base board heater. Manufacturers instructions state that base board heaters are not to be installed under receptacles. This is a fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | F.png | file://x:/photopub/docs/0000000533/7da91d6e-545a-4130-bb5c-8ed415fa076e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ac6a852_01f4_46cc_b438_cfd9ba813699
ELIN-725186-2016 | EL-190775-2014 | 12/20/2016 2:22:25 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Missing cover plate on 240 volt receptacle. This is a shock hazard as an individual could come into contact with the energized parts of the receptacle. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 7.png | file://x:/photopub/docs/0000000533/4c86f0a0-b96a-4de6-baf1-c9c462e969bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30af6d29_d2e9_4636_9780_00893ba3be40
ELIN-725312-2016 | EL-345404-2016 | 12/20/2016 10:26:16 AM | ASSESS: EL: Final | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 2 | Unused openings in panels require approved fillers. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | A.png | file://x:/photopub/docs/0000000533/6b74571a-3ae0-4390-bd5e-91e137c140b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b27334e_ad2f_4bcc_a4dd_cf3506397acc
ELIN-719559-2016 | EL-426317-2016 | 12/13/2016 11:35:20 AM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Conductors used for Service are under sized for main distribution. Without a load calculation performed and proven the hazard could be the overloading of the conductors causing a thermal effect. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | No_ground_bushing.png | file://x:/photopub/docs/0000000531/941f420e-bec2-406f-aa18-d4936671f68b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3a38be2_1548_473d_a092_e5169480bf22
ELIN-719559-2016 | EL-426317-2016 | 12/13/2016 11:35:20 AM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Conductors used for Service are under sized for main distribution. Without a load calculation performed and proven the hazard could be the overloading of the conductors causing a thermal effect. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | LB_in_wall.png | file://x:/photopub/docs/0000000531/fd5a47a6-fcad-40c5-a516-b53461364aca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3a38be2_1548_473d_a092_e5169480bf22
ELIN-740079-2017 | EL-491679-2017 | 1/18/2017 3:40:14 PM | ASSESS: EL: Final | png | #asFound | EL179 | General Construction Indoor: Inadequate spacing from walls for transformer. | 4 | 4 | #A.png 600 V dry type transformer installed in a dwelling adjacent to combustible material. This is a fire hazard as the transformer could heat up the adjacent material and cause a fire. A minimum of 300 mm clearance is required. | 4 | General Construction Indoor: Inadequate spacing from walls for transformer. | A.png | file://x:/photopub/docs/0000000545/06e0ac54-c9e9-4746-80c6-fbaee34b82db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b82ede89_1a66_4fb0_9b73_51ae46f3461c
ELOP-738799-2017 | EL-018145-2013 | 1/13/2017 8:41:02 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL190 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 3 | #Oil_relief_valve.png 500 KVA 25KV/14.4KV to 120/208V Distribution Transformer shows visible signs of failure, without transformer testing to confirm where and how the transformer failed it is unsafe to use. Failure of transformer poses potential of equipment damage to other associated components and cabling. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | Oil_relief_valve.png | file://x:/photopub/docs/0000000543/9d529e20-f700-4f91-a3e3-d792668af8da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3153605_065a_4241_8a27_25c785d8f579
ELIN-746011-2017 | EL-491084-2017 | 1/30/2017 1:25:55 PM | ASSESS: EL: Final | png | #asFound | EL056 | Protection and control Overcurrent protection for transformer has not been provided, or is not properly rated | 3 | 3 | #Distribution.png Existing distribution is not code compliant; transformers and load centres are not adequately protected. This is a possible fire hazard. | 3 | Protection and control Overcurrent protection for transformer has not been provided, or is not properly rated | Distribution.png | file://x:/photopub/docs/0000000550/c0136fe1-3341-4b8a-94e7-63ba847a7efd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5004af04_f05b_4a56_88ad_f0605036f643
ELIN-748023-2017 | EL-403195-2016 | 1/31/2017 2:20:41 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Microwave_Branch_Breaker1.png,Microwave_Branch_Breaker2.png The 15 amp 120 volt receptacle provided for the microwave has not been AFCI protected. This could pose a fire hazard or possible damage to the electrical equipment. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Microwave_Branch_Breaker2.png | file://x:/photopub/docs/0000000550/fcb99396-f361-4d7a-a85f-42bc286afc98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b98d7827_46cd_4022_8818_e3cbe5ea6733
ELIN-748023-2017 | EL-403195-2016 | 1/31/2017 2:20:41 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Microwave_Branch_Breaker1.png,Microwave_Branch_Breaker2.png The 15 amp 120 volt receptacle provided for the microwave has not been AFCI protected. This could pose a fire hazard or possible damage to the electrical equipment. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Microwave_Branch_Breaker1.png | file://x:/photopub/docs/0000000550/a627b6b0-80ee-4335-8c5a-fc783e120337.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b98d7827_46cd_4022_8818_e3cbe5ea6733
ELHE-749090-2017 | HE-496794-2017 | 2/1/2017 11:27:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_conductors_connected_to_an_attachment_plug_for_a_light_fixture_1.png,Open_energized_conductors_connected_to_an_attachment_plug_for_a_light_fixture_2.png,Open_energized_conductors_connected_to_an_attachment_plug_for_a_light_fixture_3.png Branch circuit wiring is required to be contained inside of electrical boxes or equipment. Cord connected electrical equipment is required to be provided with proper receptacles for connection of the equipment. This is required to prevent open energized conductors and connections from being energized and exposed to accidental contact from persons, objects, or adjacent electrical components. This installation on a rural residential property had open energized 15A 120V conductors connected to the blades of an attachment cord of a portable light fixture. The conductors were energized and exposed to contact which posed a shock hazard and in close proximity to each other which caused a fire hazard. Left uncorrected this installation posed an immediate shock and fire | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_conductors_connected_to_an_attachment_plug_for_a_light_fixture_1.png | file://x:/photopub/docs/0000000553/17a545ea-c5ae-4d08-872d-d3321b6b3ff2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__282f0eda_a7f0_4773_9db0_57b12fcd4b0d
ELIN-733007-2017 | EL-486841-2017 | 1/5/2017 10:36:59 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables in concealed spaces are subject to mechanical damage | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable-3.png | file://x:/photopub/docs/0000000539/d023743b-4b31-4a17-aa59-4de34840a19a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe557bf7_f80c_4dcd_905e_8ebcb8dd7533
ELIN-733007-2017 | EL-486841-2017 | 1/5/2017 10:36:59 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables in concealed spaces are subject to mechanical damage | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable-6.png | file://x:/photopub/docs/0000000539/6ba99e36-1229-4561-82ae-794e951b13ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe557bf7_f80c_4dcd_905e_8ebcb8dd7533
ELIN-733007-2017 | EL-486841-2017 | 1/5/2017 10:36:59 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables in concealed spaces are subject to mechanical damage | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable-4.png | file://x:/photopub/docs/0000000539/762ff875-9899-4e0e-a0f3-4f42435a8f88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe557bf7_f80c_4dcd_905e_8ebcb8dd7533
ELIN-733007-2017 | EL-486841-2017 | 1/5/2017 10:36:59 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables in concealed spaces are subject to mechanical damage | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable-1.png | file://x:/photopub/docs/0000000539/1c6eedb3-7522-4c20-8c71-f980402e12be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe557bf7_f80c_4dcd_905e_8ebcb8dd7533
ELIN-733007-2017 | EL-486841-2017 | 1/5/2017 10:36:59 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables in concealed spaces are subject to mechanical damage | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable-5.png | file://x:/photopub/docs/0000000539/a2ea3964-3efe-43ad-96ae-83936e78bd2c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe557bf7_f80c_4dcd_905e_8ebcb8dd7533
ELHE-749090-2017 | HE-496794-2017 | 2/1/2017 11:27:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_conductors_connected_to_an_attachment_plug_for_a_light_fixture_1.png,Open_energized_conductors_connected_to_an_attachment_plug_for_a_light_fixture_2.png,Open_energized_conductors_connected_to_an_attachment_plug_for_a_light_fixture_3.png Branch circuit wiring is required to be contained inside of electrical boxes or equipment. Cord connected electrical equipment is required to be provided with proper receptacles for connection of the equipment. This is required to prevent open energized conductors and connections from being energized and exposed to accidental contact from persons, objects, or adjacent electrical components. This installation on a rural residential property had open energized 15A 120V conductors connected to the blades of an attachment cord of a portable light fixture. The conductors were energized and exposed to contact which posed a shock hazard and in close proximity to each other which caused a fire hazard. Left uncorrected this installation posed an immediate shock and fire | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_conductors_connected_to_an_attachment_plug_for_a_light_fixture_3.png | file://x:/photopub/docs/0000000553/84e995b5-b5b6-47b3-a668-8ada12008272.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__282f0eda_a7f0_4773_9db0_57b12fcd4b0d
ELIN-751718-2017 | UW-498416-2017 | 2/6/2017 8:03:08 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Walk_in_cooler1.png,Walk_in_cooler2.png,Walk_in_cooler3.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. During an unpermited work assessment in a commercial building, an energized 30 amp 208 volt compressor for a walk-in cooler was found with the no cover installed over the electrical contactor. The exposed, energized terminals on the contactor are a potential shock hazard for any persons that make contact with the terminal. There is also a potential for an arc fault hazard to persons or a fire hazard to the structure if conductive material was to come in contact with the exposed, energized terminals. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Walk_in_cooler2.png | file://x:/photopub/docs/0000000554/33b5959d-3045-44ed-8d4f-f2de01319b33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__152f6d64_e6ae_47bf_8a14_f6285ec1b8b3
ELIN-718884-2016 | UW-477276-2016 | 12/7/2016 8:16:03 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | No hazard identified. | 0 | No Created Hazard Identified | Estimate.png | file://x:/photopub/docs/0000000528/194cb9a8-aee5-49aa-b54e-02ff7223bb14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd1cece8_98ef_46f6_8e89_855fe1df2ae3
ELIN-718884-2016 | UW-477276-2016 | 12/7/2016 8:16:03 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | No hazard identified. | 0 | No Created Hazard Identified | Lights.png | file://x:/photopub/docs/0000000528/2b56e1bf-d469-45ac-94c8-647b4dae07be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd1cece8_98ef_46f6_8e89_855fe1df2ae3
ELIN-718884-2016 | UW-477276-2016 | 12/7/2016 8:16:03 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | No hazard identified. | 0 | No Created Hazard Identified | Main.png | file://x:/photopub/docs/0000000528/9835a1be-3152-4f0e-ac86-647029b173d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd1cece8_98ef_46f6_8e89_855fe1df2ae3
GAIN-712765-2016 | GA-455569-2016 | 12/7/2016 9:11:40 AM | ASSESS: GA: Final | png | #asFound | GA039 | Painting of exterior piping | 1 | 1 |  | 1 | Painting of exterior piping | Meter_piping_1.png | file://x:/photopub/docs/0000000527/3a80bda8-6ecd-41d1-9fef-c6f2f44f7e29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fd84078_2d13_4c09_a33a_cebc832671fb
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C4.png | file://x:/photopub/docs/0000000540/eec8b3a7-ddf7-4ef3-a84a-f13b2d244dba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Suite310.png | file://x:/photopub/docs/0000000540/901b2925-fe53-4c94-a2cb-30d7d61b9440.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733337-2017 | EL-486852-2017 | 1/6/2017 12:49:01 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cable may get damaged and cause fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C-4.png | file://x:/photopub/docs/0000000540/82fc8484-337b-456a-8387-9cbb3c6dd8a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a20306b_ddfe_41f6_b16a_812e85e4b49a
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C13.png | file://x:/photopub/docs/0000000540/3e62d228-e835-4082-853a-980ba5a7c06a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C10.png | file://x:/photopub/docs/0000000540/589dc984-a10d-4703-885c-cb788fcc586c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C7.png | file://x:/photopub/docs/0000000540/ddc48057-fe45-4770-be72-c28e03339de8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C3.png | file://x:/photopub/docs/0000000540/9b58c185-9318-425f-8f9e-7e68670d5b05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733337-2017 | EL-486852-2017 | 1/6/2017 12:49:01 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cable may get damaged and cause fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C-1.png | file://x:/photopub/docs/0000000540/e43325ef-ff61-46e9-bf9b-25177f796e95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a20306b_ddfe_41f6_b16a_812e85e4b49a
ELIN-733337-2017 | EL-486852-2017 | 1/6/2017 12:49:01 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cable may get damaged and cause fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C-3.png | file://x:/photopub/docs/0000000540/ed84774e-0b09-4c53-91ac-85b868dc13ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a20306b_ddfe_41f6_b16a_812e85e4b49a
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C1.png | file://x:/photopub/docs/0000000540/28aa6170-09db-40c7-b7ae-7d9086ded8af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C14.png | file://x:/photopub/docs/0000000540/5e2d349c-0037-42ac-b53d-d9d2439ef411.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C5.png | file://x:/photopub/docs/0000000540/bd870466-be84-4bbd-869b-5bced18f3af6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Suite105.png | file://x:/photopub/docs/0000000540/e931e721-73b5-4a77-be67-0671e47288b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
GAWP-739457-2017 | GA-280003-2015 | 1/16/2017 4:52:06 PM | ASSESS: GA Work In Progress | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 4 | #Alkali_first_stage1.png,Alkali_first_stage2.png First stage regulator not installed on piping system, propane tank pressure entering second stage regulator at building at time of inspection 55 PSIG, cold day, regulator rated for 10 PSIG. This could prevent over pressurization of the second stage regulator causing full relief and gas escaping to the atmosphere or building. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Alkali_first_stage1.png | file://x:/photopub/docs/0000000543/1b1150e6-5893-4dff-83ae-ac42100e93c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53371f59_351f_4f2a_88b6_354a59be23eb
GAWP-739457-2017 | GA-280003-2015 | 1/16/2017 4:52:06 PM | ASSESS: GA Work In Progress | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 4 | #Alkali_first_stage1.png,Alkali_first_stage2.png First stage regulator not installed on piping system, propane tank pressure entering second stage regulator at building at time of inspection 55 PSIG, cold day, regulator rated for 10 PSIG. This could prevent over pressurization of the second stage regulator causing full relief and gas escaping to the atmosphere or building. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Alkali_first_stage2.png | file://x:/photopub/docs/0000000543/f4c8b155-1fbf-4211-973a-13410cd6c6ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53371f59_351f_4f2a_88b6_354a59be23eb
ELIN-746991-2017 | EL-385932-2016 | 1/31/2017 10:42:47 AM | ASSESS: EL: Service Connection | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Mainpanel.png The 100 amp panel is fed from a temporary panel and the cover is off. The main bus is energized and could be a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Mainpanel.png | file://x:/photopub/docs/0000000551/50bdd03c-7aff-49a7-ad41-c1fe8773e8cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2b6d119_43cb_4c4e_b2e6_bb78026f07b4
EDIN-699631-2016 | ED-457925-2016 | 12/3/2016 6:52:55 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | The emergency 2-way emergency communication in the elevator is a means of communication to a 24 hours/day monitored station. During an acceptance inspection it was found the 2-way emergency communication was not functioning properly because the monitoring station was not able to tell us our location. Without a properly functioning 2-way emergency communication in the elevator it may be difficult to get help in case of an entrapment in the elevator. This may result in a serious situation if panic sets in or if a person had a medical emergency and was trapped in the elevator. This is a 4 stop MRL traction elevator located in a newly constructed commercial building. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | Elevator_emergency_communication.png | file://x:/photopub/docs/0000000525/2440058d-57de-4339-a6a1-8dba1db20790.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce1f7064_d83d_47f6_9b98_9c7b038dbc40
ELIN-733007-2017 | EL-486841-2017 | 1/5/2017 10:36:59 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables in concealed spaces are subject to mechanical damage | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable-2.png | file://x:/photopub/docs/0000000539/a1e771c4-f175-43a1-9476-81a72483bdb4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe557bf7_f80c_4dcd_905e_8ebcb8dd7533
ELIN-751718-2017 | UW-498416-2017 | 2/6/2017 8:03:08 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Walk_in_cooler1.png,Walk_in_cooler2.png,Walk_in_cooler3.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. During an unpermited work assessment in a commercial building, an energized 30 amp 208 volt compressor for a walk-in cooler was found with the no cover installed over the electrical contactor. The exposed, energized terminals on the contactor are a potential shock hazard for any persons that make contact with the terminal. There is also a potential for an arc fault hazard to persons or a fire hazard to the structure if conductive material was to come in contact with the exposed, energized terminals. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Walk_in_cooler3.png | file://x:/photopub/docs/0000000554/1a9b880b-48bb-49d9-8430-21f8d0c1aa11.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__152f6d64_e6ae_47bf_8a14_f6285ec1b8b3
ELIN-751718-2017 | UW-498416-2017 | 2/6/2017 8:03:08 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Walk_in_cooler1.png,Walk_in_cooler2.png,Walk_in_cooler3.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. During an unpermited work assessment in a commercial building, an energized 30 amp 208 volt compressor for a walk-in cooler was found with the no cover installed over the electrical contactor. The exposed, energized terminals on the contactor are a potential shock hazard for any persons that make contact with the terminal. There is also a potential for an arc fault hazard to persons or a fire hazard to the structure if conductive material was to come in contact with the exposed, energized terminals. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Walk_in_cooler1.png | file://x:/photopub/docs/0000000554/1dbe3d73-4930-49b5-9680-880ceacb1af3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__152f6d64_e6ae_47bf_8a14_f6285ec1b8b3
ELIN-751533-2017 | EL-496343-2017 | 2/6/2017 3:38:39 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Receptacle_.png Energized 15 amp 120 volt wiring, receptacles, junction boxes and light fixtures have exposed components that pose a shock hazard to persons and have not been guarded from accidental contact. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Receptacle_.png | file://x:/photopub/docs/0000000554/5f8fff41-7a89-42b7-a01c-152c526879e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__38dc8a6e_6cf1_414f_a330_82f45da2548f
ELOP-709281-2016 | 5380601 | 11/30/2016 7:56:14 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | 120V 15A light fixtures are hanging from the outlet box exposing the energized terminals on the back of the fixture, this poses a shock hazard to person working around these lights. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Lamp_holder.png | file://x:/photopub/docs/0000000525/718a9d92-f41f-4904-b12d-de225b66ee6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df10a38e_aee7_47e6_9050_3ad3d1491fd0
ELIN-752763-2017 | EL-498697-2017 | 2/9/2017 10:59:23 AM | ASSESS: EL: Service Connection | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 4 | #5.png Overhead mast is not properly bonded to ground. This is a shock hazard. Overhead mast is not properly supported. This is a shock and fire hazard. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 5.png | file://x:/photopub/docs/0000000556/5f621ed2-583d-4392-aa72-270a66b26e41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2e9e5f3_c7de_47dc_96ce_c0134c4c5829
ELIN-752764-2017 | EL-498697-2017 | 2/9/2017 11:40:56 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #D1.png,D2.png Over head mast is not properly supported. Code requires three straps. This is a shock hazard. Over head mast is not mechanically continuously bonded to ground. This a shock and fire hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | D1.png | file://x:/photopub/docs/0000000556/9648426b-ee74-4d8f-9641-aab2839140c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dce3bfdb_950f_489b_a778_1df3a3870934
ELIN-752764-2017 | EL-498697-2017 | 2/9/2017 11:40:56 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #D1.png,D2.png Over head mast is not properly supported. Code requires three straps. This is a shock hazard. Over head mast is not mechanically continuously bonded to ground. This a shock and fire hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | D2.png | file://x:/photopub/docs/0000000556/5039eba3-14e9-4205-978c-526b94168784.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dce3bfdb_950f_489b_a778_1df3a3870934
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C12.png | file://x:/photopub/docs/0000000540/82e4519d-a202-4836-bdab-de57c76e97e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Suite305.png | file://x:/photopub/docs/0000000540/19e56476-28eb-4bb7-90b6-465a4052b97f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733337-2017 | EL-486852-2017 | 1/6/2017 12:49:01 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cable may get damaged and cause fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C-2.png | file://x:/photopub/docs/0000000540/b6e5b77b-a020-474c-904e-884db5796294.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a20306b_ddfe_41f6_b16a_812e85e4b49a
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C9.png | file://x:/photopub/docs/0000000540/6616c39a-275e-49c0-ad47-2dbfee40b27c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Suite306.png | file://x:/photopub/docs/0000000540/ca4f1a7a-ce63-4095-b035-19c0127e6abc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C2.png | file://x:/photopub/docs/0000000540/b88c231f-9c8f-4668-b68e-cee92fcf5c91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733337-2017 | EL-486852-2017 | 1/6/2017 12:49:01 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cable may get damaged and cause fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | SuiteA305.png | file://x:/photopub/docs/0000000540/4ffa9548-cb2f-4d29-8682-e10804f393d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a20306b_ddfe_41f6_b16a_812e85e4b49a
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Suite102.png | file://x:/photopub/docs/0000000540/cc457911-050c-4539-b7fb-3b5df75d6432.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C8.png | file://x:/photopub/docs/0000000540/770dbff3-f24e-4271-bc30-56024766c526.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C11.png | file://x:/photopub/docs/0000000540/ab4d2494-6b1b-4e55-9698-441745b9d7d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-733339-2017 | EL-486850-2017 | 1/6/2017 10:57:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Unprotected cables are subject to mechanical damage and creating fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Suite303.png | file://x:/photopub/docs/0000000540/86d90bdf-94d2-4443-96a2-3d1bcd0e666c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925164c3_01ea_4480_8477_4042088825c9
ELIN-714929-2016 | EL-474327-2016 | 12/5/2016 11:02:50 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | Receptacle installed in back of kitchen cupboard for the intended use of under cabinet lighting. No pernament appliance would be in front of receptacle. Person could reach for a glass or similar and grab electrical live electrical fittings. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Cupboard_recep.png | file://x:/photopub/docs/0000000526/51c9a773-6455-4656-9a2c-0d6608be5444.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7535692b_f66d_47ce_8774_e55d15ef44b1
ELIN-727388-2016 | UW-483705-2016 | 12/21/2016 2:52:38 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | Connection to hot water tank is subject to mechanical damage creating a shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Hot_water_tank_connection.png | file://x:/photopub/docs/0000000534/1d309a4d-8a3c-4401-99a6-6a53501af836.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5864cd4_e0db_4d82_ab87_0693cbce0c98
ELOP-732519-2017 | EL-024679-2013 | 1/6/2017 11:31:07 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Open breaker spaces leave energized electrical parts accessible creating a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Open_breaker_spaces.png | file://x:/photopub/docs/0000000540/225f5bfa-32d3-4ada-97b9-f140dc5ef064.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e688a59a_414d_4ba0_82f0_a654e8592553
GAUP-732715-2017 | UW-486676-2017 | 1/6/2017 1:48:11 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA045 | Gas connector passes through wall, floor, ceiling, partition or into appliance | 2 | 2 | Gas connector passes through appliance case. If the connector rubs against the case it may cause a hole in the connector causing a gas leak in the building. | 2 | Gas connector passes through wall, floor, ceiling, partition or into appliance | Gas_connector.png | file://x:/photopub/docs/0000000540/6c7852a5-db7b-47c0-9ebd-47f4bc80dbd8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46aee4bc_8af0_4efe_ad69_f9a134c40f30
GAHE-742115-2017 | HE-468765-2016 | 1/28/2017 8:28:30 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | #Isc_farm.png ISC (emergency shut off) on the liquid piping found in the open position, propane dispenser unattended and cabinet door was closed. The ISC (emergency shut off) is to be orientated so it cannot be left in the open position when door is closed and left unattended in the event of piping or equipment failure, liquid propane to be shut a source to prevent escaping liquid propane which could cause a fire or explosion if source of ignition is present. | 4 | Missing mandatory safety controls | Isc_farm.png | file://x:/photopub/docs/0000000549/7a92296c-93bb-44b4-a240-f92692c4059c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62346edb_2cc2_4fd0_b1df_e6aa1fc4ac9b
ELOP-714509-2016 | EL-458849-2016 | 12/6/2016 2:40:22 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 | A receptacle and conduit are not supported properly and will soon fall of the wall and could become a shock hazard if damaged. | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | rec_damage.png | file://x:/photopub/docs/0000000528/aba50dab-7f25-470b-a3eb-bd582bc9213c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__226C6EAF_D19E_4638_9336_8210DCA66406
ELOP-714511-2016 | EL-458854-2016 | 12/8/2016 4:03:10 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | There are receptacles and panel covers with uncovered openings. This exposes live conductors to possible contact resulting in personal injury due to shock. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Rec_damage.png | file://x:/photopub/docs/0000000528/05f946b3-960d-46d7-9701-441370b7d150.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__636F35BD_488C_4E96_A2AB_F0539897A775
ELOP-714510-2016 | EL-458853-2016 | 12/7/2016 7:37:56 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | A Westinghouse three phase panel is missing hole fillers and has open breaker slots, this is a shock hazard to persons and with evidence of mice, inside the distribution room, a fault could occur as they nest inside the panel. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | West_panel.png | file://x:/photopub/docs/0000000528/4176cd1c-12e1-4a74-b54a-6a47c6981581.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83E1FBB8_4AB4_406C_B270_0817F5FC9BE1
ELIN-740365-2017 | EL-475536-2016 | 1/19/2017 6:20:03 AM | ASSESS: EL: Service Connection | png | #asFound Sub-distribution exposed to effects of weather | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #View01_service1.png,View01_service2.png,View01_service3.png,View01_service4.png Permanent service equipment exposed to effects of weather during construction phase of installation. This poses a serious risk of personal injury (shock) or property damage (thermal event) due to failure of damaged equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | View01_service1.png | file://x:/photopub/docs/0000000545/91212ce2-8c43-4d79-b193-872a931c23b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b214fd9_7834_4b75_ac47_e2d2fdaa23ad
ELIN-740365-2017 | EL-475536-2016 | 1/19/2017 6:20:03 AM | ASSESS: EL: Service Connection | png | #asFound Water on equipment. | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #View01_service1.png,View01_service2.png,View01_service3.png,View01_service4.png Permanent service equipment exposed to effects of weather during construction phase of installation. This poses a serious risk of personal injury (shock) or property damage (thermal event) due to failure of damaged equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | View01_service2.png | file://x:/photopub/docs/0000000545/81fd4f60-241e-48da-adbb-d33627dbb5a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b214fd9_7834_4b75_ac47_e2d2fdaa23ad
ELHE-757992-2017 | HE-501595-2017 | 2/15/2017 9:07:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 4 | #Water_ingress1.png,Water_ingress2.png,Water_ingress3.png,Water_ingress4.png,Water_ingress5.png,Water_ingress6.png,Water_ingress7.png Water ingress and pooling in and around the main incoming service switch gear rated at 12,470 Volt creating a potential shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Water_ingress1.png | file://x:/photopub/docs/0000000558/28c11cc0-52dc-4797-b914-1e9e152b0653.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45c9f64e_4d6d_4ab1_bc85_67076c64eeb6
ELIN-757987-2017 | UW-501523-2017 | 2/10/2017 9:11:45 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Transformer21.png,Transformer22.png,Transformer23.png Armoured cable feeder without box, cover, fittings at the end of the cable creating a potential shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Transformer22.png | file://x:/photopub/docs/0000000558/433559f7-64b5-4dfc-8c63-bc4d23824e5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b332d65a_3759_4812_a342_9ad637f379d0
ELOP-748359-2017 | 1653 | 2/15/2017 2:08:02 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Emergency_lighting_failed1.png,Emergency_lighting_failed2.png Emergency lighting equipment has failed as indicated on testing tag. Inadequate lighting in the event of an emergency or power outage would prevent safe agrees from the building. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Emergency_lighting_failed2.png | file://x:/photopub/docs/0000000558/aad713d1-8473-4a84-99ee-cb3726e5fc6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d9d428b_1e5c_4c57_a850_32cb44d23981
ELHE-757992-2017 | HE-501595-2017 | 2/15/2017 9:07:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 4 | #Water_ingress1.png,Water_ingress2.png,Water_ingress3.png,Water_ingress4.png,Water_ingress5.png,Water_ingress6.png,Water_ingress7.png Water ingress and pooling in and around the main incoming service switch gear rated at 12,470 Volt creating a potential shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Water_ingress6.png | file://x:/photopub/docs/0000000558/eaa3c200-95b0-4b78-86b6-0f83c7d41993.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45c9f64e_4d6d_4ab1_bc85_67076c64eeb6
ELHE-757992-2017 | HE-501595-2017 | 2/15/2017 9:07:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 4 | #Water_ingress1.png,Water_ingress2.png,Water_ingress3.png,Water_ingress4.png,Water_ingress5.png,Water_ingress6.png,Water_ingress7.png Water ingress and pooling in and around the main incoming service switch gear rated at 12,470 Volt creating a potential shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Water_ingress7.png | file://x:/photopub/docs/0000000558/fafa3c6f-b01b-4b95-a938-942870286d6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45c9f64e_4d6d_4ab1_bc85_67076c64eeb6
ELHE-757992-2017 | HE-501595-2017 | 2/15/2017 9:07:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 4 | #Water_ingress1.png,Water_ingress2.png,Water_ingress3.png,Water_ingress4.png,Water_ingress5.png,Water_ingress6.png,Water_ingress7.png Water ingress and pooling in and around the main incoming service switch gear rated at 12,470 Volt creating a potential shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Water_ingress4.png | file://x:/photopub/docs/0000000558/1129082d-5151-4526-8ab2-c30672f315fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45c9f64e_4d6d_4ab1_bc85_67076c64eeb6
ELIN-757987-2017 | UW-501523-2017 | 2/10/2017 9:11:45 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Transformer21.png,Transformer22.png,Transformer23.png Armoured cable feeder without box, cover, fittings at the end of the cable creating a potential shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Transformer23.png | file://x:/photopub/docs/0000000558/bbfdd16a-efa5-437b-a191-6cbfaa68c63d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b332d65a_3759_4812_a342_9ad637f379d0
ELHE-757992-2017 | HE-501595-2017 | 2/15/2017 9:07:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 4 | #Water_ingress1.png,Water_ingress2.png,Water_ingress3.png,Water_ingress4.png,Water_ingress5.png,Water_ingress6.png,Water_ingress7.png Water ingress and pooling in and around the main incoming service switch gear rated at 12,470 Volt creating a potential shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Water_ingress3.png | file://x:/photopub/docs/0000000558/a514675a-9bb5-493b-8d43-d8a2e54c23c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45c9f64e_4d6d_4ab1_bc85_67076c64eeb6
ELOP-748359-2017 | 1653 | 2/15/2017 2:08:02 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Emergency_lighting_failed1.png,Emergency_lighting_failed2.png Emergency lighting equipment has failed as indicated on testing tag. Inadequate lighting in the event of an emergency or power outage would prevent safe agrees from the building. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Emergency_lighting_failed1.png | file://x:/photopub/docs/0000000558/4a83e44e-576f-41b3-a40f-8be33bab321d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d9d428b_1e5c_4c57_a850_32cb44d23981
ELHE-757992-2017 | HE-501595-2017 | 2/15/2017 9:07:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 4 | #Water_ingress1.png,Water_ingress2.png,Water_ingress3.png,Water_ingress4.png,Water_ingress5.png,Water_ingress6.png,Water_ingress7.png Water ingress and pooling in and around the main incoming service switch gear rated at 12,470 Volt creating a potential shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Water_ingress2.png | file://x:/photopub/docs/0000000558/44791a6b-4bc2-44c6-a71b-aeec714bc3b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45c9f64e_4d6d_4ab1_bc85_67076c64eeb6
ELHE-757992-2017 | HE-501595-2017 | 2/15/2017 9:07:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 4 | #Water_ingress1.png,Water_ingress2.png,Water_ingress3.png,Water_ingress4.png,Water_ingress5.png,Water_ingress6.png,Water_ingress7.png Water ingress and pooling in and around the main incoming service switch gear rated at 12,470 Volt creating a potential shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Water_ingress5.png | file://x:/photopub/docs/0000000558/8d1dd69f-570b-4b06-8588-3f6ed01bd01a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45c9f64e_4d6d_4ab1_bc85_67076c64eeb6
GAIN-731119-2016 | GA-456084-2016 | 1/31/2017 4:11:23 PM | ASSESS: GA: Final | png | #asFound Copper tubing installed in a return air plenum | GA054 | Code prohibited practices or materials | 3 | 3 | #Return_air.png The hazard is natural gas piping installed in a return air of ventilation system, if a gas leak developed natural gas would enter the ventilation system. | 3 | Code prohibited practices or materials | Return_air.png | file://x:/photopub/docs/0000000554/e1ffe78a-7515-469b-b919-e62e93da14d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb03e46b_c0b2_41c5_9103_dd3868971545
GAIN-738583-2017 | GA-334196-2016 | 1/13/2017 1:41:10 PM | ASSESS: GA: Final | png | #asFound | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 5 | #Reg_relief1.png,Reg_relief2.png Relief style regulator installed inside building without piping from relief to outside. On failure of regulator gas will escape into building causing possible explosion | 5 | Relief style regulator/device allowed to vent within building/confined space | Reg_relief1.png | file://x:/photopub/docs/0000000543/c7232baf-36fd-4a45-81ed-d8eecdc1fde2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceebf2e7_599d_4b99_a13e_660b7bbe4817
GAIN-738583-2017 | GA-334196-2016 | 1/13/2017 1:41:10 PM | ASSESS: GA: Final | png | #asFound | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 5 | #Reg_relief1.png,Reg_relief2.png Relief style regulator installed inside building without piping from relief to outside. On failure of regulator gas will escape into building causing possible explosion | 5 | Relief style regulator/device allowed to vent within building/confined space | Reg_relief2.png | file://x:/photopub/docs/0000000543/c7c9ceb3-743e-4d1d-b178-a8663242eeb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceebf2e7_599d_4b99_a13e_660b7bbe4817
ELIN-740670-2017 | EL-466214-2016 | 1/19/2017 9:39:49 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | #Grounding1.png,Grounding2.png Grounding electrode and conductor not properly buried or supported. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding2.png | file://x:/photopub/docs/0000000545/6f3aeb33-37ce-4635-9253-ee5dff262139.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81de20a4_2ac1_4eb3_be05_e351e34d351a
ELIN-740365-2017 | EL-475536-2016 | 1/19/2017 6:20:03 AM | ASSESS: EL: Service Connection | png | #asFound Equipment not protected from effects of weather. | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #View01_service1.png,View01_service2.png,View01_service3.png,View01_service4.png Permanent service equipment exposed to effects of weather during construction phase of installation. This poses a serious risk of personal injury (shock) or property damage (thermal event) due to failure of damaged equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | View01_service4.png | file://x:/photopub/docs/0000000545/f8831bfb-9921-4d26-a5b1-932d4d4c9444.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b214fd9_7834_4b75_ac47_e2d2fdaa23ad
ELIN-740365-2017 | EL-475536-2016 | 1/19/2017 6:20:03 AM | ASSESS: EL: Service Connection | png | #asFound Water on equipment | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #View01_service1.png,View01_service2.png,View01_service3.png,View01_service4.png Permanent service equipment exposed to effects of weather during construction phase of installation. This poses a serious risk of personal injury (shock) or property damage (thermal event) due to failure of damaged equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | View01_service3.png | file://x:/photopub/docs/0000000545/d3d4b24e-dca9-482b-8d8a-e6190be0b69d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b214fd9_7834_4b75_ac47_e2d2fdaa23ad
683253-2016 | EL-297547-2015 | 11/28/2016 11:04:44 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Found an approved 3 pole 4 wire 600 volt 400 amp rated 3 phase "GENERAL DUTY SWITCH" installed for use as a residential consumer's service connected to a utility power supply system that is rated as 120/240 volt 1 phase system. Consumer's service equipment is not approved for the use as installed for connection to utility supply system. When electrical equipment is not approved for the use and is not installed as required for the approved safe operation of equipment the installation could possibly be an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 2.png | file://x:/photopub/docs/0000000526/80b6722b-4c4f-4622-ad15-da471a9cb143.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bae2359_3c07_4f91_a434_6490f11c86fe
683253-2016 | EL-297547-2015 | 11/28/2016 11:04:44 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Found an approved 3 pole 4 wire 600 volt 400 amp rated 3 phase "GENERAL DUTY SWITCH" installed for use as a residential consumer's service connected to a utility power supply system that is rated as 120/240 volt 1 phase system. Consumer's service equipment is not approved for the use as installed for connection to utility supply system. When electrical equipment is not approved for the use and is not installed as required for the approved safe operation of equipment the installation could possibly be an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 3.png | file://x:/photopub/docs/0000000526/589ea951-2484-4656-951f-0b077e2facb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bae2359_3c07_4f91_a434_6490f11c86fe
683253-2016 | EL-297547-2015 | 11/28/2016 11:04:44 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Found an approved 3 pole 4 wire 600 volt 400 amp rated 3 phase "GENERAL DUTY SWITCH" installed for use as a residential consumer's service connected to a utility power supply system that is rated as 120/240 volt 1 phase system. Consumer's service equipment is not approved for the use as installed for connection to utility supply system. When electrical equipment is not approved for the use and is not installed as required for the approved safe operation of equipment the installation could possibly be an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 7.png | file://x:/photopub/docs/0000000526/c85170b5-8c04-42ed-be16-c83811d9ffd2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bae2359_3c07_4f91_a434_6490f11c86fe
683253-2016 | EL-297547-2015 | 11/28/2016 11:04:44 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Found an approved 3 pole 4 wire 600 volt 400 amp rated 3 phase "GENERAL DUTY SWITCH" installed for use as a residential consumer's service connected to a utility power supply system that is rated as 120/240 volt 1 phase system. Consumer's service equipment is not approved for the use as installed for connection to utility supply system. When electrical equipment is not approved for the use and is not installed as required for the approved safe operation of equipment the installation could possibly be an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4.png | file://x:/photopub/docs/0000000526/10dc50fb-5716-40bb-ac07-01323cf89640.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bae2359_3c07_4f91_a434_6490f11c86fe
683253-2016 | EL-297547-2015 | 11/28/2016 11:04:44 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Found an approved 3 pole 4 wire 600 volt 400 amp rated 3 phase "GENERAL DUTY SWITCH" installed for use as a residential consumer's service connected to a utility power supply system that is rated as 120/240 volt 1 phase system. Consumer's service equipment is not approved for the use as installed for connection to utility supply system. When electrical equipment is not approved for the use and is not installed as required for the approved safe operation of equipment the installation could possibly be an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 9.png | file://x:/photopub/docs/0000000526/fad86467-26dd-4942-ae11-f5c3eaee930c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bae2359_3c07_4f91_a434_6490f11c86fe
683253-2016 | EL-297547-2015 | 11/28/2016 11:04:44 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Found an approved 3 pole 4 wire 600 volt 400 amp rated 3 phase "GENERAL DUTY SWITCH" installed for use as a residential consumer's service connected to a utility power supply system that is rated as 120/240 volt 1 phase system. Consumer's service equipment is not approved for the use as installed for connection to utility supply system. When electrical equipment is not approved for the use and is not installed as required for the approved safe operation of equipment the installation could possibly be an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 5.png | file://x:/photopub/docs/0000000526/5f61b5c3-dc3b-400b-a3ae-9dfa1517bd28.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bae2359_3c07_4f91_a434_6490f11c86fe
683253-2016 | EL-297547-2015 | 11/28/2016 11:04:44 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Found an approved 3 pole 4 wire 600 volt 400 amp rated 3 phase "GENERAL DUTY SWITCH" installed for use as a residential consumer's service connected to a utility power supply system that is rated as 120/240 volt 1 phase system. Consumer's service equipment is not approved for the use as installed for connection to utility supply system. When electrical equipment is not approved for the use and is not installed as required for the approved safe operation of equipment the installation could possibly be an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 10.png | file://x:/photopub/docs/0000000526/f82179af-d9b3-4098-9f2a-6152465237d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bae2359_3c07_4f91_a434_6490f11c86fe
683253-2016 | EL-297547-2015 | 11/28/2016 11:04:44 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Found an approved 3 pole 4 wire 600 volt 400 amp rated 3 phase "GENERAL DUTY SWITCH" installed for use as a residential consumer's service connected to a utility power supply system that is rated as 120/240 volt 1 phase system. Consumer's service equipment is not approved for the use as installed for connection to utility supply system. When electrical equipment is not approved for the use and is not installed as required for the approved safe operation of equipment the installation could possibly be an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 6.png | file://x:/photopub/docs/0000000526/2619a705-c9b8-49d8-bb6e-d557fc15205d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bae2359_3c07_4f91_a434_6490f11c86fe
683253-2016 | EL-297547-2015 | 11/28/2016 11:04:44 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Found an approved 3 pole 4 wire 600 volt 400 amp rated 3 phase "GENERAL DUTY SWITCH" installed for use as a residential consumer's service connected to a utility power supply system that is rated as 120/240 volt 1 phase system. Consumer's service equipment is not approved for the use as installed for connection to utility supply system. When electrical equipment is not approved for the use and is not installed as required for the approved safe operation of equipment the installation could possibly be an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 11.png | file://x:/photopub/docs/0000000526/17517071-396f-43ba-9168-774a2ad50d3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bae2359_3c07_4f91_a434_6490f11c86fe
683253-2016 | EL-297547-2015 | 11/28/2016 11:04:44 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Found an approved 3 pole 4 wire 600 volt 400 amp rated 3 phase "GENERAL DUTY SWITCH" installed for use as a residential consumer's service connected to a utility power supply system that is rated as 120/240 volt 1 phase system. Consumer's service equipment is not approved for the use as installed for connection to utility supply system. When electrical equipment is not approved for the use and is not installed as required for the approved safe operation of equipment the installation could possibly be an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 1.png | file://x:/photopub/docs/0000000526/68392a84-b540-43e6-a1e3-49a40323ca69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bae2359_3c07_4f91_a434_6490f11c86fe
683253-2016 | EL-297547-2015 | 11/28/2016 11:04:44 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Found an approved 3 pole 4 wire 600 volt 400 amp rated 3 phase "GENERAL DUTY SWITCH" installed for use as a residential consumer's service connected to a utility power supply system that is rated as 120/240 volt 1 phase system. Consumer's service equipment is not approved for the use as installed for connection to utility supply system. When electrical equipment is not approved for the use and is not installed as required for the approved safe operation of equipment the installation could possibly be an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 8.png | file://x:/photopub/docs/0000000526/a47105b1-1386-4d14-8344-d92ab2a91e20.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bae2359_3c07_4f91_a434_6490f11c86fe
ELIN-728358-2016 | EL-446432-2016 | 12/22/2016 10:02:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | Service connection for new single-family dwelling. The system grounding conductor has been installed outside the framed wall below the service entrance panel. Therefore, it is susceptible to mechanical damage as it is not protected leaving the concrete floor. The result could be severing of the system and grounding conductor and loss of the system ground. Overcurrent devices then may not function as intended on a fault. Shock and fire hazard. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Grounding_conductor.png | file://x:/photopub/docs/0000000534/f8926643-5c8d-4b73-a508-737c62cb8e8c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b3d1fef_bcb3_4ad5_8af3_0dc729640672
ELIN-739328-2017 | EL-477199-2016 | 1/17/2017 12:23:43 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Panel cover missing in both upper and lower floor suites. | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Panel_cover_missing_.png Rough wire of single family dwelling being converted to two suites. Panel covers are not installed so that live parts are exposed and are a shock hazard. Service was upgraded and is energized. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel_cover_missing_.png | file://x:/photopub/docs/0000000544/830c097b-1238-4da2-83b2-abecdd2e9e03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf38ff7b_9fb0_4721_918d_2b8664f27050
ELIN-740670-2017 | EL-466214-2016 | 1/19/2017 9:39:49 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | #Grounding1.png,Grounding2.png Grounding electrode and conductor not properly buried or supported. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding1.png | file://x:/photopub/docs/0000000545/5c471475-dd6d-4e95-ab46-d8b5ce5d192a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81de20a4_2ac1_4eb3_be05_e351e34d351a
ELIN-742838-2017 | EL-423104-2016 | 1/20/2017 2:50:50 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Consumer_cable_1.png,Consumer_cable_2.png | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Consumer_cable_2.png | file://x:/photopub/docs/0000000546/d65a67ff-523a-4d09-a6ce-144e1a09d5fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2ede438_4730_468c_9144_8940566e53fd
ELIN-742838-2017 | EL-423104-2016 | 1/20/2017 2:50:50 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Consumer_cable_1.png,Consumer_cable_2.png | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Consumer_cable_1.png | file://x:/photopub/docs/0000000546/d6aa5bd9-0915-4093-a12f-ce77ce026e4c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2ede438_4730_468c_9144_8940566e53fd
GAIN-737095-2017 | GA-279930-2015 | 1/11/2017 1:49:27 PM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | #Furnace_vent_termination.png Furnace air intake terminates too close to the exhaust outlet. | 2 | Side wall vent termination not compliant with installation instructions | Furnace_vent_termination.png | file://x:/photopub/docs/0000000542/0c1fd71b-32c3-4fc4-9fe3-fe19a9544bfe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ee0478e_81ef_4d2b_89d3_a945b61e02f6
GAIN-737095-2017 | GA-279930-2015 | 1/11/2017 1:49:27 PM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | #Furnace_vent_termination.png Furnace air intake terminates too close to the exhaust outlet. | 2 | Side wall vent termination not compliant with installation instructions | Furnace_vent_termination.png | file://x:/photopub/docs/0000000542/70920f86-fa54-4324-81d4-765214fe965e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ee0478e_81ef_4d2b_89d3_a945b61e02f6
ELHE-732625-2017 | HE-467243-2016 | 12/20/2016 5:06:58 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found 120/208 volt 800 amp rated service and distribution electrical equipment is damaged due to water entering the building electrical room. When electrical equipment becomes damaged, the equipment may not operate effectively or properly and is not rated or designed for the use that the equipment was originally approved for. Damaged electrical equipment could become an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 3.png | file://x:/photopub/docs/0000000538/f5fe66b8-6bc4-49b8-962c-27fd0244685c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3d451bd_1e19_47d2_b184_de600437fc48
ELHE-732625-2017 | HE-467243-2016 | 12/20/2016 5:06:58 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found 120/208 volt 800 amp rated service and distribution electrical equipment is damaged due to water entering the building electrical room. When electrical equipment becomes damaged, the equipment may not operate effectively or properly and is not rated or designed for the use that the equipment was originally approved for. Damaged electrical equipment could become an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 5.png | file://x:/photopub/docs/0000000538/e4f36c08-83a4-4b62-bf43-bb5179c22958.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3d451bd_1e19_47d2_b184_de600437fc48
ELHE-732625-2017 | HE-467243-2016 | 12/20/2016 5:06:58 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found 120/208 volt 800 amp rated service and distribution electrical equipment is damaged due to water entering the building electrical room. When electrical equipment becomes damaged, the equipment may not operate effectively or properly and is not rated or designed for the use that the equipment was originally approved for. Damaged electrical equipment could become an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 2.png | file://x:/photopub/docs/0000000538/08dad938-9250-41d3-90dc-5bf0a52dcf59.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3d451bd_1e19_47d2_b184_de600437fc48
ELHE-732625-2017 | HE-467243-2016 | 12/20/2016 5:06:58 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found 120/208 volt 800 amp rated service and distribution electrical equipment is damaged due to water entering the building electrical room. When electrical equipment becomes damaged, the equipment may not operate effectively or properly and is not rated or designed for the use that the equipment was originally approved for. Damaged electrical equipment could become an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 6.png | file://x:/photopub/docs/0000000538/554bec56-c72e-4feb-a93a-fb79bf62ee48.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3d451bd_1e19_47d2_b184_de600437fc48
ELHE-732625-2017 | HE-467243-2016 | 12/20/2016 5:06:58 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Found 120/208 volt 800 amp rated service and distribution electrical equipment is damaged due to water entering the building electrical room. When electrical equipment becomes damaged, the equipment may not operate effectively or properly and is not rated or designed for the use that the equipment was originally approved for. Damaged electrical equipment could become an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4.png | file://x:/photopub/docs/0000000538/2ce97e9c-281b-4fc0-b4e9-b4bce6263eb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3d451bd_1e19_47d2_b184_de600437fc48
ELOP-716380-2016 | 5374344 | 12/5/2016 1:57:02 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Water is dripping on the floor in front of the switchgear and splashing on the front causing oxidization. This presents a shock hazard as well as damage to regulated electrical equipment. | 3 | General Equipment is not approved for the specific use | Drip_point.png | file://x:/photopub/docs/0000000527/646fc307-600d-4a52-a1bc-2ab9ca98e741.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__319f4352_37fe_431b_81ce_df9292843d05
ELOP-716380-2016 | 5374344 | 12/5/2016 1:57:02 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Water is dripping on the floor in front of the switchgear and splashing on the front causing oxidization. This presents a shock hazard as well as damage to regulated electrical equipment. | 3 | General Equipment is not approved for the specific use | Water_damage.png | file://x:/photopub/docs/0000000527/2d0de484-f82e-4bcf-aa42-0ff4a5274ef0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__319f4352_37fe_431b_81ce_df9292843d05
ELIN-757543-2017 | UW-329633-2015 | 2/15/2017 1:27:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | #Bent_mast.png Service Mast has been damaged by bending from unknown causes. The hazard is the conductors may be compromised causing a thermal effect. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Bent_mast.png | file://x:/photopub/docs/0000000558/81d0fcdd-9d7f-4b13-9b38-b19f90552123.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d36cc8ee_5613_46eb_9707_dd48f8eba789
GAIN-708125-2016 | GA-444750-2016 | 12/2/2016 8:57:42 AM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | Filter rack installed inside of down flow furnace. Filter could get drawn into fan housing due to lack of maintenance. Possible overheating condition or cycling on high temperature switch. | 3 | Appliance not installed according to installation instructions | Brooks.png | file://x:/photopub/docs/0000000525/b9d556d4-8950-4ecf-92fa-843116ef09f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0df1beb9_914e_4e21_b236_2f71d1f46c34
ELIN-741459-2017 | EL-491971-2017 | 1/25/2017 10:37:06 AM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | #One_receptacle_for_counter.png The receptacles for the kitchen counter are not adequately spaced. The is could result in the use of extension cords creating a thermal hazard. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | One_receptacle_for_counter.png | file://x:/photopub/docs/0000000549/0667c360-6065-4ca9-a88a-3dd58d89be38.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcf143a8_3653_4625_bf3f_51d16e5c1c9c
ELOP-653876-2016 | 6426 | 12/5/2016 10:34:02 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | Approximately 3 inches of standing water on the floor directly in front of the distribution center. Upon routine operation of the electrical equipment handles or troubleshooting there would be a shock hazard. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Distribution_center.png | file://x:/photopub/docs/0000000526/83963d3e-1e61-4794-9894-ac0e2790de90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2D975614_49A8_4CC2_9240_C59B02F0B4D1
ELOP-653876-2016 | 6426 | 12/5/2016 10:34:02 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | Approximately 3 inches of standing water on the floor directly in front of the distribution center. Upon routine operation of the electrical equipment handles or troubleshooting there would be a shock hazard. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Distr_2.png | file://x:/photopub/docs/0000000526/2fa39987-3867-4a37-885f-6e6d86cf9657.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2D975614_49A8_4CC2_9240_C59B02F0B4D1
PROP-715798-2016 | PR-469872-2016 | 12/9/2016 8:20:56 AM | ASSESS: PR OP: Annual | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Tag line was not installed, carriage could fall if chainfall failed | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Tag_line_on_tensioning_at_drive.png | file://x:/photopub/docs/0000000528/7ac13cee-039f-4275-bfc8-c404f08c2f46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d42ff8cf_4314_4bad_89e5_f6bf7e1cad17
ELIN-747318-2017 | EL-495906-2017 | 1/30/2017 12:33:38 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Thermostat box says do not contain a raceway to the floor for the heating panel sets. | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | #Thermostat.png Rough wire of the new single family dwelling. Bathroom thermostat boxes for in floor heating do not include a raceway to mechanically protect the connections to the heating pad at the floor. Possible mechanical damage which could result in fire if the leads are damaged. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Thermostat.png | file://x:/photopub/docs/0000000550/4e9327a5-16f0-4d13-8333-0d3602337822.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d83d611b_f11a_4f7a_b88f_b205611747ba
BPVIN-724181-2016 | BPV-461766-2016 | 11/8/2016 5:46:30 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Safety relief valve will not function properly. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Relief_valve_installation.png | file://x:/photopub/docs/0000000531/7d9c0c58-d9c3-4317-95d6-c682e8cc03d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96d1f207_e378_430e_9287_82b80cd1532e
ELIN-736055-2017 | EL-327248-2015 | 1/26/2017 10:16:34 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Incomplete_receptacle_.png Home owner has requested final prematurely, completion was not done and circuits were not complete. If energized would be hazardous to occupants for shock potential. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Incomplete_receptacle_.png | file://x:/photopub/docs/0000000549/8ba70996-98fd-4043-8d89-6a74d9ae6c36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ee7de78_83b0_431d_9ad4_aa6f47007abf
GAIN-720391-2016 | GA-473991-2016 | 12/12/2016 2:01:04 PM | ASSESS: GA: Final | png | #asFound | GA131 | Equipment service clearance non compliant | 1 | 1 |  | 1 | Equipment service clearance non compliant | No_Service_clearance_to_front_of_furnace.png | file://x:/photopub/docs/0000000530/f191579e-a897-4106-aacf-b12c7c9bd572.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b563aa95_338d_440a_ada0_f8f117caeab6
ELOP-655145-2016 | 4703593 | 1/5/2017 9:43:30 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 3 | Electrical panel with open breaker spaces. Energized parts exposed creating a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Panel_4A_open_breaker_spaces.png | file://x:/photopub/docs/0000000539/7f03e0d9-601b-4d20-9826-ca2f9fad79d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9A4FC7C5_54F3_455A_8F47_E745E90DC5E6
ELIN-722792-2016 | EL-478450-2016 | 1/3/2017 12:05:02 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacles installed for temporary construction use on residential properties are required to be ground fault circuit interrupter protected (GFCI). This is required to protect persons from electrical shocks when using portable appliances and electrical equipment during construction. This installation has a 15A, 120V receptacle that was installed below the panel for temporary construction use. The receptacle is not GFCI protected. Left uncorrected this is a potential shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Non-GFCI_protected_receptacle_below_the_panel.png | file://x:/photopub/docs/0000000538/85fda208-534d-468a-9ce0-f83760c8b625.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5029f49c_d47b_44f4_8a36_d6ae67d689de
GAHE-749669-2017 | HE-497181-2017 | 2/1/2017 9:30:24 AM | ASSESS: GA HE: Hazard Elimination | JPG | #asFound Leaking Gas valve | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | #Photo-2017-02-01-09-36-23_0258.JPG While assessing a hazard call, i found a small gas leak at an appliance shut off valve. If left unchecked gas may accumulate in the occupied space until it finds a source of ignition, leading to a fire or explosion. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Photo-2017-02-01-09-36-23_0258.JPG | file://x:/photopub/docs/0000000551/17e3befb-0965-4a34-8ee8-0a3c2c0af2e6.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93c738f0_4e56_414d_ada5_7e8b301afe58
GAIN-743864-2017 | GA-412512-2016 | 2/15/2017 9:19:45 AM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Zone_valve.png The as found hazard was a zone valve certified for use with a water system which had been installed on a gas system. This creates a risk of a gas leak and or potential damage to the valve as it is not rated for the potential low temperature of the propane gas. | 3 | Non-compliant material/fittings installed | Zone_valve.png | file://x:/photopub/docs/0000000557/7cd6fc82-3c82-451e-ae4d-534041151040.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f56a875a_873f_4267_8037_3da850865942
ELHE-757646-2017 | HE-501405-2017 | 2/15/2017 3:45:25 PM | ASSESS: EL HE: Hazard Elimination | JPG | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #IMG_3947.JPG,IMG_3950.JPG,IMG_3749.JPG The existing unfused 120/240 volt overhead utility supply conductors are in contact with a detached building and unsuitably protected from mechanical damage that can lead to equipment damage, shock and thermal hazards. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | IMG_3950.JPG | file://x:/photopub/docs/0000000558/70d4078f-c414-4632-b9dd-710c3c34a8fa.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5408e021_3a26_419d_8aef_751ad95f0907
ELHE-757646-2017 | HE-501405-2017 | 2/15/2017 3:45:25 PM | ASSESS: EL HE: Hazard Elimination | JPG | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #IMG_3947.JPG,IMG_3950.JPG,IMG_3749.JPG The existing unfused 120/240 volt overhead utility supply conductors are in contact with a detached building and unsuitably protected from mechanical damage that can lead to equipment damage, shock and thermal hazards. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | IMG_3749.JPG | file://x:/photopub/docs/0000000558/4b9d130f-5c68-49ed-99d0-7b4f59f7057a.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5408e021_3a26_419d_8aef_751ad95f0907
ELHE-757646-2017 | HE-501405-2017 | 2/15/2017 3:45:25 PM | ASSESS: EL HE: Hazard Elimination | JPG | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #IMG_3947.JPG,IMG_3950.JPG,IMG_3749.JPG The existing unfused 120/240 volt overhead utility supply conductors are in contact with a detached building and unsuitably protected from mechanical damage that can lead to equipment damage, shock and thermal hazards. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | IMG_3749.JPG | file://x:/photopub/docs/0000000558/2114aeb0-784d-4e69-a890-c0771fe1ad3d.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5408e021_3a26_419d_8aef_751ad95f0907
ELHE-757646-2017 | HE-501405-2017 | 2/15/2017 3:45:25 PM | ASSESS: EL HE: Hazard Elimination | JPG | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #IMG_3947.JPG,IMG_3950.JPG,IMG_3749.JPG The existing unfused 120/240 volt overhead utility supply conductors are in contact with a detached building and unsuitably protected from mechanical damage that can lead to equipment damage, shock and thermal hazards. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | IMG_3947.JPG | file://x:/photopub/docs/0000000558/d56c8e5d-62ee-4038-8d43-a2faf1612974.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5408e021_3a26_419d_8aef_751ad95f0907
ELHE-757646-2017 | HE-501405-2017 | 2/15/2017 3:45:25 PM | ASSESS: EL HE: Hazard Elimination | JPG | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #IMG_3947.JPG,IMG_3950.JPG,IMG_3749.JPG The existing unfused 120/240 volt overhead utility supply conductors are in contact with a detached building and unsuitably protected from mechanical damage that can lead to equipment damage, shock and thermal hazards. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | IMG_3950.JPG | file://x:/photopub/docs/0000000558/5d07bf3b-d4f1-4566-868a-055195e09db1.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5408e021_3a26_419d_8aef_751ad95f0907
ELHE-757646-2017 | HE-501405-2017 | 2/15/2017 3:45:25 PM | ASSESS: EL HE: Hazard Elimination | JPG | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #IMG_3947.JPG,IMG_3950.JPG,IMG_3749.JPG The existing unfused 120/240 volt overhead utility supply conductors are in contact with a detached building and unsuitably protected from mechanical damage that can lead to equipment damage, shock and thermal hazards. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | IMG_3947.JPG | file://x:/photopub/docs/0000000558/a9b0f6a5-d939-4b0e-bc08-dc5719f7f431.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5408e021_3a26_419d_8aef_751ad95f0907
BPVOP-743744-2017 | UW-493640-2017 | 1/23/2017 3:27:21 PM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_valve_.png,Safety_valvle2.png BP131 All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve(s). Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve_.png | file://x:/photopub/docs/0000000550/92f87d62-e498-42ea-b053-92824867d684.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78751349_cdd7_47c6_af1e_f987025d7bc0
GAIN-748421-2017 | GA-462914-2016 | 2/14/2017 3:29:08 PM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | #Flex_connector_on_tube_heater__.png Installer used a Corrugated appliance connector for connection of gas line to a suspended Radiant Tube heater. | 2 | Certified appliance connector installed but not approved for application | Flex_connector_on_tube_heater__.png | file://x:/photopub/docs/0000000557/5d786108-e626-48c4-991a-9061179ce8e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3269c93d_6d5c_41b8_85ee_5d996c56c209
ELOP-655010-2016 | 4703581 | 1/5/2017 9:06:06 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 3 | The electrical panel has open breaker spaces. Bus bars inside could be contacted creating a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Panel_6B_open_breaker_spaces.png | file://x:/photopub/docs/0000000539/f2fc367e-a5ba-4a53-93b7-d0a5371b3e4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5418897A_EA2F_4C08_8ECB_AB96B649A754
GAIN-732691-2017 | GA-471501-2016 | 1/5/2017 1:49:53 PM | ASSESS: GA: Final | png | #asFound | GA138 | Equipment unserviceable due to lack of clearance. | 3 | 3 | T & P valve discharge does not meet code required clearance of 12" from discharge opening to floor level. | 3 | Equipment unserviceable due to lack of clearance. | Boiler.png | file://x:/photopub/docs/0000000539/58047b11-61e9-4f95-a2d4-596590615aca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0d6c62d_622f_49ec_8f99_fdc7134c586f
ELIN-716219-2016 | EL-439907-2016 | 12/5/2016 3:16:56 PM | ASSESS: EL: Final | png | #asFound | EL135 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | 3 | 3 | Panel is recessed allowing space between breakers and cover. The gap is larger than acceptable allowing access for small items and reducing support for securing breakers. | 3 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | Sub_distribution.png | file://x:/photopub/docs/0000000526/e2383d66-c80a-456b-9aa1-88056b6d3651.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__049c5f0f_5e2f_4c7e_a307_531fea66eb2d
ELIN-716219-2016 | EL-439907-2016 | 12/5/2016 3:16:56 PM | ASSESS: EL: Final | png | #asFound | EL135 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | 3 | 3 | Panel is recessed allowing space between breakers and cover. The gap is larger than acceptable allowing access for small items and reducing support for securing breakers. | 3 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | Sub_distribution2.png | file://x:/photopub/docs/0000000526/9d6199db-fc00-4702-afa5-c9220dc7ca55.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__049c5f0f_5e2f_4c7e_a307_531fea66eb2d
ELIN-730879-2016 | EL-485664-2016 | 1/3/2017 2:09:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Electrical conductors are required to be sized properly to safely conduct the current they are intended to carry. This is required to prevent over heating of conductor insulation and terminations. This installation of a 3c#4/0 ACWU service cable installed to relocate an existing service connection for a commercial building is rated at 180A. The existing service size is rated at 200A. Left uncorrected this is a potential fire hazard if the service cable is overloaded and conductor insulation or terminations are damaged. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Marking_on_service_cable.png | file://x:/photopub/docs/0000000538/ada45e92-7d25-40bc-b0b2-65d10ec7c39d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a78f436c_4c19_4305_83d0_c8bce8c923ae
ELIN-722792-2016 | EL-478450-2016 | 1/3/2017 12:05:02 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacles installed for temporary construction use on residential properties are required to be ground fault circuit interrupter protected (GFCI). This is required to protect persons from electrical shocks when using portable appliances and electrical equipment during construction. This installation has a 15A, 120V receptacle that was installed below the panel for temporary construction use. The receptacle is not GFCI protected. Left uncorrected this is a potential shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | New_house_under_construction_.png | file://x:/photopub/docs/0000000538/0a573ec1-9089-4b3b-bc56-a9d8aba8fd18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5029f49c_d47b_44f4_8a36_d6ae67d689de
ELIN-730879-2016 | EL-485664-2016 | 1/3/2017 2:09:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Electrical conductors are required to be sized properly to safely conduct the current they are intended to carry. This is required to prevent over heating of conductor insulation and terminations. This installation of a 3c#4/0 ACWU service cable installed to relocate an existing service connection for a commercial building is rated at 180A. The existing service size is rated at 200A. Left uncorrected this is a potential fire hazard if the service cable is overloaded and conductor insulation or terminations are damaged. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Back_of_existing_building_where_service_connection_is_being_relocated_to.png | file://x:/photopub/docs/0000000538/5227427a-4e0c-426b-af32-d00947b77c4c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a78f436c_4c19_4305_83d0_c8bce8c923ae
ELIN-730879-2016 | EL-485664-2016 | 1/3/2017 2:09:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Electrical conductors are required to be sized properly to safely conduct the current they are intended to carry. This is required to prevent over heating of conductor insulation and terminations. This installation of a 3c#4/0 ACWU service cable installed to relocate an existing service connection for a commercial building is rated at 180A. The existing service size is rated at 200A. Left uncorrected this is a potential fire hazard if the service cable is overloaded and conductor insulation or terminations are damaged. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Front_of_building_where_service_connection_is_being_relocated_from.png | file://x:/photopub/docs/0000000538/ff15feb8-d05c-4c93-8b3c-3e0d8162fc8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a78f436c_4c19_4305_83d0_c8bce8c923ae
ELIN-730879-2016 | EL-485664-2016 | 1/3/2017 2:09:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Electrical conductors are required to be sized properly to safely conduct the current they are intended to carry. This is required to prevent over heating of conductor insulation and terminations. This installation of a 3c#4/0 ACWU service cable installed to relocate an existing service connection for a commercial building is rated at 180A. The existing service size is rated at 200A. Left uncorrected this is a potential fire hazard if the service cable is overloaded and conductor insulation or terminations are damaged. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Cable_installed_for_service_connection_relocation_to_back_of_building.png | file://x:/photopub/docs/0000000538/5fa924e0-4e24-4b04-bba9-6ca953e87dbe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a78f436c_4c19_4305_83d0_c8bce8c923ae
ELIN-730879-2016 | EL-485664-2016 | 1/3/2017 2:09:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Electrical conductors are required to be sized properly to safely conduct the current they are intended to carry. This is required to prevent over heating of conductor insulation and terminations. This installation of a 3c#4/0 ACWU service cable installed to relocate an existing service connection for a commercial building is rated at 180A. The existing service size is rated at 200A. Left uncorrected this is a potential fire hazard if the service cable is overloaded and conductor insulation or terminations are damaged. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Service_switch_label.png | file://x:/photopub/docs/0000000538/43e91f8d-ef21-49f6-9846-d5adc14528fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a78f436c_4c19_4305_83d0_c8bce8c923ae
ELIN-722792-2016 | EL-478450-2016 | 1/3/2017 12:05:02 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacles installed for temporary construction use on residential properties are required to be ground fault circuit interrupter protected (GFCI). This is required to protect persons from electrical shocks when using portable appliances and electrical equipment during construction. This installation has a 15A, 120V receptacle that was installed below the panel for temporary construction use. The receptacle is not GFCI protected. Left uncorrected this is a potential shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Temporary_construction_receptacle_below_service_panel.png | file://x:/photopub/docs/0000000538/418ade3a-7543-4f17-a1ae-f02807126afe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5029f49c_d47b_44f4_8a36_d6ae67d689de
GAIN-752060-2017 | GA-498509-2017 | 2/9/2017 2:31:45 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Missing_bonding.png | 2 | Physical protection of piping and tubing absent. | Missing_bonding.png | file://x:/photopub/docs/0000000555/d8195bf9-3d78-418b-9505-078f5fd5de26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24ce85d4_d076_486f_8c0c_735858ac614b
BPVOP-650186-2016 | 2854919 | 2/1/2017 10:09:13 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 | #scale.png | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | scale.png | file://x:/photopub/docs/0000000551/1fa044a8-a5e7-4e8e-a514-cd717042b72f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01aa6249_507b_455d_8e1f_b4e99420438e
ELIN-730866-2016 | EL-485065-2016 | 12/30/2016 11:54:06 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL188 | Installation of electrical equipment Equipment is not approved for the specific use | 2 | 2 |  | 2 | Installation of electrical equipment Equipment is not approved for the specific use | Wrong_staple_size.png | file://x:/photopub/docs/0000000536/61ccdc84-cb38-4baa-a9ae-de2aab0ce63e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e504804_36dc_4167_9e6c_dfcba6b35118
ELIN-730866-2016 | EL-485065-2016 | 12/30/2016 11:54:06 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL188 | Installation of electrical equipment Equipment is not approved for the specific use | 2 | 2 |  | 2 | Installation of electrical equipment Equipment is not approved for the specific use | Box_not_flush.png | file://x:/photopub/docs/0000000536/aac1e6a0-a57c-4e07-acbf-36df84448fa0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e504804_36dc_4167_9e6c_dfcba6b35118
BPVOP-724635-2016 | UW-481617-2016 | 12/15/2016 4:42:26 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP094 | 2.0.1 Control system may overrun - No commissioning or start ups completed | 3 | 3 | All newly installed regulated equipment must undergo all necessary commissioning protocols in order to ensure safe installation. I found that there was no proper commissioning procedures completed for this installation of 3 hot water boilers and 1 low pressure (15 PSIG) steam boiler. Potential exists for an incident because required safety checkups have not been completed and documented. | 3 | 2.0.1 Control system may overrun - No commissioning or start ups completed | steam_unit.png | file://x:/photopub/docs/0000000531/40300fd4-c071-4a83-92e3-45a46550beaf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a81d0fa_6a70_4997_8cf5_b7ac0dc3e816
ELIN-743327-2017 | EL-475591-2016 | 1/23/2017 10:19:40 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Receptacles_without_cover_plates_1.png,Receptacles_without_cover_plates_2.png Energized receptacles did not have cover plates on them exposing occupants to a potential shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Receptacles_without_cover_plates_2.png | file://x:/photopub/docs/0000000546/097fad84-fe48-4ede-83ad-98dbf1f7e2e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fc4b0ab_7540_46f9_a2cf_8241c6d3e318
ELIN-739825-2017 | EL-485687-2016 | 1/23/2017 2:25:28 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Raceway_required.png A string line from the junction box to the floor was installed to pull in non heating leads of an in floor heating system where a raceway is required. This condition could lead to damage to the non heating leads or adjacent wires when fishing them through the wall. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Raceway_required.png | file://x:/photopub/docs/0000000546/0e992fa2-0c02-4970-a14d-6d0b76bf142e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2df52878_e86b_476e_b4bc_a2bac23f3ca3
ELIN-743327-2017 | EL-475591-2016 | 1/23/2017 10:19:40 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Receptacles_without_cover_plates_1.png,Receptacles_without_cover_plates_2.png Energized receptacles did not have cover plates on them exposing occupants to a potential shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Receptacles_without_cover_plates_1.png | file://x:/photopub/docs/0000000546/59cd5f22-89fd-4885-9f62-031050564aa8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fc4b0ab_7540_46f9_a2cf_8241c6d3e318
ELIN-739820-2017 | EL-485686-2016 | 1/23/2017 1:55:56 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 2 | #Raceway_required_.png A string line from the junction box to floor was installed to pull in non heating leads of in floor heating system where a raceway is required. This condition could lead to damage of the non heating leads or adjacent wires when fishing them through the wall. | 3 | Conductors Equipment is not approved for the specific use. | Raceway_required_.png | file://x:/photopub/docs/0000000546/fba912b1-6b58-46f3-a640-bb90d046a9ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31455a50_bbb0_4e44_9ea7_93532b3a24a8
GAIN-726370-2016 | GA-473066-2016 | 12/21/2016 9:28:45 AM | ASSESS: GA: Rough-In | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | Sidewall air intake and vent terminations taken from two different pressure zones. | 2 | Side wall vent termination not compliant with installation instructions | Air_intake.png | file://x:/photopub/docs/0000000534/676e1d88-cb3f-4adf-8e43-a63401a3eff4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7f0ed87_9a81_48e3_96d2_8622a7898a37
GAIN-727166-2016 | GA-483514-2016 | 12/21/2016 11:29:34 AM | ASSESS: GA: Rough-In | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Piping not sleeved where passing through masonry wall. This could lead to corrosion of the pipe and a potential gas leak. | 2 | Physical protection of piping and tubing absent. | Piping.png | file://x:/photopub/docs/0000000534/e3409f8f-4cea-4157-834a-1f968d8805cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__befb5cd2_c259_4e99_ae4e_c93549506cda
BPVIN-756435-2017 | BPV-500807-2017 | 2/14/2017 11:04:33 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP137 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | 4 | 4 | #Hot_water_storage_tank_.png,Vessel_nameplate.png,Pressure_relief_valve.png At least one pressure relief valve shall be provided for protection of a pressure vessel with the set pressure marked on the device not to exceed the maximum allowable working pressure of the vessel its protecting. I found a 150psi pressure relief valve installed on a pressure vessel with a MAWP nameplate rating of 125psi.Potential exists for an incident due to over pressure conditions. | 4 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | Hot_water_storage_tank_.png | file://x:/photopub/docs/0000000557/0032872d-852f-4251-8d93-a3208e13474c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6245064_641e_4ce3_923b_f0f4817fab8a
BPVIN-756435-2017 | BPV-500807-2017 | 2/14/2017 11:04:33 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP137 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | 4 | 4 | #Hot_water_storage_tank_.png,Vessel_nameplate.png,Pressure_relief_valve.png At least one pressure relief valve shall be provided for protection of a pressure vessel with the set pressure marked on the device not to exceed the maximum allowable working pressure of the vessel its protecting. I found a 150psi pressure relief valve installed on a pressure vessel with a MAWP nameplate rating of 125psi.Potential exists for an incident due to over pressure conditions. | 4 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | Vessel_nameplate.png | file://x:/photopub/docs/0000000557/cd9ad355-ab57-4221-b647-2717c466327f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6245064_641e_4ce3_923b_f0f4817fab8a
BPVIN-756435-2017 | BPV-500807-2017 | 2/14/2017 11:04:33 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP137 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | 4 | 4 | #Hot_water_storage_tank_.png,Vessel_nameplate.png,Pressure_relief_valve.png At least one pressure relief valve shall be provided for protection of a pressure vessel with the set pressure marked on the device not to exceed the maximum allowable working pressure of the vessel its protecting. I found a 150psi pressure relief valve installed on a pressure vessel with a MAWP nameplate rating of 125psi.Potential exists for an incident due to over pressure conditions. | 4 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | Pressure_relief_valve.png | file://x:/photopub/docs/0000000557/cef7fc36-3683-49dd-a4fa-cac6e67cb7bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6245064_641e_4ce3_923b_f0f4817fab8a
ELIN-732984-2017 | EL-424372-2016 | 1/6/2017 5:11:03 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Electrical conductors are required to be sized properly to safely conduct the current they are intended to carry. This is required to prevent over heating of conductor insulation, electrical devices and equipment, and terminations at electrical equipment. This electrical installation at an older house has 15A branch circuits protected by 30A fuses. Left uncorrected this is a potential fire hazard if branch circuits are overloaded and conductor insulation, devices and equipment, or terminations are damaged. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 60A_load_center_with_glass_fuses.png | file://x:/photopub/docs/0000000540/efdba026-1fb8-4620-90bd-b4d1341df141.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5ea65d5_b5a0_4a66_90cb_89a67dcafa91
ELIN-732984-2017 | EL-424372-2016 | 1/6/2017 5:11:03 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Electrical conductors are required to be sized properly to safely conduct the current they are intended to carry. This is required to prevent over heating of conductor insulation, electrical devices and equipment, and terminations at electrical equipment. This electrical installation at an older house has 15A branch circuits protected by 30A fuses. Left uncorrected this is a potential fire hazard if branch circuits are overloaded and conductor insulation, devices and equipment, or terminations are damaged. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 30A_fuses_protecting_15A_branch_circuits_and_equipment.png | file://x:/photopub/docs/0000000540/9290026e-d3a5-4709-8f7c-a93df86b80ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5ea65d5_b5a0_4a66_90cb_89a67dcafa91
ELIN-732984-2017 | EL-424372-2016 | 1/6/2017 5:11:03 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Electrical conductors are required to be sized properly to safely conduct the current they are intended to carry. This is required to prevent over heating of conductor insulation, electrical devices and equipment, and terminations at electrical equipment. This electrical installation at an older house has 15A branch circuits protected by 30A fuses. Left uncorrected this is a potential fire hazard if branch circuits are overloaded and conductor insulation, devices and equipment, or terminations are damaged. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Front_of_house__.png | file://x:/photopub/docs/0000000540/9089700b-8ae5-46b1-8e26-af2ee87f7a6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5ea65d5_b5a0_4a66_90cb_89a67dcafa91
ELHE-735737-2017 | HE-488235-2017 | 1/10/2017 8:32:39 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound feeder damaged and bent and not approved for the use | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use1.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use2.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use3.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use4.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use5.png Found temporary construction 120/240 volt 100 amp armoured feeder cable was moved or relocated by unqualified individuals and cable became bent and damaged. When armoured cable is moved or relocated improperly by unqualified individuals and cable is bent and subjected to mechanical damage, the electrical equipment becomes a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use3.png | file://x:/photopub/docs/0000000545/5c50ece1-dacb-4138-9a78-83776ec222f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cd3f5f5_9b65_47b0_89c7_1c056ee14c67
ELIN-749115-2017 | EL-461677-2016 | 2/1/2017 12:51:55 PM | ASSESS: EL: Service Connection | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_panel_without_cover_.png A 100 amp panel that was energized did not have a cover on it. This condition could lead to accidental contact with energized parts potentially leading to shock or electrocution. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_panel_without_cover_.png | file://x:/photopub/docs/0000000552/a6d15a12-39c9-4405-9d53-2106d5d27f8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d925464f_152e_4831_80e5_83509b0a13e6
BPVOP-724635-2016 | UW-481617-2016 | 12/15/2016 4:42:26 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP094 | 2.0.1 Control system may overrun - No commissioning or start ups completed | 3 | 3 | All newly installed regulated equipment must undergo all necessary commissioning protocols in order to ensure safe installation. I found that there was no proper commissioning procedures completed for this installation of 3 hot water boilers and 1 low pressure (15 PSIG) steam boiler. Potential exists for an incident because required safety checkups have not been completed and documented. | 3 | 2.0.1 Control system may overrun - No commissioning or start ups completed | boilers_.png | file://x:/photopub/docs/0000000531/67f06f80-5d7f-40a8-8699-d3aa6573f5a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a81d0fa_6a70_4997_8cf5_b7ac0dc3e816
ELIN-752528-2017 | UW-498720-2017 | 2/6/2017 3:12:46 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Rectifier21.png,Rectifier22.png Cover removed on energized rectifier leaving exposed electrical parts and a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Rectifier21.png | file://x:/photopub/docs/0000000554/234e5588-0cdd-4f02-a773-fe2c3efb7d2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2434ea32_e3f8_4b50_bd76_1d36a27fa52e
ELIN-752528-2017 | UW-498720-2017 | 2/6/2017 3:12:46 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Rectifier21.png,Rectifier22.png Cover removed on energized rectifier leaving exposed electrical parts and a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Rectifier22.png | file://x:/photopub/docs/0000000554/c3daea2d-c0cc-4821-a72c-29de7ad6e305.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2434ea32_e3f8_4b50_bd76_1d36a27fa52e
ELOP-753143-2017 | EL-066164-2013 | 2/7/2017 3:09:18 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Open_breaker_spaces1.png,Open_breaker_spaces2.png,Open_breaker_spaces3.png Open breaker spaces on energized panel leaving exposed electrical parts and a potential shock hazard. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Open_breaker_spaces3.png | file://x:/photopub/docs/0000000555/ae1760fc-2aaa-4422-b046-3d1f1900b2f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5502eb32_431f_45ea_9e00_5624daa19178
ELIN-729626-2016 | EL-347460-2016-1 | 12/28/2016 3:16:54 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | This assessment found several receptacles in the dwelling that were not Arc Fault protected as required. Arc Fault protection reduces the risk of electrical fires. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Panel_labeling.png | file://x:/photopub/docs/0000000536/9c312cd6-0fbd-49b4-b2c4-2e05f38ed70c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__893b8f3b_5995_4f3c_9119_4170093b74b6
ELHE-717780-2016 | HE-476613-2016 | 12/9/2016 7:48:30 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | The 100 amp 120/240 volt consumer service cable is not buried near pole and exposed to mechanical damage. This can lead to a shock, thermal and equipment damage issue. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Feeder_cable_exposed.png | file://x:/photopub/docs/0000000529/37a8fa55-d0ac-479f-9012-4903277c995b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9df8706_c624_43c9_8bf7_ac7cce393723
ELHE-735737-2017 | HE-488235-2017 | 1/10/2017 8:32:39 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound feeder damaged and bent and not approved for the use | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use1.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use2.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use3.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use4.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use5.png Found temporary construction 120/240 volt 100 amp armoured feeder cable was moved or relocated by unqualified individuals and cable became bent and damaged. When armoured cable is moved or relocated improperly by unqualified individuals and cable is bent and subjected to mechanical damage, the electrical equipment becomes a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use5.png | file://x:/photopub/docs/0000000545/8cea54e5-21a6-4751-a7de-23556cca0d28.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cd3f5f5_9b65_47b0_89c7_1c056ee14c67
ELHE-735737-2017 | HE-488235-2017 | 1/10/2017 8:32:39 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound feeder damaged and bent and not approved for the use | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use1.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use2.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use3.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use4.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use5.png Found temporary construction 120/240 volt 100 amp armoured feeder cable was moved or relocated by unqualified individuals and cable became bent and damaged. When armoured cable is moved or relocated improperly by unqualified individuals and cable is bent and subjected to mechanical damage, the electrical equipment becomes a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use1.png | file://x:/photopub/docs/0000000545/5aa137e8-95d0-4760-9241-3c8fa3cb0a5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cd3f5f5_9b65_47b0_89c7_1c056ee14c67
ELIN-737558-2017 | EL-481239-2016 | 1/20/2017 9:33:45 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #No_bonding_bushing_metal_conduit_nipple_service_raceway.png A new residential service rated 100 amps and 240 volts was installed. A metal pipe was used to feed the service conductors from the meter base to the panel. Standard locknuts were used to bond this metal pipe. To ensure that service installations are protected other means are required to be used other than standard locknuts. when other measures such as bonding bushings, property damage or injury to persons can occur. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_bonding_bushing_metal_conduit_nipple_service_raceway.png | file://x:/photopub/docs/0000000545/95e49679-a6fa-4bcf-bbe6-7ee11316b7a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f3f3b9e_fc13_40a1_9070_063392dce4f6
ELIN-741629-2017 | EL-489243-2017 | 1/20/2017 12:31:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | #Spacing_not_ok.png A new house under construction has a distance of 1.3 meters to the first 120 volt 20 amp receptacles on the left side of the sink in the kitchen. This can result in owners resorting to the use of extension cords to feed appliances. This can also result in damage to property or injury to persons. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Spacing_not_ok.png | file://x:/photopub/docs/0000000546/dcd70c9e-b782-4e77-b718-39fcb2b474b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01fa75fe_4bd7_4035_8dc0_100ed848ba6c
ELIN-733863-2017 | EL-480018-2016 | 1/11/2017 1:56:20 PM | ASSESS: EL: Service Connection | png | #asFound Ground conductor terminated to panel enclosure | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | #Grounding_termination.png The 200 amp 120/208 volt 3-phase 4-wire service grounding conductor terminated to the panel enclosure and not the required identified conductor. A portion of a fault required to follow to ground in the system would rely on the existing bonding jumper and this can lead to an equipment damage issue | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Grounding_termination.png | file://x:/photopub/docs/0000000542/c0a8a36d-eae6-4bb4-b107-f6908cb78268.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98ea0d3c_2660_49ff_8494_89036f79c148
GAIN-730161-2016 | GA-467581-2016 | 1/6/2017 12:55:27 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | The gas dryer ducting was installed in direct contact with combustible material. The manufacturer specifies a 2" clearance to all combustible material. The heat produced by the duct could eventually lead to a fire. | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Dryer_ducting_.png | file://x:/photopub/docs/0000000539/a943b6cb-dd70-4776-911d-6fbaeb6c7a6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c03e240a_4fa6_4b64_9624_8dca8450a66b
GAUP-734405-2017 | UW-487618-2017 | 1/6/2017 7:04:35 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | The as found hazard was corrugated stainless steel tubing which had been directly connected to a coffee roaster mounted on casters (movable). This is a hazard because if the coffee roaster were to be moved forcefully the tubing would kink and/or break allow unburnt gas to be released into the building. | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Vent.png | file://x:/photopub/docs/0000000540/4580ca05-c2b8-4044-9cc6-faeebb529036.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eed64404_9def_47f6_a22d_bd4df5ffe4c8
GAUP-734405-2017 | UW-487618-2017 | 1/6/2017 7:04:35 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | The as found hazard was corrugated stainless steel tubing which had been directly connected to a coffee roaster mounted on casters (movable). This is a hazard because if the coffee roaster were to be moved forcefully the tubing would kink and/or break allow unburnt gas to be released into the building. | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | CSST_.png | file://x:/photopub/docs/0000000540/f8319466-a14c-468e-82f8-81bc9187d154.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eed64404_9def_47f6_a22d_bd4df5ffe4c8
GAUP-734405-2017 | UW-487618-2017 | 1/6/2017 7:04:35 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | The as found hazard was corrugated stainless steel tubing which had been directly connected to a coffee roaster mounted on casters (movable). This is a hazard because if the coffee roaster were to be moved forcefully the tubing would kink and/or break allow unburnt gas to be released into the building. | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Roaster.png | file://x:/photopub/docs/0000000540/c31904c1-c603-4f75-8506-3ae1e345154d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eed64404_9def_47f6_a22d_bd4df5ffe4c8
GAUP-734405-2017 | UW-487618-2017 | 1/6/2017 7:04:35 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | The as found hazard was corrugated stainless steel tubing which had been directly connected to a coffee roaster mounted on casters (movable). This is a hazard because if the coffee roaster were to be moved forcefully the tubing would kink and/or break allow unburnt gas to be released into the building. | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Contractor_invoice.png | file://x:/photopub/docs/0000000540/83ab084b-5b4e-44a8-8fe3-3b34cded2b5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eed64404_9def_47f6_a22d_bd4df5ffe4c8
ELIN-726154-2016 | EL-482057-2016 | 1/5/2017 5:05:20 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors hanging out of electrical equipment while electrical equipment is not safe, is not compliant and is not ready or authorized for connection to power supply system. When electrical equipment and its branch circuit conductors are energized and exposed, the electrical equipment could come in contact with people or property structures and could become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | exposed_energized_conductors_hanging_from_outlet_box_3.png | file://x:/photopub/docs/0000000540/4d307933-f987-4280-ac92-01bf83f9cfc2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43319062_eea2_4339_9c95_412f9be18439
ELIN-726154-2016 | EL-482057-2016 | 1/5/2017 5:05:20 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors hanging out of electrical equipment while electrical equipment is not safe, is not compliant and is not ready or authorized for connection to power supply system. When electrical equipment and its branch circuit conductors are energized and exposed, the electrical equipment could come in contact with people or property structures and could become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | exposed_energized_conductors_hanging_from_outlet_box_2.png | file://x:/photopub/docs/0000000540/51091aaa-c5cf-48a2-a6c7-a5322f343118.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43319062_eea2_4339_9c95_412f9be18439
ELOP-753143-2017 | EL-066164-2013 | 2/7/2017 3:09:18 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Open_breaker_spaces1.png,Open_breaker_spaces2.png,Open_breaker_spaces3.png Open breaker spaces on energized panel leaving exposed electrical parts and a potential shock hazard. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Open_breaker_spaces1.png | file://x:/photopub/docs/0000000555/4df6a63e-8e26-4077-a573-c79cbe2c7e62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5502eb32_431f_45ea_9e00_5624daa19178
ELOP-753143-2017 | EL-066164-2013 | 2/7/2017 3:09:18 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Open_breaker_spaces1.png,Open_breaker_spaces2.png,Open_breaker_spaces3.png Open breaker spaces on energized panel leaving exposed electrical parts and a potential shock hazard. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Open_breaker_spaces2.png | file://x:/photopub/docs/0000000555/ddef50ec-344b-4559-ace2-fa8ee710d37a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5502eb32_431f_45ea_9e00_5624daa19178
ELIN-757152-2017 | EL-493449-2017 | 2/17/2017 8:51:42 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Shock1.png,Shock2.png,Shock3.png,Shock4.png,Shock5.png This assessment found bare live wires through out dwelling, creating a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Shock5.png | file://x:/photopub/docs/0000000558/a87bfbac-8257-4c05-981d-f7ebcaff64a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e05329c5_7ade_492b_8cfe_20e7b2664126
ELIN-757152-2017 | EL-493449-2017 | 2/17/2017 8:51:42 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Shock1.png,Shock2.png,Shock3.png,Shock4.png,Shock5.png This assessment found bare live wires through out dwelling, creating a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Shock3.png | file://x:/photopub/docs/0000000558/a3150479-d15e-44c7-a9e8-9ae97b68c846.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e05329c5_7ade_492b_8cfe_20e7b2664126
ELIN-757152-2017 | EL-493449-2017 | 2/17/2017 8:51:42 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Shock1.png,Shock2.png,Shock3.png,Shock4.png,Shock5.png This assessment found bare live wires through out dwelling, creating a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Shock1.png | file://x:/photopub/docs/0000000558/9c9bb324-580d-4d18-8e14-8dcd7c857d17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e05329c5_7ade_492b_8cfe_20e7b2664126
ELIN-757152-2017 | EL-493449-2017 | 2/17/2017 8:51:42 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Shock1.png,Shock2.png,Shock3.png,Shock4.png,Shock5.png This assessment found bare live wires through out dwelling, creating a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Shock2.png | file://x:/photopub/docs/0000000558/cb230646-7b32-433d-94c0-d17f73b96494.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e05329c5_7ade_492b_8cfe_20e7b2664126
ELIN-757152-2017 | EL-493449-2017 | 2/17/2017 8:51:42 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Shock1.png,Shock2.png,Shock3.png,Shock4.png,Shock5.png This assessment found bare live wires through out dwelling, creating a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Shock4.png | file://x:/photopub/docs/0000000558/ac247ca8-7de1-41a6-841b-dde7a3885ab0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e05329c5_7ade_492b_8cfe_20e7b2664126
ELIN-726586-2016 | EL-474463-2016 | 12/20/2016 11:04:01 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Consumer service raceways are not suitably drained so as to prevent the ingress of moisture into metering equipment. This poses a serious risk of property damage (thermal event) due to water contacting energized equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | View_01_site.png | file://x:/photopub/docs/0000000533/c1029f2f-09bd-4218-9515-1877facd8cc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f824250_bbef_48de_bab0_3106e6fe76ca
ELHE-735737-2017 | HE-488235-2017 | 1/10/2017 8:32:39 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound feeder damaged and bent and not approved for the use | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use1.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use2.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use3.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use4.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use5.png Found temporary construction 120/240 volt 100 amp armoured feeder cable was moved or relocated by unqualified individuals and cable became bent and damaged. When armoured cable is moved or relocated improperly by unqualified individuals and cable is bent and subjected to mechanical damage, the electrical equipment becomes a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use2.png | file://x:/photopub/docs/0000000545/859fc232-533c-4102-84af-634cd4da692c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cd3f5f5_9b65_47b0_89c7_1c056ee14c67
ELHE-735737-2017 | HE-488235-2017 | 1/10/2017 8:32:39 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound feeder damaged and bent and not approved for the use | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use1.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use2.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use3.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use4.png,Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use5.png Found temporary construction 120/240 volt 100 amp armoured feeder cable was moved or relocated by unqualified individuals and cable became bent and damaged. When armoured cable is moved or relocated improperly by unqualified individuals and cable is bent and subjected to mechanical damage, the electrical equipment becomes a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Feeder_bent_and_damaged_and_temporary_construction_wiring_system_is_not_approved_for_the_use4.png | file://x:/photopub/docs/0000000545/38be5712-5ba7-4268-b632-6532b6377373.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cd3f5f5_9b65_47b0_89c7_1c056ee14c67
ELOP-724078-2016 | 1637 | 12/14/2016 3:57:29 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 | The electrical room is being used for storage. This condition limits safe egress from the room in case of a failure. | 1 | General Working space or dedicated space is being used for storage | Storage_in_electrical_room.png | file://x:/photopub/docs/0000000531/41a90093-79ec-479a-b391-43e967d1a57a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a732ed97_51cb_4e03_93ff_6b0d58f02c7e
ELOP-724083-2016 | 7125 | 12/14/2016 4:49:02 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Various panel boards with open breaker spaces. Panel EE, L, AA, CR, LL. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Breaker_spaces.png | file://x:/photopub/docs/0000000531/6b2a27e9-78a4-4db5-a1b4-091cc90da054.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4371dae0_7a84_4241_bd9b_8921cf1abde4
ELOP-724083-2016 | 7125 | 12/14/2016 4:49:02 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Various panel boards with open breaker spaces. Panel EE, L, AA, CR, LL. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 2.png | file://x:/photopub/docs/0000000531/c5c0a334-8f8c-4470-ae94-ca2f2ffa390a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4371dae0_7a84_4241_bd9b_8921cf1abde4
ELOP-724083-2016 | 7125 | 12/14/2016 4:49:02 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Various panel boards with open breaker spaces. Panel EE, L, AA, CR, LL. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3.png | file://x:/photopub/docs/0000000531/bb889bf6-615d-4053-aa87-e29387513c39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4371dae0_7a84_4241_bd9b_8921cf1abde4
BPVIN-751513-2017 | BPV-498262-2017 | 2/3/2017 4:07:24 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD_.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of an Air Receiver part of system with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 5 years as per CSA B51-2014. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD_.png | file://x:/photopub/docs/0000000553/170d5a7b-762a-4ed9-b58b-976abcf3b91e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d78a2815_66c5_40a6_b3e5_8958a5adcc02
GAUP-734405-2017 | UW-487618-2017 | 1/6/2017 7:04:35 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | The as found hazard was corrugated stainless steel tubing which had been directly connected to a coffee roaster mounted on casters (movable). This is a hazard because if the coffee roaster were to be moved forcefully the tubing would kink and/or break allow unburnt gas to be released into the building. | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Rating_plate.png | file://x:/photopub/docs/0000000540/fe73f64e-2c38-4b68-b59f-5b85466e45d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eed64404_9def_47f6_a22d_bd4df5ffe4c8
GAIN-734475-2017 | GA-431577-2016 | 1/10/2017 12:17:01 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #5279_197_A1.png,5279_197_A2.png,5279_197_A3.png Gas contractor has replaced a counterflow furnace and the existing base is not adequate to protect the floor from the radiant heat. Long term operation of furnace will cause combustible flooring to dry out and catch fire causing a building fire of a occupied home | 3 | Clearance to combustible not met | 5279_197_A3.png | file://x:/photopub/docs/0000000541/9b785315-49ca-453a-995f-506b708c3b20.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bb4a360_8e01_46c1_aa87_db69ea8233d8
GAIN-734475-2017 | GA-431577-2016 | 1/10/2017 12:17:01 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #5279_197_A1.png,5279_197_A2.png,5279_197_A3.png Gas contractor has replaced a counterflow furnace and the existing base is not adequate to protect the floor from the radiant heat. Long term operation of furnace will cause combustible flooring to dry out and catch fire causing a building fire of a occupied home | 3 | Clearance to combustible not met | 5279_197_A1.png | file://x:/photopub/docs/0000000541/8caaa747-9a15-450a-8d5b-9003d09c7ffa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bb4a360_8e01_46c1_aa87_db69ea8233d8
GAIN-734475-2017 | GA-431577-2016 | 1/10/2017 12:17:01 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #5279_197_A1.png,5279_197_A2.png,5279_197_A3.png Gas contractor has replaced a counterflow furnace and the existing base is not adequate to protect the floor from the radiant heat. Long term operation of furnace will cause combustible flooring to dry out and catch fire causing a building fire of a occupied home | 3 | Clearance to combustible not met | 5279_197_A2.png | file://x:/photopub/docs/0000000541/f216583c-cf61-4ecc-8c45-837a72d44918.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bb4a360_8e01_46c1_aa87_db69ea8233d8
ELIN-726154-2016 | EL-482057-2016 | 1/5/2017 5:05:20 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors hanging out of electrical equipment while electrical equipment is not safe, is not compliant and is not ready or authorized for connection to power supply system. When electrical equipment and its branch circuit conductors are energized and exposed, the electrical equipment could come in contact with people or property structures and could become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | exposed_energized_conductors_hanging_from_outlet_box_6.png | file://x:/photopub/docs/0000000540/31a3d66a-a038-4aa7-b24d-fd52bae7cfef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43319062_eea2_4339_9c95_412f9be18439
ELIN-726154-2016 | EL-482057-2016 | 1/5/2017 5:05:20 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors hanging out of electrical equipment while electrical equipment is not safe, is not compliant and is not ready or authorized for connection to power supply system. When electrical equipment and its branch circuit conductors are energized and exposed, the electrical equipment could come in contact with people or property structures and could become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | exposed_energized_conductors_hanging_from_outlet_box_.png | file://x:/photopub/docs/0000000540/5d15b599-65a3-4b55-a5a1-6e81be4cf2b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43319062_eea2_4339_9c95_412f9be18439
ELIN-726154-2016 | EL-482057-2016 | 1/5/2017 5:05:20 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors hanging out of electrical equipment while electrical equipment is not safe, is not compliant and is not ready or authorized for connection to power supply system. When electrical equipment and its branch circuit conductors are energized and exposed, the electrical equipment could come in contact with people or property structures and could become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | exposed_energized_conductors_hanging_from_outlet_box_4.png | file://x:/photopub/docs/0000000540/bdf82ca8-336f-415c-abc5-ca90f638de26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43319062_eea2_4339_9c95_412f9be18439
GAIN-722801-2016 | GA-480206-2016 | 1/6/2017 9:47:41 AM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | 4" single wall vent approximately 30" away from water heater connection installed against 2X4 wood. Minimum clearance required from combustibles to prevent overheating of combustible material and causing a fire. | 3 | Non compliant Type C Vent clearance | St_laurant.png | file://x:/photopub/docs/0000000540/83ef3b5c-7543-456f-a852-ebccdade1847.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3515f9cc_9a7b_4651_a6e4_36315bc05b83
ELOP-721110-2016 | 1965 | 11/29/2016 10:24:25 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 2 | 15 amp receptacle installed within 1.5m of washroom sink is not GFCI protected. This creates potential for a shock hazard should there be contact between the appliance, the user and water. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Not_GFCI_protected.png | file://x:/photopub/docs/0000000529/0fc8b66f-be16-4984-8f1c-b9ec23fd0280.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c6e3cd6_bfa1_418a_bb12_5d3916b67cc8
ELIN-757987-2017 | UW-501523-2017 | 2/10/2017 9:11:45 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Transformer21.png,Transformer22.png,Transformer23.png Armoured cable feeder without box, cover, fittings at the end of the cable creating a potential shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Transformer21.png | file://x:/photopub/docs/0000000558/cc85b1ad-530f-48cb-b923-fc32894eb9b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b332d65a_3759_4812_a342_9ad637f379d0
ELIN-726586-2016 | EL-474463-2016 | 12/20/2016 11:04:01 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Consumer service raceways are not suitably drained so as to prevent the ingress of moisture into metering equipment. This poses a serious risk of property damage (thermal event) due to water contacting energized equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | View02_site.png | file://x:/photopub/docs/0000000533/1a74cfdd-119a-4391-ba11-e61f15c60cdb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f824250_bbef_48de_bab0_3106e6fe76ca
BPVOP-751299-2017 | 2302792 | 2/3/2017 12:45:53 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD__.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of an Air Receiver part of system with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 5 years as per CSA B51-2014. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD__.png | file://x:/photopub/docs/0000000553/c5006c2d-0abb-4e68-88b0-9de110ac6265.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1fce7197_dbfb_44d0_b3ff_4398ea2ba0db
BPVOP-751305-2017 | 2302791 | 2/3/2017 1:03:26 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Prd_.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 3 years as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Prd_.png | file://x:/photopub/docs/0000000553/51ff77f7-a414-44f5-a975-c6ed3d1983d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65ffa300_b527_47ed_aa2b_0ee913cbbbe5
BPVOP-751307-2017 | 2302780 | 2/3/2017 1:11:49 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Prd.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 3 years as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Prd.png | file://x:/photopub/docs/0000000553/ddb61508-353c-4ae0-a259-33f56042bc80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6cdebcb_291e_4a4e_946c_0c4d91184e7f
ELIN-731783-2017 | EL-483343-2016 | 1/3/2017 2:47:42 PM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Consumer service conductors located underneath mobile home terminated in rigid PVC raceway has come undone. This could be hazard if a person(s) were to touch this, this could be a shock hazard due to overcurrent protection provided by supply authority being oversized. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Ug_consumer_service_conductos.png | file://x:/photopub/docs/0000000538/53422b99-5b11-4a8e-aa65-a73369f7a619.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56cbcc51_2afe_4ffd_ba73_88ad03bd40f7
GAIN-718281-2016 | GA-465343-2016 | 12/13/2016 7:57:04 AM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | A gas connector must be connected to ridged piping or tubing. Gas tubing can be damaged due to movement of the gas connector. | 2 | Physical protection of piping and tubing absent. | Tubing_not_adequately_secured_at_connection_for_appliance_connector.png | file://x:/photopub/docs/0000000530/44bc8a1e-496f-4b12-9343-3d5e60247740.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5baaa9e6_fa25_406c_b136_9ba4094ba045
ELIN-755138-2017 | EL-492637-2017 | 2/14/2017 12:54:00 PM | ASSESS: EL: Final | png | #asFound Cable connector is in use but is not mechanically connected to equipment | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | #Cable_not_connceted.png Armoured cable connector is installed onto armoured cable, but is not installed to equipment. Multiple hazards exist in this scenario: 1-cable is being supported by conductor connections only and putting a strain on these conductors due to cable weight. 2-bonding continuity for the cable sheath is not in place, both scenarios provide a risk of shock and fire to persons and property if accidental contact or a electrical fault were to take place. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Cable_not_connceted.png | file://x:/photopub/docs/0000000557/5268debe-4f09-4900-88b5-4e8a8d0d0dd8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30d3e3a2_5276_4c84_9181_af4910e12a9b
ELIN-755138-2017 | EL-492637-2017 | 2/14/2017 12:54:00 PM | ASSESS: EL: Final | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | #Cable_not_connceted.png Armoured cable connector is installed onto armoured cable, but is not installed to equipment. Multiple hazards exist in this scenario: 1-cable is being supported by conductor connections only and putting a strain on these conductors due to cable weight. 2-bonding continuity for the cable sheath is not in place, both scenarios provide a risk of shock and fire to persons and property if accidental contact or a electrical fault were to take place. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Cable_not_connceted.png | file://x:/photopub/docs/0000000557/38e7d00c-09f9-4f20-aa20-1042ab605908.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30d3e3a2_5276_4c84_9181_af4910e12a9b
ELIN-758430-2017 | EL-496000-2017 | 2/17/2017 3:16:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Distributions_exposed_to_weather1.png,Distributions_exposed_to_weather2.png,Distributions_exposed_to_weather3.png,Distributions_exposed_to_weather4.png Distributions are exposed to damage from weather. Shock hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Distributions_exposed_to_weather4.png | file://x:/photopub/docs/0000000559/42816298-1f53-43a8-8d69-023735bf2c5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4695f4e_c07e_4298_b503_8d7538089317
ELIN-758430-2017 | EL-496000-2017 | 2/17/2017 3:16:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Distributions_exposed_to_weather1.png,Distributions_exposed_to_weather2.png,Distributions_exposed_to_weather3.png,Distributions_exposed_to_weather4.png Distributions are exposed to damage from weather. Shock hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Distributions_exposed_to_weather2.png | file://x:/photopub/docs/0000000559/0ad6b4f6-f645-490f-90d9-1859c0fc3951.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4695f4e_c07e_4298_b503_8d7538089317
ELIN-758430-2017 | EL-496000-2017 | 2/17/2017 3:16:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Distributions_exposed_to_weather1.png,Distributions_exposed_to_weather2.png,Distributions_exposed_to_weather3.png,Distributions_exposed_to_weather4.png Distributions are exposed to damage from weather. Shock hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Distributions_exposed_to_weather1.png | file://x:/photopub/docs/0000000559/62930a13-e62c-4fe6-8ee3-81681321084e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4695f4e_c07e_4298_b503_8d7538089317
ELIN-758430-2017 | EL-496000-2017 | 2/17/2017 3:16:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Distributions_exposed_to_weather1.png,Distributions_exposed_to_weather2.png,Distributions_exposed_to_weather3.png,Distributions_exposed_to_weather4.png Distributions are exposed to damage from weather. Shock hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Distributions_exposed_to_weather3.png | file://x:/photopub/docs/0000000559/d3971973-a833-48ad-b5d9-416103a7f841.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4695f4e_c07e_4298_b503_8d7538089317
ELHE-749090-2017 | HE-496794-2017 | 2/1/2017 11:27:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_conductors_connected_to_an_attachment_plug_for_a_light_fixture_1.png,Open_energized_conductors_connected_to_an_attachment_plug_for_a_light_fixture_2.png,Open_energized_conductors_connected_to_an_attachment_plug_for_a_light_fixture_3.png Branch circuit wiring is required to be contained inside of electrical boxes or equipment. Cord connected electrical equipment is required to be provided with proper receptacles for connection of the equipment. This is required to prevent open energized conductors and connections from being energized and exposed to accidental contact from persons, objects, or adjacent electrical components. This installation on a rural residential property had open energized 15A 120V conductors connected to the blades of an attachment cord of a portable light fixture. The conductors were energized and exposed to contact which posed a shock hazard and in close proximity to each other which caused a fire hazard. Left uncorrected this installation posed an immediate shock and fire | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_conductors_connected_to_an_attachment_plug_for_a_light_fixture_2.png | file://x:/photopub/docs/0000000553/4e83586c-fe57-42c8-8561-c431b72622f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__282f0eda_a7f0_4773_9db0_57b12fcd4b0d
GAIN-710141-2016 | GA-469518-2016 | 12/5/2016 9:45:11 AM | ASSESS: GA: Rough-In | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | While site walk through of construction site, rubber hoses scattered all over site in use and not in use, when going to meter, seen a rubber hose on the inner wall not plugged, went to meter pulled the hose to the outdoors and was connected to the live gas meter. If the valve was open as there was no identification of which valve did what natural gas would be released into building causing fire or explosion. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Gas1.png | file://x:/photopub/docs/0000000529/db78ebfa-719e-4b48-aa78-5cd51526a9ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11a4d6f9_df30_4893_9fc8_a0d961768e74
GAIN-710141-2016 | GA-469518-2016 | 12/5/2016 9:45:11 AM | ASSESS: GA: Rough-In | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | While site walk through of construction site, rubber hoses scattered all over site in use and not in use, when going to meter, seen a rubber hose on the inner wall not plugged, went to meter pulled the hose to the outdoors and was connected to the live gas meter. If the valve was open as there was no identification of which valve did what natural gas would be released into building causing fire or explosion. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Gas_2.png | file://x:/photopub/docs/0000000529/660534c8-8f2d-4a82-8adf-f4b484fccf71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11a4d6f9_df30_4893_9fc8_a0d961768e74
GAIN-710141-2016 | GA-469518-2016 | 12/5/2016 9:45:11 AM | ASSESS: GA: Rough-In | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | While site walk through of construction site, rubber hoses scattered all over site in use and not in use, when going to meter, seen a rubber hose on the inner wall not plugged, went to meter pulled the hose to the outdoors and was connected to the live gas meter. If the valve was open as there was no identification of which valve did what natural gas would be released into building causing fire or explosion. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Gas3.png | file://x:/photopub/docs/0000000529/cc85f3e2-eae7-4c0e-ae63-0760fcf88c37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11a4d6f9_df30_4893_9fc8_a0d961768e74
ELIN-748351-2017 | EL-495161-2017 | 2/1/2017 2:46:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Unapproved_wiring_1.png,Unapproved_wiring_2.png,Unapproved_wiring_3.png,Unapproved_wiring_4.png,Unapproved_wiring_5.png,Unapproved_wiring_6.png,Unapproved_wiring_7.png,Unapproved_wiring_8.png,Unapproved_wiring_9.png,Unapproved_wiring_10.png Unapproved wiring and protection of temporary construction circuit, also see pictures under checklist. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Unapproved_wiring_6.png | file://x:/photopub/docs/0000000551/6d1e1ab0-c908-40aa-9e89-6fe8b088e011.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7232870d_223f_490c_806d_22f6c53f4035
ELIN-748351-2017 | EL-495161-2017 | 2/1/2017 2:46:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Unapproved_wiring_1.png,Unapproved_wiring_2.png,Unapproved_wiring_3.png,Unapproved_wiring_4.png,Unapproved_wiring_5.png,Unapproved_wiring_6.png,Unapproved_wiring_7.png,Unapproved_wiring_8.png,Unapproved_wiring_9.png,Unapproved_wiring_10.png Unapproved wiring and protection of temporary construction circuit, also see pictures under checklist. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Unapproved_wiring_9.png | file://x:/photopub/docs/0000000551/481ad4d0-82d1-4a30-9906-86896c94126e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7232870d_223f_490c_806d_22f6c53f4035
ELIN-748351-2017 | EL-495161-2017 | 2/1/2017 2:46:47 PM | ASSESS: EL: Service Connection | png | #asFound Unapproved wiring by unknown individual, energized at time of inspection. | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Unapproved_wiring_1.png,Unapproved_wiring_2.png,Unapproved_wiring_3.png,Unapproved_wiring_4.png,Unapproved_wiring_5.png,Unapproved_wiring_6.png,Unapproved_wiring_7.png,Unapproved_wiring_8.png,Unapproved_wiring_9.png,Unapproved_wiring_10.png Unapproved wiring and protection of temporary construction circuit, also see pictures under checklist. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Unapproved_wiring_10.png | file://x:/photopub/docs/0000000551/9143584f-e6c3-45c3-80a5-d4aa39767322.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7232870d_223f_490c_806d_22f6c53f4035
ELIN-748351-2017 | EL-495161-2017 | 2/1/2017 2:46:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Unapproved_wiring_1.png,Unapproved_wiring_2.png,Unapproved_wiring_3.png,Unapproved_wiring_4.png,Unapproved_wiring_5.png,Unapproved_wiring_6.png,Unapproved_wiring_7.png,Unapproved_wiring_8.png,Unapproved_wiring_9.png,Unapproved_wiring_10.png Unapproved wiring and protection of temporary construction circuit, also see pictures under checklist. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Unapproved_wiring_2.png | file://x:/photopub/docs/0000000551/7249744f-fa98-40c0-81b6-8524704f08ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7232870d_223f_490c_806d_22f6c53f4035
ELIN-748351-2017 | EL-495161-2017 | 2/1/2017 2:46:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Unapproved_wiring_1.png,Unapproved_wiring_2.png,Unapproved_wiring_3.png,Unapproved_wiring_4.png,Unapproved_wiring_5.png,Unapproved_wiring_6.png,Unapproved_wiring_7.png,Unapproved_wiring_8.png,Unapproved_wiring_9.png,Unapproved_wiring_10.png Unapproved wiring and protection of temporary construction circuit, also see pictures under checklist. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Unapproved_wiring_5.png | file://x:/photopub/docs/0000000551/7348f1d4-ee82-4689-a086-5bff51d23843.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7232870d_223f_490c_806d_22f6c53f4035
ELIN-748351-2017 | EL-495161-2017 | 2/1/2017 2:46:47 PM | ASSESS: EL: Service Connection | png | #asFound Unapproved wiring. | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Unapproved_wiring_1.png,Unapproved_wiring_2.png,Unapproved_wiring_3.png,Unapproved_wiring_4.png,Unapproved_wiring_5.png,Unapproved_wiring_6.png,Unapproved_wiring_7.png,Unapproved_wiring_8.png,Unapproved_wiring_9.png,Unapproved_wiring_10.png Unapproved wiring and protection of temporary construction circuit, also see pictures under checklist. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Unapproved_wiring_1.png | file://x:/photopub/docs/0000000551/023451f8-b26f-4f29-a72b-98b6f44c2ca6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7232870d_223f_490c_806d_22f6c53f4035
ELIN-748351-2017 | EL-495161-2017 | 2/1/2017 2:46:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Unapproved_wiring_1.png,Unapproved_wiring_2.png,Unapproved_wiring_3.png,Unapproved_wiring_4.png,Unapproved_wiring_5.png,Unapproved_wiring_6.png,Unapproved_wiring_7.png,Unapproved_wiring_8.png,Unapproved_wiring_9.png,Unapproved_wiring_10.png Unapproved wiring and protection of temporary construction circuit, also see pictures under checklist. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Unapproved_wiring_8.png | file://x:/photopub/docs/0000000551/81ca36d7-1823-44f0-988a-ec5b95809b44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7232870d_223f_490c_806d_22f6c53f4035
ELIN-748351-2017 | EL-495161-2017 | 2/1/2017 2:46:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Unapproved_wiring_1.png,Unapproved_wiring_2.png,Unapproved_wiring_3.png,Unapproved_wiring_4.png,Unapproved_wiring_5.png,Unapproved_wiring_6.png,Unapproved_wiring_7.png,Unapproved_wiring_8.png,Unapproved_wiring_9.png,Unapproved_wiring_10.png Unapproved wiring and protection of temporary construction circuit, also see pictures under checklist. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Unapproved_wiring_3.png | file://x:/photopub/docs/0000000551/bb67ab80-0257-4317-b7b2-3b6e470753f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7232870d_223f_490c_806d_22f6c53f4035
ELIN-748351-2017 | EL-495161-2017 | 2/1/2017 2:46:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Unapproved_wiring_1.png,Unapproved_wiring_2.png,Unapproved_wiring_3.png,Unapproved_wiring_4.png,Unapproved_wiring_5.png,Unapproved_wiring_6.png,Unapproved_wiring_7.png,Unapproved_wiring_8.png,Unapproved_wiring_9.png,Unapproved_wiring_10.png Unapproved wiring and protection of temporary construction circuit, also see pictures under checklist. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Unapproved_wiring_4.png | file://x:/photopub/docs/0000000551/a34a6522-3adb-41e7-84af-8ada236c9781.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7232870d_223f_490c_806d_22f6c53f4035
ELIN-748351-2017 | EL-495161-2017 | 2/1/2017 2:46:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Unapproved_wiring_1.png,Unapproved_wiring_2.png,Unapproved_wiring_3.png,Unapproved_wiring_4.png,Unapproved_wiring_5.png,Unapproved_wiring_6.png,Unapproved_wiring_7.png,Unapproved_wiring_8.png,Unapproved_wiring_9.png,Unapproved_wiring_10.png Unapproved wiring and protection of temporary construction circuit, also see pictures under checklist. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Unapproved_wiring_7.png | file://x:/photopub/docs/0000000551/caf6a831-0453-4b13-8570-53a98ddfa651.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7232870d_223f_490c_806d_22f6c53f4035
GAUP-723319-2016 | UW-480599-2016 | 12/14/2016 11:12:41 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | Vent undersized may lead to products of combustion spillage | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Regulator_.png | file://x:/photopub/docs/0000000531/ba9a291f-d234-4f8c-b9ea-baaf40721837.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b7f9440_d668_435a_999b_1f1907d2cb79
GAUP-723319-2016 | UW-480599-2016 | 12/14/2016 11:12:41 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | Vent undersized may lead to products of combustion spillage | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Vent.png | file://x:/photopub/docs/0000000531/8b1befbb-dec1-4508-b3de-b7574c464c10.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b7f9440_d668_435a_999b_1f1907d2cb79
GAUP-723319-2016 | UW-480599-2016 | 12/14/2016 11:12:41 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | Vent undersized may lead to products of combustion spillage | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Invoice.png | file://x:/photopub/docs/0000000531/8939a665-a15f-455d-982b-b93846995b53.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b7f9440_d668_435a_999b_1f1907d2cb79
ELIN-752809-2017 | EL-493655-2017 | 2/8/2017 11:54:27 AM | ASSESS: EL: Service Connection | png | #asFound Photo showing that the neutral conductor (white conductor) is not isolated from the meter enclosure | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #Meter_base_.png Service change to existing commercial building. Meter bases installed for revenue metering of tenancy units have been installed without isolating the non-load carrying conductors. In a Fault condition the path to carry the fault to earth is broken and a circuit breaker may not function so that the fault could not clear. The result would be equipment damage from thermal damage to the equipment. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Meter_base_.png | file://x:/photopub/docs/0000000555/1271b617-6e67-41b7-91e3-e2b3bdecba05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e22076a9_1d1d_4291_82bb_6d2e45e25fae
ELOP-GAOP-663936-2016 | 1107 | 12/14/2016 10:25:44 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The bag house motor Junction box and Teck connector are not rated for the hazardous location they are operating in. A motor fault during operation of baghouse could ignite the wood dust inside the room. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Motor_connection.png | file://x:/photopub/docs/0000000531/49167836-06df-429c-ada3-628b825d3338.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__D7F850BF_BE51_4C4E_89EA_CC0179F17486
ELIN-738022-2017 | UW-490096-2017 | 1/13/2017 8:58:22 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #6666.png Fire Alarm Panel lock was broken making it possible to open cover and be exposed to live electrical | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 6666.png | file://x:/photopub/docs/0000000543/3c90cf00-cbfe-4c01-8f1d-27e64f6dc272.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7b1eea5_22fb_45e1_ba1a_c79b4a2415bf
GAIN-750638-2017 | GA-490127-2017 | 2/17/2017 9:46:26 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Vent_pipe.png The as-found-condition is that the vent serving a tankless water heater is not certified for use. The potential hazard is that the vent pipe will fail in time, resulting in the release of harmful products of combustion into an occupied space where human health could be adversely affected by emissions such as carbon monoxide. | 3 | Unapproved venting material | Vent_pipe.png | file://x:/photopub/docs/0000000559/bcf17c64-e15f-498f-a797-1691fdff5f69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba291b1b_62b9_4e15_bc3a_e947ba3fa225
ELHE-757919-2017 | HE-501551-2017 | 2/16/2017 10:53:49 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Live_downed_power_lines_in_areas_used_by_public_as_part_of_commercial_health_treatment_center1.png,Live_downed_power_lines_in_areas_used_by_public_as_part_of_commercial_health_treatment_center2.png,Live_downed_power_lines_in_areas_used_by_public_as_part_of_commercial_health_treatment_center3.png an investigation into reports of electrical hazards at a commercial health treatment centre with a 200 amp 240 volt service was conducted. Live overhead lines had been damaged by snow sliding off of a metal roof. The overhead lines were found laying on grade energized in 5 locations. Additionally, trees and shrubs and ropes had been utilized to feed power to 4 cabins for use by patients. The risk to injury to persons was substantial and the potential for damage to structures or forest interface fire was significant. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Live_downed_power_lines_in_areas_used_by_public_as_part_of_commercial_health_treatment_center1.png | file://x:/photopub/docs/0000000559/c04e341a-c73d-4b6e-958c-3ceb9927fd8e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8c02d53_f49e_4c21_a140_3f7032fa14e2
ELHE-757919-2017 | HE-501551-2017 | 2/16/2017 10:53:49 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Live_downed_power_lines_in_areas_used_by_public_as_part_of_commercial_health_treatment_center1.png,Live_downed_power_lines_in_areas_used_by_public_as_part_of_commercial_health_treatment_center2.png,Live_downed_power_lines_in_areas_used_by_public_as_part_of_commercial_health_treatment_center3.png an investigation into reports of electrical hazards at a commercial health treatment centre with a 200 amp 240 volt service was conducted. Live overhead lines had been damaged by snow sliding off of a metal roof. The overhead lines were found laying on grade energized in 5 locations. Additionally, trees and shrubs and ropes had been utilized to feed power to 4 cabins for use by patients. The risk to injury to persons was substantial and the potential for damage to structures or forest interface fire was significant. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Live_downed_power_lines_in_areas_used_by_public_as_part_of_commercial_health_treatment_center2.png | file://x:/photopub/docs/0000000559/cb3ce1cb-9121-4a95-b65f-9066840b83c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8c02d53_f49e_4c21_a140_3f7032fa14e2
ELHE-757919-2017 | HE-501551-2017 | 2/16/2017 10:53:49 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Live_downed_power_lines_in_areas_used_by_public_as_part_of_commercial_health_treatment_center1.png,Live_downed_power_lines_in_areas_used_by_public_as_part_of_commercial_health_treatment_center2.png,Live_downed_power_lines_in_areas_used_by_public_as_part_of_commercial_health_treatment_center3.png an investigation into reports of electrical hazards at a commercial health treatment centre with a 200 amp 240 volt service was conducted. Live overhead lines had been damaged by snow sliding off of a metal roof. The overhead lines were found laying on grade energized in 5 locations. Additionally, trees and shrubs and ropes had been utilized to feed power to 4 cabins for use by patients. The risk to injury to persons was substantial and the potential for damage to structures or forest interface fire was significant. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Live_downed_power_lines_in_areas_used_by_public_as_part_of_commercial_health_treatment_center3.png | file://x:/photopub/docs/0000000559/09170155-3a38-4cdc-a90c-a5008434a4d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8c02d53_f49e_4c21_a140_3f7032fa14e2
ELHE-726255-2016 | HE-482959-2016 | 12/19/2016 3:05:26 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuit wiring is incorrectly installed and exposed to the weather this could lead to a shock or fire hazard if not installed in a safe manner. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_for_exterior_receptacle.png | file://x:/photopub/docs/0000000533/6575a42c-b314-42e0-b126-ebc71a5c9cdd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b1376da8_09a0_415b_8c59_7b287f58acdc
ELHE-726255-2016 | HE-482959-2016 | 12/19/2016 3:05:26 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuit wiring is incorrectly installed and exposed to the weather this could lead to a shock or fire hazard if not installed in a safe manner. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exterior_receptacle.png | file://x:/photopub/docs/0000000533/d61abe2a-4119-4777-828f-3db1daae8ce0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b1376da8_09a0_415b_8c59_7b287f58acdc
GAIN-717708-2016 | GA-451752-2016 | 12/13/2016 11:28:09 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | 1) the vent serving a category 1 appliance with a draft hood is required to be type B-vent 2) approx 15 feet of the vertical vent serving a commercial water heater is type single wall C-vent . 3) A single wall vent could cause low flue gas temperatures which could cause down draft vent spillage and or condensation build up which could cause corrosion/ failure of the vent. | 3 | Unapproved venting material | Single_wall_vent_passing_through_wall.png | file://x:/photopub/docs/0000000530/1f7c3065-69cf-494f-91e2-606afbc1b23b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3882d56e_f0b5_49c5_bac3_6e058b9040ca
GAIN-717708-2016 | GA-451752-2016 | 12/13/2016 11:28:09 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | 1) the vent serving a category 1 appliance with a draft hood is required to be type B-vent 2) approx 15 feet of the vertical vent serving a commercial water heater is type single wall C-vent . 3) A single wall vent could cause low flue gas temperatures which could cause down draft vent spillage and or condensation build up which could cause corrosion/ failure of the vent. | 3 | Unapproved venting material | Water_heater_installed_against_combustible_surface__.png | file://x:/photopub/docs/0000000530/8dff72c9-8601-4f61-b205-4dd1a689f728.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3882d56e_f0b5_49c5_bac3_6e058b9040ca
GAIN-717708-2016 | GA-451752-2016 | 12/13/2016 11:28:09 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | 1) the vent serving a category 1 appliance with a draft hood is required to be type B-vent 2) approx 15 feet of the vertical vent serving a commercial water heater is type single wall C-vent . 3) A single wall vent could cause low flue gas temperatures which could cause down draft vent spillage and or condensation build up which could cause corrosion/ failure of the vent. | 3 | Unapproved venting material | Approx_15_feet_of_vertical_C-vent.png | file://x:/photopub/docs/0000000530/909d8523-4b1f-4796-a713-4718fd289c6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3882d56e_f0b5_49c5_bac3_6e058b9040ca
ELIN-750085-2017 | EL-484992-2016 | 2/2/2017 1:19:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Image_11.png,Image_12.png -Mechanical protection not provided for service conductor conduit. -More than 1.5 m of conductors inside building. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Image_12.png | file://x:/photopub/docs/0000000552/b1cf0fc1-9531-43f9-8360-6937bcc8ebc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bee516ef_d9c3_4873_9238_0fc2172d6b4c
ELIN-750085-2017 | EL-484992-2016 | 2/2/2017 1:19:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Image_11.png,Image_12.png -Mechanical protection not provided for service conductor conduit. -More than 1.5 m of conductors inside building. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Image_11.png | file://x:/photopub/docs/0000000552/aaa21cfc-8b2a-4df6-9675-5277c708b09b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bee516ef_d9c3_4873_9238_0fc2172d6b4c
GAIN-749870-2017 | GA-455545-2016 | 2/17/2017 10:42:55 AM | ASSESS: GA: Final | png | #asFound Edge of walkway to roof edge is less than 6'. Fall hazard exists | GA138 | Equipment unserviceable due to lack of clearance. | 3 | 3 | #Hazard1.png,Hazard2.png Access from narrow rooftop walkway is a hazard due to no guard rails on 3 story roof. There is a fall hazard should someone walk or slip too close to roof edge. | 3 | Equipment unserviceable due to lack of clearance. | Hazard1.png | file://x:/photopub/docs/0000000558/66944605-eaaa-4b1c-a04f-ee95b745602a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bdaef926_983d_47ab_86a3_23db3bf78b30
GAIN-749870-2017 | GA-455545-2016 | 2/17/2017 10:42:55 AM | ASSESS: GA: Final | png | #asFound | GA138 | Equipment unserviceable due to lack of clearance. | 3 | 3 | #Hazard1.png,Hazard2.png Access from narrow rooftop walkway is a hazard due to no guard rails on 3 story roof. There is a fall hazard should someone walk or slip too close to roof edge. | 3 | Equipment unserviceable due to lack of clearance. | Hazard2.png | file://x:/photopub/docs/0000000558/cec850f4-cc17-47bc-b104-f2496d57dada.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bdaef926_983d_47ab_86a3_23db3bf78b30
ELOP-730582-2016 | EL-484852-2016 | 1/4/2017 5:08:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings require proper fillers. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | I.png | file://x:/photopub/docs/0000000538/7726aa7a-61ad-4454-a586-b617a31ed5eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08446B3E_A8FE_4EEE_BA33_9444AB568438
ELOP-730582-2016 | EL-484852-2016 | 1/4/2017 5:08:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings require proper fillers. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | A.png | file://x:/photopub/docs/0000000538/d50b61cc-adb5-4244-908e-644878fc0171.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08446B3E_A8FE_4EEE_BA33_9444AB568438
ELOP-730582-2016 | EL-484852-2016 | 1/4/2017 5:08:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings require proper fillers. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | D.png | file://x:/photopub/docs/0000000538/783ba4b3-ef9a-4afc-a70e-755e188257dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08446B3E_A8FE_4EEE_BA33_9444AB568438
ELOP-730582-2016 | EL-484852-2016 | 1/4/2017 5:08:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings require proper fillers. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | C.png | file://x:/photopub/docs/0000000538/a5b47d75-34cc-4d23-89e2-d25e9d24d4be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08446B3E_A8FE_4EEE_BA33_9444AB568438
ELOP-730582-2016 | EL-484852-2016 | 1/4/2017 5:08:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings require proper fillers. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | F.png | file://x:/photopub/docs/0000000538/6b58abf9-66ea-45c1-af09-114d233f2260.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08446B3E_A8FE_4EEE_BA33_9444AB568438
ELOP-730582-2016 | EL-484852-2016 | 1/4/2017 5:08:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings require proper fillers. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | E.png | file://x:/photopub/docs/0000000538/671ce4bd-7413-49b6-8c57-6a977e5a937f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08446B3E_A8FE_4EEE_BA33_9444AB568438
ELOP-730582-2016 | EL-484852-2016 | 1/4/2017 5:08:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings require proper fillers. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | J.png | file://x:/photopub/docs/0000000538/2d125cd9-13bd-4b7c-b82b-25a0b42b844e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08446B3E_A8FE_4EEE_BA33_9444AB568438
ELOP-730582-2016 | EL-484852-2016 | 1/4/2017 5:08:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings require proper fillers. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | G.png | file://x:/photopub/docs/0000000538/322487dc-1dfd-4925-bb04-1fac936ac21c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08446B3E_A8FE_4EEE_BA33_9444AB568438
ELOP-730582-2016 | EL-484852-2016 | 1/4/2017 5:08:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings require proper fillers. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | L.png | file://x:/photopub/docs/0000000538/8fa19cea-8529-42f8-a249-3dda1f4ee913.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08446B3E_A8FE_4EEE_BA33_9444AB568438
ELOP-730582-2016 | EL-484852-2016 | 1/4/2017 5:08:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings require proper fillers. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | B.png | file://x:/photopub/docs/0000000538/ee4506ce-2612-4a60-be5c-5a8ba8185b3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08446B3E_A8FE_4EEE_BA33_9444AB568438
ELOP-730582-2016 | EL-484852-2016 | 1/4/2017 5:08:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings require proper fillers. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | K.png | file://x:/photopub/docs/0000000538/41783a00-da98-407c-9eef-23709eeb21fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08446B3E_A8FE_4EEE_BA33_9444AB568438
ELOP-730582-2016 | EL-484852-2016 | 1/4/2017 5:08:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings require proper fillers. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | M.png | file://x:/photopub/docs/0000000538/74fb2653-83f7-439c-91e5-aeeb749b006b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08446B3E_A8FE_4EEE_BA33_9444AB568438
ELOP-730582-2016 | EL-484852-2016 | 1/4/2017 5:08:42 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings require proper fillers. This is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | H.png | file://x:/photopub/docs/0000000538/baefeffb-d1ef-4377-b9c8-80082405e85a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08446B3E_A8FE_4EEE_BA33_9444AB568438
ELHE-760730-2017 | HE-503124-2017 | 2/21/2017 3:30:38 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL159 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | 3 | 3 | #Doorswtch.png The door switch inside the top head MCC bucket was jumped out due to problems with the door mechanics. The switch would not always make contact, not allowing the top head to start. This resulted in the programable logic controller energizing the motor mag relay, after the disconnect was turned off, which resulted in an arc flash incident when an operator turned the switch on after locking the switch out to do some work on the machine. | 3 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | Doorswtch.png | file://x:/photopub/docs/0000000561/d8c6dd6a-770d-4ba9-a7b2-4cb117c80c16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff3d500b_3a79_4062_abe3_dcdb000f21d8
ELIN-753283-2017 | EL-431691-2016 | 2/22/2017 10:18:03 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | #Non_TR_rated_receptacles.png Receptacles for dwellings must be tamper resistant, where designated by code, to prevent the insertion of conductive objects into an energized receptacle thereby minimizing the likelihood of accidental electrocution by children | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Non_TR_rated_receptacles.png | file://x:/photopub/docs/0000000561/0675f6e5-403f-4b87-8997-5f6bd57872d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__16cf0505_b0c8_42b0_abcb_bd097c3236bd
BPVOP-708952-2016 | 2250721 | 2/22/2017 7:22:00 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP209 | 5.1.1 Work done: unqualified ind - Maintenance work carried out by contractor or individual qualified to do regulated work in other province but not licensed or qualified for regulated work in British Columbia. | 1 | 1 | #AB_license.png | 1 | 5.1.1 Work done: unqualified ind - Maintenance work carried out by contractor or individual qualified to do regulated work in other province but not licensed or qualified for regulated work in British Columbia. | AB_license.png | file://x:/photopub/docs/0000000561/72a82b94-f14f-4de8-b881-5f6e0acb6cde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e05ea6c2_cf80_4b7d_93bc_23d83a7d66c9
ELIN-742329-2017 | EL-492995-2017 | 1/24/2017 12:53:48 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 4 | 4 | #Panel_board_in_garage_suite.png Panelboards which are not accessible contribute to unsafe use of extension cords and oversizing OC devices by tenants who have no access. | 4 | General Location of equipment does not allow for proper access to disconnecting means | Panel_board_in_garage_suite.png | file://x:/photopub/docs/0000000547/22e14673-8279-4a78-810a-b610150531f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f995a03_1047_4fc3_a25b_3089113554fc
ELIN-737868-2017 | EL-294213-2015 | 1/16/2017 2:35:20 PM | ASSESS: EL: Final | png | #asFound Meter base is attached to pole without use of rated hardware; FSR has opened sealed, energized metering equipment to replace non-rated hardware with rated hardware; meter base is not attached to pole using approved means. | EL203 | Energized work by qualified persons High or Low Voltage: • no procedures • no PPE in place; and • qualified workers performing work. | 4 | 4 | #View01_service1.png,View01_service2.png Certified electrical contractor has opened sealed utility metering equipment while energized in attempt to effect correction of non-compliance without mitigation measures in place and without notifying utility of actions. This poses a serious risk of personal injury (shock/electrocution) and property damage (thermal event) as this portion of the consumer service is not protected by standard overload protection equipment. | 4 | Energized work by qualified persons High or Low Voltage: • no procedures • no PPE in place; and • qualified workers performing work. | View01_service2.png | file://x:/photopub/docs/0000000543/33ff2691-d4d6-4719-9863-56ade43cef29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__344f819a_c1b9_4f7c_83d7_a6b2bdc7d804
ELIN-737868-2017 | EL-294213-2015 | 1/16/2017 2:35:20 PM | ASSESS: EL: Final | png | #asFound General configuration of consumer service equipment; meter base not secured to pole using approved means. | EL203 | Energized work by qualified persons High or Low Voltage: • no procedures • no PPE in place; and • qualified workers performing work. | 4 | 4 | #View01_service1.png,View01_service2.png Certified electrical contractor has opened sealed utility metering equipment while energized in attempt to effect correction of non-compliance without mitigation measures in place and without notifying utility of actions. This poses a serious risk of personal injury (shock/electrocution) and property damage (thermal event) as this portion of the consumer service is not protected by standard overload protection equipment. | 4 | Energized work by qualified persons High or Low Voltage: • no procedures • no PPE in place; and • qualified workers performing work. | View01_service1.png | file://x:/photopub/docs/0000000543/10c19453-55a2-4a98-810b-dad80f777c4c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__344f819a_c1b9_4f7c_83d7_a6b2bdc7d804
ELIN-714473-2016 | EL-431401-2016 | 12/5/2016 4:44:31 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables that are installed for appliances or spare branch circuits in the future must either be terminated into appliances or into junction boxes with covers. This is required so that the cable is safe from accidental contact. This installation has a 15A, 120V cable that is installed into the living room gas fire place and is not terminated into an appliance or a junction box with a cover. The conductors of the cable are covered with electrical tape and the cable is energized. Left uncorrected this is a shock and fire hazard if the tape on the end of the cable falls off or is removed, and conductors are contacted by persons or objects. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exterior_of_new_unit.png | file://x:/photopub/docs/0000000526/c400d1fe-95fa-41c3-bd4e-689cdff6a47a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e00a117_b71a_41da_a889_9575b78bde53
ELIN-714473-2016 | EL-431401-2016 | 12/5/2016 4:44:31 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables that are installed for appliances or spare branch circuits in the future must either be terminated into appliances or into junction boxes with covers. This is required so that the cable is safe from accidental contact. This installation has a 15A, 120V cable that is installed into the living room gas fire place and is not terminated into an appliance or a junction box with a cover. The conductors of the cable are covered with electrical tape and the cable is energized. Left uncorrected this is a shock and fire hazard if the tape on the end of the cable falls off or is removed, and conductors are contacted by persons or objects. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Fire_place_.png | file://x:/photopub/docs/0000000526/7728553a-c20f-4327-a2c6-a53bd9add461.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e00a117_b71a_41da_a889_9575b78bde53
ELIN-714472-2016 | EL-431402-2016 | 12/5/2016 5:05:47 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables that are installed for appliances or spare branch circuits in the future must either be terminated into appliances or into junction boxes with covers. This is required so that the cable is safe from accidental contact. This installation has a 15A, 120V cable that is installed into the living room gas fire place and is not terminated into an appliance or a junction box with a cover. The conductors of the cable are covered with electrical tape and the cable is energized. Left uncorrected this is a shock and fire hazard if the tape on the end of the cable falls off or is removed, and conductors are contacted by persons or objects. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exterior_of_building__.png | file://x:/photopub/docs/0000000526/f5c2963d-cced-4ad5-9781-2fb2c3283640.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89c7d1be_3d58_417f_8f33_d6a19a92ecdd
ELIN-714472-2016 | EL-431402-2016 | 12/5/2016 5:05:47 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables that are installed for appliances or spare branch circuits in the future must either be terminated into appliances or into junction boxes with covers. This is required so that the cable is safe from accidental contact. This installation has a 15A, 120V cable that is installed into the living room gas fire place and is not terminated into an appliance or a junction box with a cover. The conductors of the cable are covered with electrical tape and the cable is energized. Left uncorrected this is a shock and fire hazard if the tape on the end of the cable falls off or is removed, and conductors are contacted by persons or objects. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable_not_installed_in_box_with_a_cover.png | file://x:/photopub/docs/0000000526/285fb4d4-16a6-4598-b85a-2b8b53600b35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89c7d1be_3d58_417f_8f33_d6a19a92ecdd
ELIN-714472-2016 | EL-431402-2016 | 12/5/2016 5:05:47 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables that are installed for appliances or spare branch circuits in the future must either be terminated into appliances or into junction boxes with covers. This is required so that the cable is safe from accidental contact. This installation has a 15A, 120V cable that is installed into the living room gas fire place and is not terminated into an appliance or a junction box with a cover. The conductors of the cable are covered with electrical tape and the cable is energized. Left uncorrected this is a shock and fire hazard if the tape on the end of the cable falls off or is removed, and conductors are contacted by persons or objects. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exterior_of_unit_.png | file://x:/photopub/docs/0000000526/fc533040-1cc5-4bb0-a6e3-1f55849c36ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89c7d1be_3d58_417f_8f33_d6a19a92ecdd
ELIN-714473-2016 | EL-431401-2016 | 12/5/2016 4:44:31 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables that are installed for appliances or spare branch circuits in the future must either be terminated into appliances or into junction boxes with covers. This is required so that the cable is safe from accidental contact. This installation has a 15A, 120V cable that is installed into the living room gas fire place and is not terminated into an appliance or a junction box with a cover. The conductors of the cable are covered with electrical tape and the cable is energized. Left uncorrected this is a shock and fire hazard if the tape on the end of the cable falls off or is removed, and conductors are contacted by persons or objects. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Energized_cable_not_in_a_box.png | file://x:/photopub/docs/0000000526/be5f9f17-825f-4b42-83e5-1f1ed488e9ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e00a117_b71a_41da_a889_9575b78bde53
BPVOP-738859-2017 | 2260318 | 1/17/2017 1:30:14 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP149 | 4.1.1 Incorrect readings/alarms - Refrigerant vapour detector out of calibration | 3 | 3 | #Ovderdue_Leak_detector.png During the inspection of a 303 KW chiller unit it was found that the mechanical room freon leak detector was overdue since Jan 2016. In case of a leak this detector can malfunction and not start the mechanical ventilation and the alarm. | 3 | 4.1.1 Incorrect readings/alarms - Refrigerant vapour detector out of calibration | Ovderdue_Leak_detector.png | file://x:/photopub/docs/0000000545/9d8fc5a3-548f-4d74-bd0c-53da4bc587f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b733e89_71ea_4055_babe_7f8c8764196e
BPVIN-734458-2017 | UW-487635-2017 | 1/6/2017 3:25:08 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Machine mounted air receiver nameplate dated built in 1979 this unit is over 20 years old and requires non-destructive testing to verify that it is still safe for use. Condensed air causes water to form at the bottom of these units resulting in corrosion and if not drained on a regular basis may contribute to an incident. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Air_receiver_nameplate_date_1979.png | file://x:/photopub/docs/0000000540/7583628d-46f2-4186-827f-1dc16004b09d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f57634b_f18f_4592_8b3a_2e67f24a2437
BPVIN-734458-2017 | UW-487635-2017 | 1/6/2017 3:25:08 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Machine mounted air receiver nameplate dated built in 1979 this unit is over 20 years old and requires non-destructive testing to verify that it is still safe for use. Condensed air causes water to form at the bottom of these units resulting in corrosion and if not drained on a regular basis may contribute to an incident. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Air_receiver_overview_photo2.png | file://x:/photopub/docs/0000000540/591ec05d-59c2-4eb4-b1f2-9c187d77ff4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f57634b_f18f_4592_8b3a_2e67f24a2437
BPVIN-734458-2017 | UW-487635-2017 | 1/6/2017 3:25:08 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Machine mounted air receiver nameplate dated built in 1979 this unit is over 20 years old and requires non-destructive testing to verify that it is still safe for use. Condensed air causes water to form at the bottom of these units resulting in corrosion and if not drained on a regular basis may contribute to an incident. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Air__receiver_tank_PRD.png | file://x:/photopub/docs/0000000540/2d3ed11b-057b-4257-8637-219715754aa6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f57634b_f18f_4592_8b3a_2e67f24a2437
BPVIN-734458-2017 | UW-487635-2017 | 1/6/2017 3:25:08 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Machine mounted air receiver nameplate dated built in 1979 this unit is over 20 years old and requires non-destructive testing to verify that it is still safe for use. Condensed air causes water to form at the bottom of these units resulting in corrosion and if not drained on a regular basis may contribute to an incident. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Air_receiver_overview_photo.png | file://x:/photopub/docs/0000000540/7ed040b3-3ab4-4a2a-8a2b-1e58b661dbc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f57634b_f18f_4592_8b3a_2e67f24a2437
ELOP-651497-2016 | 1284 | 1/23/2017 9:53:35 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #No_cover.png In an existing commercial space, a 15amp 120volt outlet was found in an energized state with no cover installed. This can lead to a shock hazard. Pic attached. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | No_cover.png | file://x:/photopub/docs/0000000549/7cd7a3b0-f987-4e28-8635-0c0b6c3af8c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__B2958047_2ED4_4B17_978E_7D3432C81B0D
ELIN-713224-2016 | EL-465107-2016 | 12/2/2016 2:33:19 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Mast_clamp_without_through_bolt_or_carriage_bolts.png | file://x:/photopub/docs/0000000525/693db15e-f623-4c4e-87dd-fd7f7fbd2340.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec30892f_57fb_4a8c_84e1_d0a9f7faf16d
ELIN-713224-2016 | EL-465107-2016 | 12/2/2016 2:33:19 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Lag_and_wood_screws_securing_mast.png | file://x:/photopub/docs/0000000525/8c0414dc-6f4b-4b16-af8e-c90a5d4857eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec30892f_57fb_4a8c_84e1_d0a9f7faf16d
ELIN-715151-2016 | EL-473221-2016 | 12/2/2016 2:10:02 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | The 30 amp 240 volt overcurrent protection utilizes the #8 cu branch circuit for the range where a #12 awg NMSC ( max 20 amp o/c) is spliced without cover, laid on floor with a 30 amp 250 volt receptacle installed in plastic ROUGH in box for a temporary construction heater, this creates both a shock and thermal hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 30_amp_breaker_on__8_cu_.png | file://x:/photopub/docs/0000000525/f8aeb9ef-69a5-4ff7-aaf9-08ef42427293.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5288fb7c_ff91_459c_83fb_61f33e398556
ELIN-715151-2016 | EL-473221-2016 | 12/2/2016 2:10:02 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | The 30 amp 240 volt overcurrent protection utilizes the #8 cu branch circuit for the range where a #12 awg NMSC ( max 20 amp o/c) is spliced without cover, laid on floor with a 30 amp 250 volt receptacle installed in plastic ROUGH in box for a temporary construction heater, this creates both a shock and thermal hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 30_amp_oc_protection_on__12_conductor_exposed_to_mech_damage.png | file://x:/photopub/docs/0000000525/780a5922-f9b6-4958-88f6-99ec4f088f84.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5288fb7c_ff91_459c_83fb_61f33e398556
BPVOP-744503-2017 | 3804585 | 1/24/2017 10:58:43 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Gas_valve.png A gas incident was reported and it was found that the single shut-off gas valve was stuck open. During an Inspection of a Hot Water Boiler with MAWP of 160 psig No Low Water Cutoff Device or flow switch or emergency shut-down. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Gas_valve.png | file://x:/photopub/docs/0000000547/66a55fa5-d940-4f17-91ef-14d0e005f1cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53b163b5_f8af_416a_b382_04483f8ed967
BPVOP-650572-2016 | BPV-091785-2014 | 1/6/2017 11:02:56 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Scale.png | file://x:/photopub/docs/0000000540/e583d079-da76-4d5b-b0a6-4cd99aa277c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c2b2c46_7bd5_4e17_af2d_adf5aa09dfd2
ELIN-745648-2017 | EL-471299-2016 | 2/10/2017 7:01:39 AM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #Unsupported_EMT_tubing.png Support of the EMT tubing is required to prevent stress at termination points so tubing will not come apart when stress is applied. Rule 12-1406 requires the support to be installed within one meter of termination points and the spacing between the supports be in accordance with rule 12-1010 | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Unsupported_EMT_tubing.png | file://x:/photopub/docs/0000000556/0feccb49-4974-4ac9-8d74-f6ed4d7856bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9f3db72_02b0_4d9d_bc24_40b10500ba38
GAHE-720316-2016 | HE-478193-2016 | 12/8/2016 1:18:18 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | Unqualified individual had installed venting on pool heater. The result was leaking venting and single walled venting penetrating roof. This could be hazardous to anyone entering the pool house and would expose them to carbon monoxide. | 3 | Unapproved venting material | 30__gauge_c.png | file://x:/photopub/docs/0000000528/f19cc7b6-e6be-4fae-82ca-674937cab301.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7398f347_a79b_4244_9d4e_c454ff406b9f
GAHE-720316-2016 | HE-478193-2016 | 12/8/2016 1:18:18 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | Unqualified individual had installed venting on pool heater. The result was leaking venting and single walled venting penetrating roof. This could be hazardous to anyone entering the pool house and would expose them to carbon monoxide. | 3 | Unapproved venting material | Direction_of_flow.png | file://x:/photopub/docs/0000000528/0406fcda-282a-4979-a2c0-33979ef6e018.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7398f347_a79b_4244_9d4e_c454ff406b9f
ELIN-730109-2016 | EL-411885-2016 | 12/30/2016 9:05:02 AM | ASSESS: EL: Final | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Exposed DB2 will deteriorate in sunlight and expose energized conductors | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | UG_DB2_emerging_from_ground.png | file://x:/photopub/docs/0000000537/511d3b39-209d-49ca-bed7-e7432349495f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aee5a3fe_33c9_419b_9bfb_3b7fc381470f
ELIN-730109-2016 | EL-411885-2016 | 12/30/2016 9:05:02 AM | ASSESS: EL: Final | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Exposed DB2 will deteriorate in sunlight and expose energized conductors | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | UG_db2_exposed.png | file://x:/photopub/docs/0000000537/6dad5398-01a0-4a40-b454-1c9dad4e5c1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aee5a3fe_33c9_419b_9bfb_3b7fc381470f
GAIN-732221-2017 | GA-480154-2016 | 1/6/2017 11:37:27 AM | ASSESS: GA: Rough-In | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 2 | Clearance to wood studs not sufficient to prevent possible fire from occurring | 2 | Non compliant Type B Vent Clearance | 219_fern.png | file://x:/photopub/docs/0000000539/ae5a3a3c-4a5a-4049-90e1-7f7debd856d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49b8c23f_a0ee_4679_a6a0_2cb4b29f2062
BPVOP-728117-2016 | UW-481617-2016 | 12/21/2016 2:35:37 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | scale.png | file://x:/photopub/docs/0000000534/af23851d-f738-4c4c-a965-6267894cee74.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__822ad1de_a515_4789_a949_12e1dace2464
ELOP-728923-2016 | 634 | 1/4/2017 11:11:24 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | An unapproved cord adapter is connected to a track lighting fixture. This creates a potential fire hazard. | 4 | Conductors, Misuse of flexible cords. | Cord_adapter.png | file://x:/photopub/docs/0000000538/430383f2-0c66-4668-93b2-dd1ad2b5a576.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83ab1237_9b62_4ff9_a53b_5b7c4ded55f8
BPVIN-734130-2017 | BPV-486577-2017 | 1/9/2017 2:40:19 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #steam_generator.png On assessment of a steam boiler with a maximum allowable working pressure of 100 psig, there was no manual operated remote shutdown switch or circuit breaker for the boiler located at boiler room door. In event of an incident, this provides an operator of shutting down the boiler remotely. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | steam_generator.png | file://x:/photopub/docs/0000000540/5d44af63-c4dc-4f29-bea7-180b8eb0a610.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bbfb4098_ca86_4def_931b_13acd51559dc
GAIN-756347-2017 | GA-473966-2016 | 2/15/2017 12:09:27 PM | ASSESS: GA: Final | png | #asFound Swing joint missing on one riser. | GA003 | Provision for expansion Incorrect swing joint | 2 | 2 | #Swing_joint_missing.png If no protection is installed to allow for movement of the ground or riser at time of installation undue stress on piping could potentially cause a leak in the piping system and release gas into the atmosphere. | 2 | Provision for expansion Incorrect swing joint | Swing_joint_missing.png | file://x:/photopub/docs/0000000558/a82ec5fa-af99-4981-b0ef-c6d053755e06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1a0496e_8063_435a_9e43_60de71a08f28
BPVIN-756199-2017 | BPV-497703-2017 | 2/15/2017 7:26:47 AM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Boiler_room_door.png Upon assessment of Potable hot water heater with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the water heater room entrance. In the event of failure of pressure retaining components, the flashing hot water can make it impossible to shutdown heater from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_room_door.png | file://x:/photopub/docs/0000000558/eee929ad-cb30-46e7-b26c-ff1f4bfb3fbe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aedf168d_c4d6_4a4b_a5e3_fe7208866d93
GAIN-753670-2017 | GA-499289-2017 | 2/16/2017 1:47:27 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Clearance_to_combustible_material_not_met_.png Clearance to combustible material not met. Combustible material with in the area outlined in the manufacturers installation instructions may catch fire. | 3 | Clearance to combustible not met | Clearance_to_combustible_material_not_met_.png | file://x:/photopub/docs/0000000558/1044c3b1-c619-4cf7-8091-0e8415ec55c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2c1d24c_6629_46da_92b4_5a80deb9ac56
GAUP-710795-2016 | UW-471698-2016 | 11/28/2016 4:57:50 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA047 | Damage to natural gas or propane distribution systems due to unsafe work practices no release of gas | 2 | 2 | #Broken_weld_point_on_pressure_vessel.png Damage to propane tank. A broken weld onto a pressure vessel could affect the pressure rating of the tank possibly causing a propane leak at the damage point. | 2 | Damage to natural gas or propane distribution systems due to unsafe work practices no release of gas | Broken_weld_point_on_pressure_vessel.png | file://x:/photopub/docs/0000000559/4875f094-2b9a-46c1-9b48-6a69eca706a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__201dc564_f6a1_4d55_9668_6964bb5acaa7
ELIN-725551-2016 | EL-482228-2016 | 12/21/2016 12:56:56 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | Single ground electode. Code requires a minimum of two rods. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | A.png | file://x:/photopub/docs/0000000534/a14d8e47-8a17-4ae9-9c3c-c58526e0a883.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__864a4c67_e676_4891_9cda_e86fc8223db6
GAIN-730768-2016 | GA-485557-2016 | 1/3/2017 12:30:33 PM | ASSESS: GA: Rough-In | png | #asFound | GA038 | Pipe supports not compliant but in place | 1 | 1 | Non compliant pipe supports. | 1 | Pipe supports not compliant but in place | Non_compliant_pipe_supports.png | file://x:/photopub/docs/0000000538/7f7db701-ce44-4330-9f1b-90fe63973aa1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4cf4243_bade_43d6_b7b3_bf742aeeb94b
GAIN-729330-2016 | GA-473820-2016 | 1/3/2017 10:57:13 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | Non compliant vent clearance. Clearance of 3ft horizontally and 15ft vertically must be maintained to prevent damage to gas meter from condensation and ice. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Non_compliant_vent_clearance.png | file://x:/photopub/docs/0000000538/cbff2b77-bffb-4870-9556-6ceb2a1a10c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b2f757c_c35b_4652_873f_9fa8f3457f18
GAHE-727962-2016 | HE-483952-2016 | 12/21/2016 8:02:30 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The as found condition was a decorative fireplace found to be back-drafting into the living space of a residence from the firebox. The as found hazard is products of combustion from gas appliances venting in a living space can readily subject people to deadly carbon monoxide poisoning. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Contractor_document.png | file://x:/photopub/docs/0000000534/01bc7904-7253-4ad1-8ea0-ec6ee1e61f72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21a3d631_6d29_4578_85f0_2a732a250c6a
GAHE-727962-2016 | HE-483952-2016 | 12/21/2016 8:02:30 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The as found condition was a decorative fireplace found to be back-drafting into the living space of a residence from the firebox. The as found hazard is products of combustion from gas appliances venting in a living space can readily subject people to deadly carbon monoxide poisoning. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Fireplace.png | file://x:/photopub/docs/0000000534/27bd5db5-e197-4ce9-a452-e8641548bbda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21a3d631_6d29_4578_85f0_2a732a250c6a
GAHE-740072-2017 | HE-491689-2017 | 1/17/2017 10:09:01 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Canwest1.png,Canwest2.png 5000 USWG propane tank installed part way under power line. This could be create a hazard as the electrical line could be a source of ignition if tank relieved, a leak, or spit valve when filling tank | 4 | Ignition sources present with-in minimum distance required | Canwest2.png | file://x:/photopub/docs/0000000544/5f0b0e76-a810-4559-a43d-5e2a90a5180e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7ffd28f_339f_4dd0_a324_6e0c1449086f
GAHE-740072-2017 | HE-491689-2017 | 1/17/2017 10:09:01 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Canwest1.png,Canwest2.png 5000 USWG propane tank installed part way under power line. This could be create a hazard as the electrical line could be a source of ignition if tank relieved, a leak, or spit valve when filling tank | 4 | Ignition sources present with-in minimum distance required | Canwest1.png | file://x:/photopub/docs/0000000544/f7e574c0-6b00-401b-a5e6-68ca58467722.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7ffd28f_339f_4dd0_a324_6e0c1449086f
PROP-746382-2017 | PR-434164-2016 | 1/25/2017 12:11:30 PM | ASSESS: PR OP: Operational | png | #asFound The sling required to hold the counterweight carries no work load rating. It was made in house of an undetermined time ago. | PR018 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | #Sling_holding_counterweight.png The sling required to hold the counterweight carries no work load rating. It was made in house of an undetermined time ago. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Sling_holding_counterweight.png | file://x:/photopub/docs/0000000549/aede82f4-f8a5-4157-9656-9b33a156c123.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9786e81b_7d67_4fec_8d44_1241a303f234
ELIN-731110-2016 | EL-436975-2016 | 1/3/2017 11:33:05 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Screw type anchor used for long triplex span | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | attachment_point.png | file://x:/photopub/docs/0000000538/e951aa98-1d07-4c47-b9a9-f4574ea4cce5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d2c9934_daf2_42bb_97de_c0d36393fdae
ELOP-GAOP-663933-2016 | 1086 | 12/16/2016 2:42:21 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The area has fine wood dust with filter bags, these are inside a room with a motor that is not approved for possible explosive atmospheres. This could result in a fire if the motor faults when the system is running. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Motor.png | file://x:/photopub/docs/0000000532/b6aac164-18d6-4c40-a1a9-5a1e5b2a6240.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__B708B5BC_D74B_46D6_8BD7_4DB68583B463
ELIN-759481-2017 | EL-493449-2017 | 2/20/2017 2:39:45 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Live_Wires1.png,Live_Wires2.png,Live_Wires3.png,Live_Wires4.png,Live_Wires5.png This assessment found live wires throughout dwelling, that can cause a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Live_Wires4.png | file://x:/photopub/docs/0000000560/15b9f080-2a39-4dcd-912b-7df56dad7f9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c56cee1_5c02_43a3_81cf_5d74a17b9b08
ELIN-759481-2017 | EL-493449-2017 | 2/20/2017 2:39:45 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Live_Wires1.png,Live_Wires2.png,Live_Wires3.png,Live_Wires4.png,Live_Wires5.png This assessment found live wires throughout dwelling, that can cause a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Live_wires2.png | file://x:/photopub/docs/0000000560/a23b0930-d73f-4717-9682-3d5584a5b12d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c56cee1_5c02_43a3_81cf_5d74a17b9b08
ELIN-759481-2017 | EL-493449-2017 | 2/20/2017 2:39:45 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Live_Wires1.png,Live_Wires2.png,Live_Wires3.png,Live_Wires4.png,Live_Wires5.png This assessment found live wires throughout dwelling, that can cause a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Live_Wires3.png | file://x:/photopub/docs/0000000560/5c71f5a3-f4d5-40df-bf48-d798f988ad4c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c56cee1_5c02_43a3_81cf_5d74a17b9b08
ELIN-759481-2017 | EL-493449-2017 | 2/20/2017 2:39:45 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Live_Wires1.png,Live_Wires2.png,Live_Wires3.png,Live_Wires4.png,Live_Wires5.png This assessment found live wires throughout dwelling, that can cause a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Live_wires1.png | file://x:/photopub/docs/0000000560/49b75f53-c13e-4cc2-a61c-c853e7739665.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c56cee1_5c02_43a3_81cf_5d74a17b9b08
ELIN-759481-2017 | EL-493449-2017 | 2/20/2017 2:39:45 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Live_Wires1.png,Live_Wires2.png,Live_Wires3.png,Live_Wires4.png,Live_Wires5.png This assessment found live wires throughout dwelling, that can cause a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Live_wires4.png | file://x:/photopub/docs/0000000560/8d773c00-0c8b-4d56-99bf-754e97e72f55.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c56cee1_5c02_43a3_81cf_5d74a17b9b08
ELIN-759481-2017 | EL-493449-2017 | 2/20/2017 2:39:45 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Live_Wires1.png,Live_Wires2.png,Live_Wires3.png,Live_Wires4.png,Live_Wires5.png This assessment found live wires throughout dwelling, that can cause a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Live_Wires1.png | file://x:/photopub/docs/0000000560/94e2d57c-2dae-4aee-a41a-47fde30bd60d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c56cee1_5c02_43a3_81cf_5d74a17b9b08
BPVOP-720369-2016 | 4793168 | 12/8/2016 1:57:10 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | Risk hazard is very low. Replacement tube installation could not be properly hydrostatic tested due to leaking valves. Tubes are a compression fit into the headers and pose no danger. Proper testing needs to take place after the valves have been replaced. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | Replacement.png | file://x:/photopub/docs/0000000529/3e002959-6e88-4269-9e53-9a7a857ceee6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__193a8e3d_d43f_4093_a6cf_a2a77678ca40
BPVOP-720369-2016 | 4793168 | 12/8/2016 1:57:10 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | Risk hazard is very low. Replacement tube installation could not be properly hydrostatic tested due to leaking valves. Tubes are a compression fit into the headers and pose no danger. Proper testing needs to take place after the valves have been replaced. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | Pluggedtube.png | file://x:/photopub/docs/0000000529/fba0acea-2bbe-4786-9058-e9a5dafbfa23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__193a8e3d_d43f_4093_a6cf_a2a77678ca40
ELIN-734340-2017 | EL-480989-2016 | 1/10/2017 3:57:01 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | #Neutral_not_connected_to_meter_base_.png The required bonding of the neutral conductor to the meter base ensures a low impedance path for the grounding circuit in the event of equipment failure within the meter base | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Neutral_not_connected_to_meter_base_.png | file://x:/photopub/docs/0000000541/633633ee-1450-45c3-b949-fb17091b0ec6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf8bf540_e4f5_4f0c_9903_a343830d28ad
PRIN-711062-2016 | PR-471960-2016 | 12/9/2016 9:37:17 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR020 | Defect that impairs performance: Performance is outside of limitations or is degenerative Reasonably detectable by the maintenance or operation program | 3 | 3 | The actuation of the transition relief plate stopping distance is excessive. This could result in an entrapment hazard if a persons lime or clothing was caught in the transition area. | 3 | Defect that impairs performance: Performance is outside of limitations or is degenerative Reasonably detectable by the maintenance or operation program | Transition_relief_plate.png | file://x:/photopub/docs/0000000530/e602c598-4208-4fb2-b495-e5382e433241.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d300d96d_341c_4795_84c2_c63dd0c5a7b9
BPVIN-681972-2016 | BPV-385115-2016 | 1/13/2017 8:29:30 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP001 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | 5 | 5 | #Safety_Valve.png The pressure relief valve installed on each boiler is set to relieve at a pressure that is "higher" than the maximum allowable working pressure of the boiler. The boiler maybe subjected to over pressurization and lead to a serious failure. The installed safety valve is set at 45 psi and the boiler maximum allowable working pressure is 30 psi. | 5 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | Safety_Valve.png | file://x:/photopub/docs/0000000543/46e19743-7d9e-46d4-8a65-1ceb61cf6be5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23e77498_89a3_4799_9994_2c0bccb387b0
ELIN-714472-2016 | EL-431402-2016 | 12/5/2016 5:05:47 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables that are installed for appliances or spare branch circuits in the future must either be terminated into appliances or into junction boxes with covers. This is required so that the cable is safe from accidental contact. This installation has a 15A, 120V cable that is installed into the living room gas fire place and is not terminated into an appliance or a junction box with a cover. The conductors of the cable are covered with electrical tape and the cable is energized. Left uncorrected this is a shock and fire hazard if the tape on the end of the cable falls off or is removed, and conductors are contacted by persons or objects. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Gas_fire_place_.png | file://x:/photopub/docs/0000000526/aaae1878-e3b4-4128-8265-376334a3b549.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89c7d1be_3d58_417f_8f33_d6a19a92ecdd
ELIN-714472-2016 | EL-431402-2016 | 12/5/2016 5:05:47 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cables that are installed for appliances or spare branch circuits in the future must either be terminated into appliances or into junction boxes with covers. This is required so that the cable is safe from accidental contact. This installation has a 15A, 120V cable that is installed into the living room gas fire place and is not terminated into an appliance or a junction box with a cover. The conductors of the cable are covered with electrical tape and the cable is energized. Left uncorrected this is a shock and fire hazard if the tape on the end of the cable falls off or is removed, and conductors are contacted by persons or objects. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable_is_energized.png | file://x:/photopub/docs/0000000526/6f78968e-643c-457e-a7b5-19bc83f05036.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89c7d1be_3d58_417f_8f33_d6a19a92ecdd
GAHE-742714-2017 | HE-493182-2017 | 1/20/2017 2:34:48 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA089 | No hydrostatic relief in liquid propane system where required | 5 | 5 | #Propane_refuelling_station_1.png,Propane_refuelling_station_2.png,Propane_refuelling_station_3.png The as-found-condition is that a section of black iron pipe containing liquid propane, which could be isolated, does not have a hydrostatic relief valve installed. The hazard is that the liquid propane could expand and rupture the pipe, resulting in the release of liquid propane into the atmosphere. | 5 | No hydrostatic relief in liquid propane system where required | Propane_refuelling_station_3.png | file://x:/photopub/docs/0000000546/a4edcbd5-4943-4da9-b576-3012c1db81b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8eaf0c6e_b65b_41c6_870f_06920e9e5fd8
GAUP-742797-2017 | UW-493256-2017 | 1/20/2017 2:06:50 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Vent_clearance.png The as found hazard is single wall venting system in direct contact with combustible framing. This is a hazard because the excessive heat from the venting system creates a fire risk to the building. | 3 | Non compliant Type C Vent clearance | Vent_clearance.png | file://x:/photopub/docs/0000000546/cb531825-67f1-47a0-8119-b6081191cf7c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40fa3c4d_e195_4911_bfa0_e9fd04b8490d
GAHE-742714-2017 | HE-493182-2017 | 1/20/2017 2:34:48 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA089 | No hydrostatic relief in liquid propane system where required | 5 | 5 | #Propane_refuelling_station_1.png,Propane_refuelling_station_2.png,Propane_refuelling_station_3.png The as-found-condition is that a section of black iron pipe containing liquid propane, which could be isolated, does not have a hydrostatic relief valve installed. The hazard is that the liquid propane could expand and rupture the pipe, resulting in the release of liquid propane into the atmosphere. | 5 | No hydrostatic relief in liquid propane system where required | Propane_refuelling_station_2.png | file://x:/photopub/docs/0000000546/1add7556-bdad-495f-b571-4c24c71449f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8eaf0c6e_b65b_41c6_870f_06920e9e5fd8
GAHE-742714-2017 | HE-493182-2017 | 1/20/2017 2:34:48 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA089 | No hydrostatic relief in liquid propane system where required | 5 | 5 | #Propane_refuelling_station_1.png,Propane_refuelling_station_2.png,Propane_refuelling_station_3.png The as-found-condition is that a section of black iron pipe containing liquid propane, which could be isolated, does not have a hydrostatic relief valve installed. The hazard is that the liquid propane could expand and rupture the pipe, resulting in the release of liquid propane into the atmosphere. | 5 | No hydrostatic relief in liquid propane system where required | Propane_refuelling_station_1.png | file://x:/photopub/docs/0000000546/e04093ab-5b86-4dac-8694-2cc9619dc7e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8eaf0c6e_b65b_41c6_870f_06920e9e5fd8
GAIN-752827-2017 | GA-483815-2016 | 2/16/2017 10:49:43 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Furnace_vent_1.png Section of furnace venting was an unapproved material. This may lead to a failure of the vent allowing for products of combustion to enter the home possibly leading to carbon monoxide poisoning for the occupants. | 3 | Unapproved venting material | Furnace_vent_1.png | file://x:/photopub/docs/0000000558/f90a54a6-7c9c-4345-a55b-90df8bc72df8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a28e886_87ca_437f_8da5_60b874b615df
GAIN-752827-2017 | GA-483815-2016 | 2/16/2017 10:49:43 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Furnace_vent_1.png Section of furnace venting was an unapproved material. This may lead to a failure of the vent allowing for products of combustion to enter the home possibly leading to carbon monoxide poisoning for the occupants. | 3 | Unapproved venting material | Furnace_vent_1.png | file://x:/photopub/docs/0000000558/c4256e15-cb3f-4e72-9a67-0d4ced4e1cc4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a28e886_87ca_437f_8da5_60b874b615df
GAIN-752824-2017 | GA-476621-2016 | 2/16/2017 10:01:23 AM | ASSESS: GA: Final | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 5 | #Unsecured_vent.png Venting system not secured to the furnace flue outlet. If it was to become dislodged the furnace would vent into the residence possibly leading to carbon monoxide poisoning. | 5 | Special venting system not glued or connected as per certified instructions | Unsecured_vent.png | file://x:/photopub/docs/0000000558/a92a54c3-ff6e-46d9-9a0f-3e79ae801cac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a3f1d09_cebb_402b_9ab9_a83b79fa4abf
GAIN-752824-2017 | GA-476621-2016 | 2/16/2017 10:01:23 AM | ASSESS: GA: Final | png | #asFound Vent unsecured to the furnace flue outlet. Removed from socket for picture. | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 5 | #Unsecured_vent.png Venting system not secured to the furnace flue outlet. If it was to become dislodged the furnace would vent into the residence possibly leading to carbon monoxide poisoning. | 5 | Special venting system not glued or connected as per certified instructions | Unsecured_vent.png | file://x:/photopub/docs/0000000558/40f305e5-f739-4ac8-a587-389e4db85101.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a3f1d09_cebb_402b_9ab9_a83b79fa4abf
ELHE-724766-2016 | HE-481737-2016 | 12/15/2016 4:39:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | HV switch shows evidence of corrosion, oxidization, tracking and Arc damage from a flash over event. The hazard is both thermal and shock . | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Paint_chips_located_1_meter_away_from_HV_switch_.png | file://x:/photopub/docs/0000000532/9fefb857-2d98-419c-b286-12c1cbd4559d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73839dbc_b700_47ca_b88a_ec8e89f807ba
ELHE-724766-2016 | HE-481737-2016 | 12/15/2016 4:39:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | HV switch shows evidence of corrosion, oxidization, tracking and Arc damage from a flash over event. The hazard is both thermal and shock . | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Corrosion_and_enclosure_flakes_on_secondary.png | file://x:/photopub/docs/0000000532/60e5c44d-a872-4be2-b777-f1a506a28ed8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73839dbc_b700_47ca_b88a_ec8e89f807ba
ELHE-724766-2016 | HE-481737-2016 | 12/15/2016 4:39:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | HV switch shows evidence of corrosion, oxidization, tracking and Arc damage from a flash over event. The hazard is both thermal and shock . | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Corrosion_on_exterior_of_enclosure_.png | file://x:/photopub/docs/0000000532/1e1c2d93-def4-4f1c-99db-8055882a9a72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73839dbc_b700_47ca_b88a_ec8e89f807ba
ELHE-724766-2016 | HE-481737-2016 | 12/15/2016 4:39:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | HV switch shows evidence of corrosion, oxidization, tracking and Arc damage from a flash over event. The hazard is both thermal and shock . | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Tracking_located_on_insulator__.png | file://x:/photopub/docs/0000000532/8d30de49-5025-4786-a0fe-1d5dd59adf35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73839dbc_b700_47ca_b88a_ec8e89f807ba
ELHE-724766-2016 | HE-481737-2016 | 12/15/2016 4:39:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | HV switch shows evidence of corrosion, oxidization, tracking and Arc damage from a flash over event. The hazard is both thermal and shock . | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Fence_enclosure.png | file://x:/photopub/docs/0000000532/43eeb16c-aa2c-4da6-a220-4facad29e3bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73839dbc_b700_47ca_b88a_ec8e89f807ba
ELHE-724766-2016 | HE-481737-2016 | 12/15/2016 4:39:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | HV switch shows evidence of corrosion, oxidization, tracking and Arc damage from a flash over event. The hazard is both thermal and shock . | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Corrosion_on_the_inside_of_enclosure_.png | file://x:/photopub/docs/0000000532/4656ebd5-1a16-4f95-a013-d81b148f21b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73839dbc_b700_47ca_b88a_ec8e89f807ba
ELHE-724766-2016 | HE-481737-2016 | 12/15/2016 4:39:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | HV switch shows evidence of corrosion, oxidization, tracking and Arc damage from a flash over event. The hazard is both thermal and shock . | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Insulators_that_show_residue_from_flash_over_.png | file://x:/photopub/docs/0000000532/795e2d50-5620-4e46-8433-8f6b24837d08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73839dbc_b700_47ca_b88a_ec8e89f807ba
ELHE-724766-2016 | HE-481737-2016 | 12/15/2016 4:39:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | HV switch shows evidence of corrosion, oxidization, tracking and Arc damage from a flash over event. The hazard is both thermal and shock . | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Name_plate_.png | file://x:/photopub/docs/0000000532/f5a343ef-6109-4da7-a724-f4ff26555443.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73839dbc_b700_47ca_b88a_ec8e89f807ba
ELHE-724766-2016 | HE-481737-2016 | 12/15/2016 4:39:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | HV switch shows evidence of corrosion, oxidization, tracking and Arc damage from a flash over event. The hazard is both thermal and shock . | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Damage_inside_switch_chamber_.png | file://x:/photopub/docs/0000000532/2fb9a7d1-a222-4723-9feb-533be2319b34.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73839dbc_b700_47ca_b88a_ec8e89f807ba
GAIN-701159-2016 | GA-464951-2016 | 12/5/2016 2:09:18 PM | ASSESS: GA: Final | png | #asFound | GA039 | Painting of exterior piping | 1 | 1 |  | 1 | Painting of exterior piping | 361.png | file://x:/photopub/docs/0000000526/f886ea6a-e8bc-4659-8705-a7b495de50cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2de90147_7733_436b_afa4_c656cf001070
ELIN-747421-2017 | EL-147253-2014 | 2/3/2017 8:10:47 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Outside_gfci_protected_receptacle.png The 15 amp 120 volt GFCI receptacle did not trip on testing, the polarity was good. This can become a shock hazard for persons utilizing this outlet in undesirable conditions | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Outside_gfci_protected_receptacle.png | file://x:/photopub/docs/0000000553/6d9bfa22-640e-4473-a248-7170f499681c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd11f031_c314_4a18_b9de_8ef94adac21a
ELOP-751785-2017 | EL-493886-2017 | 2/16/2017 8:59:09 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_JBs_and_Panels1.png,Open_JBs_and_Panels2.png,Open_JBs_and_Panels3.png,Open_JBs_and_Panels4.png,Open_JBs_and_Panels5.png,Open_JBs_and_Panels6.png,Open_JBs_and_Panels7.png,Open_JBs_and_Panels8.png,Open_JBs_and_Panels9.png,Open_JBs_and_Panels10.png 120V 15A junction boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_JBs_and_Panels3.png | file://x:/photopub/docs/0000000559/e019fb23-365b-4c32-873f-a6999b09e8ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9A269E71_3559_45C1_AEEB_F000F396D66E
ELOP-751785-2017 | EL-493886-2017 | 2/16/2017 8:59:09 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_JBs_and_Panels1.png,Open_JBs_and_Panels2.png,Open_JBs_and_Panels3.png,Open_JBs_and_Panels4.png,Open_JBs_and_Panels5.png,Open_JBs_and_Panels6.png,Open_JBs_and_Panels7.png,Open_JBs_and_Panels8.png,Open_JBs_and_Panels9.png,Open_JBs_and_Panels10.png 120V 15A junction boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_JBs_and_Panels7.png | file://x:/photopub/docs/0000000559/492b5f15-1f19-4894-8574-fa04c136fbac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9A269E71_3559_45C1_AEEB_F000F396D66E
ELOP-751785-2017 | EL-493886-2017 | 2/16/2017 8:59:09 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_JBs_and_Panels1.png,Open_JBs_and_Panels2.png,Open_JBs_and_Panels3.png,Open_JBs_and_Panels4.png,Open_JBs_and_Panels5.png,Open_JBs_and_Panels6.png,Open_JBs_and_Panels7.png,Open_JBs_and_Panels8.png,Open_JBs_and_Panels9.png,Open_JBs_and_Panels10.png 120V 15A junction boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_JBs_and_Panels2.png | file://x:/photopub/docs/0000000559/963cef07-70f9-4f19-aee4-bc1ec67b365a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9A269E71_3559_45C1_AEEB_F000F396D66E
ELOP-751785-2017 | EL-493886-2017 | 2/16/2017 8:59:09 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_JBs_and_Panels1.png,Open_JBs_and_Panels2.png,Open_JBs_and_Panels3.png,Open_JBs_and_Panels4.png,Open_JBs_and_Panels5.png,Open_JBs_and_Panels6.png,Open_JBs_and_Panels7.png,Open_JBs_and_Panels8.png,Open_JBs_and_Panels9.png,Open_JBs_and_Panels10.png 120V 15A junction boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_JBs_and_Panels8.png | file://x:/photopub/docs/0000000559/cd150b6f-fee0-4238-bc00-1338ecf32eb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9A269E71_3559_45C1_AEEB_F000F396D66E
ELOP-751785-2017 | EL-493886-2017 | 2/16/2017 8:59:09 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_JBs_and_Panels1.png,Open_JBs_and_Panels2.png,Open_JBs_and_Panels3.png,Open_JBs_and_Panels4.png,Open_JBs_and_Panels5.png,Open_JBs_and_Panels6.png,Open_JBs_and_Panels7.png,Open_JBs_and_Panels8.png,Open_JBs_and_Panels9.png,Open_JBs_and_Panels10.png 120V 15A junction boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_JBs_and_Panels6.png | file://x:/photopub/docs/0000000559/c022be29-b7f2-47ad-8134-b32a104f07aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9A269E71_3559_45C1_AEEB_F000F396D66E
ELOP-751785-2017 | EL-493886-2017 | 2/16/2017 8:59:09 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_JBs_and_Panels1.png,Open_JBs_and_Panels2.png,Open_JBs_and_Panels3.png,Open_JBs_and_Panels4.png,Open_JBs_and_Panels5.png,Open_JBs_and_Panels6.png,Open_JBs_and_Panels7.png,Open_JBs_and_Panels8.png,Open_JBs_and_Panels9.png,Open_JBs_and_Panels10.png 120V 15A junction boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_JBs_and_Panels4.png | file://x:/photopub/docs/0000000559/4b39c112-53b7-42c1-8643-654bf5e0f4d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9A269E71_3559_45C1_AEEB_F000F396D66E
GAUP-726442-2016 | UW-483143-2016 | 12/19/2016 1:43:18 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Fireplace installed to close to combustible material as per manufactures recommended installation. Potential fire hazard. | 3 | Clearance to combustible not met | Fireplace.png | file://x:/photopub/docs/0000000533/7abf33a3-b199-4351-bfec-77eb5420bacc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__558844c3_f610_42bd_9465_9435ed17f840
GAUP-726442-2016 | UW-483143-2016 | 12/19/2016 1:43:18 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Fireplace installed to close to combustible material as per manufactures recommended installation. Potential fire hazard. | 3 | Clearance to combustible not met | Fireplace2.png | file://x:/photopub/docs/0000000533/d2a9a0cc-13b8-421c-88ca-73e778699229.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__558844c3_f610_42bd_9465_9435ed17f840
GAUP-726448-2016 | UW-483147-2016 | 12/19/2016 2:37:35 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Fireplace installed to close to combustibles as per manufactures installation instructions. Potential fire hazard. | 3 | Clearance to combustible not met | Fireplace3.png | file://x:/photopub/docs/0000000533/6bb1813b-1880-478f-9338-a701b0f93a33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea1ebba7_5c02_4606_9260_dfff09c3e239
ELIN-731159-2016 | EL-479862-2016 | 12/30/2016 12:43:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | This assessment found service cable inside a building to be longer than the 1.5M allowed. These cables are extra hazardous because they are the unfused portion between Hydro and the service panel. Damage to the cable poses a shock and fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Service_cable.png | file://x:/photopub/docs/0000000536/e7403af6-38e1-483a-bec4-3a276e541516.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbc4de3b_59ab_4341_90b8_e8778b5b3d65
ELIN-729115-2016 | EL-484690-2016 | 12/30/2016 1:28:35 PM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | In an electrical service the grounded service conductor is required to be connected to a ground electrode at the supply side of the service disconnect only. This is to prevent neutral currents from circulating through the bonding system and to carry any unbalanced fault currents back to the source. In this installation of a 60A electrical panel for a mobile food truck, the bonding strap between the neutral buss and the bonding buss was not removed inside the panel. If an electrical fault was to occur while the truck was connected to a 120/240V power source, there is the potential for unbalanced fault currents to flow through the metal of the electrical panel and the metal of the vehicle. These fault currents are a potential shock hazard for any persons in contact with the vehicle. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Bonding_strap_connected_in_Subpanel.png | file://x:/photopub/docs/0000000537/b7abb7ed-2d0b-4e80-9ee2-46b3c16b61b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e45e8b31_a24d_49b3_8cef_f4d1a959d079
ELIN-729639-2016 | EL-451509-2016 | 12/30/2016 8:52:18 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | A shock hazard exists when live screws are exposed on receptacles due to cover plates that are not installed. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Exposed_wires.png | file://x:/photopub/docs/0000000536/6048a251-37cd-4dd6-8a65-558cee2eb881.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a184871_65fe_4131_bfef_fdef05e79b09
ELIN-729639-2016 | EL-451509-2016 | 12/30/2016 8:52:18 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | A shock hazard exists when live screws are exposed on receptacles due to cover plates that are not installed. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Missing_cover_plate.png | file://x:/photopub/docs/0000000536/5f6708e6-6f53-4594-b120-16d197b36dd7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a184871_65fe_4131_bfef_fdef05e79b09
ELIN-728195-2016 | EL-477733-2016 | 12/30/2016 8:21:38 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | This assessment found the gas pipe installed without the required bond jumper. There is a risk of the pipe becoming energized from internal circuits or lightening; thereby presenting a fire and shock hazard. This assessment found the gas pipe installed without the required bond jumper. There is a risk of the pipe becoming energized from internal circuits or lightening; thereby presenting a fire and shock hazard. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Gas_pipe_not_bonded.png | file://x:/photopub/docs/0000000536/aa8c3b9c-5d32-4195-9571-6aa5ff05bbbc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__819a20c7_d8ee_49ce_a329_6af11ed9f08f
ELIN-759946-2017 | EL-502038-2017 | 2/22/2017 3:37:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Open_panel_energized_.png Panel cover was not in place leaving energized lugs exposed to accidental contact. This condition could lead to potential shock or electrocution. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Open_panel_energized_.png | file://x:/photopub/docs/0000000561/572c72dd-89c1-4ff2-b67b-b9211e1c1201.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56f53903_59e3_4c4e_aaa4_a5dcb8365b49
ELIN-737854-2017 | UW-490021-2017 | 1/12/2017 3:45:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Generator_without_grounding_instlled_on_a_construction_site_1.png,Generator_without_grounding_instlled_on_a_construction_site_2.png,Generator_without_grounding_instlled_on_a_construction_site_3.png,Generator_without_grounding_instlled_on_a_construction_site_4.png,Generator_without_grounding_instlled_on_a_construction_site_5.png,Generator_without_grounding_instlled_on_a_construction_site_6.png Temporary generators used for construction and other purposes are required to be grounded. This is required to keep the electrical equipment and ground around electrical equipment at the same potential during an electrical fault condition or a lightening strike. This intended to minimize the potential difference between the equipment and the earth to reduce/remove a potential shock hazard. This installation of a 14.4 KW 120/240V generator used as temporary power for a commercial construction site does not have the generator grounded. Left uncorrected this is a shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Generator_without_grounding_instlled_on_a_construction_site_4.png | file://x:/photopub/docs/0000000542/b23e6ecb-b4e1-4f83-befd-9dddaf13818e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e448e31_cc5b_481f_a3a3_f83ab23ed782
ELIN-737854-2017 | UW-490021-2017 | 1/12/2017 3:45:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Generator_without_grounding_instlled_on_a_construction_site_1.png,Generator_without_grounding_instlled_on_a_construction_site_2.png,Generator_without_grounding_instlled_on_a_construction_site_3.png,Generator_without_grounding_instlled_on_a_construction_site_4.png,Generator_without_grounding_instlled_on_a_construction_site_5.png,Generator_without_grounding_instlled_on_a_construction_site_6.png Temporary generators used for construction and other purposes are required to be grounded. This is required to keep the electrical equipment and ground around electrical equipment at the same potential during an electrical fault condition or a lightening strike. This intended to minimize the potential difference between the equipment and the earth to reduce/remove a potential shock hazard. This installation of a 14.4 KW 120/240V generator used as temporary power for a commercial construction site does not have the generator grounded. Left uncorrected this is a shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Generator_without_grounding_instlled_on_a_construction_site_6.png | file://x:/photopub/docs/0000000542/055f6589-9cf9-46ff-b346-911168447b10.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e448e31_cc5b_481f_a3a3_f83ab23ed782
ELOP-751785-2017 | EL-493886-2017 | 2/16/2017 8:59:09 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_JBs_and_Panels1.png,Open_JBs_and_Panels2.png,Open_JBs_and_Panels3.png,Open_JBs_and_Panels4.png,Open_JBs_and_Panels5.png,Open_JBs_and_Panels6.png,Open_JBs_and_Panels7.png,Open_JBs_and_Panels8.png,Open_JBs_and_Panels9.png,Open_JBs_and_Panels10.png 120V 15A junction boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_JBs_and_Panels1.png | file://x:/photopub/docs/0000000559/f34cad31-874a-4b08-8c9d-f26c5562c4f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9A269E71_3559_45C1_AEEB_F000F396D66E
ELOP-751785-2017 | EL-493886-2017 | 2/16/2017 8:59:09 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_JBs_and_Panels1.png,Open_JBs_and_Panels2.png,Open_JBs_and_Panels3.png,Open_JBs_and_Panels4.png,Open_JBs_and_Panels5.png,Open_JBs_and_Panels6.png,Open_JBs_and_Panels7.png,Open_JBs_and_Panels8.png,Open_JBs_and_Panels9.png,Open_JBs_and_Panels10.png 120V 15A junction boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_JBs_and_Panels10.png | file://x:/photopub/docs/0000000559/6ebfeb7f-c805-4b42-9e38-68312c08f51a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9A269E71_3559_45C1_AEEB_F000F396D66E
ELOP-751785-2017 | EL-493886-2017 | 2/16/2017 8:59:09 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_JBs_and_Panels1.png,Open_JBs_and_Panels2.png,Open_JBs_and_Panels3.png,Open_JBs_and_Panels4.png,Open_JBs_and_Panels5.png,Open_JBs_and_Panels6.png,Open_JBs_and_Panels7.png,Open_JBs_and_Panels8.png,Open_JBs_and_Panels9.png,Open_JBs_and_Panels10.png 120V 15A junction boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_JBs_and_Panels9.png | file://x:/photopub/docs/0000000559/9128cfb3-5085-4b70-aa23-f5e368abefc7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9A269E71_3559_45C1_AEEB_F000F396D66E
ELOP-751785-2017 | EL-493886-2017 | 2/16/2017 8:59:09 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_JBs_and_Panels1.png,Open_JBs_and_Panels2.png,Open_JBs_and_Panels3.png,Open_JBs_and_Panels4.png,Open_JBs_and_Panels5.png,Open_JBs_and_Panels6.png,Open_JBs_and_Panels7.png,Open_JBs_and_Panels8.png,Open_JBs_and_Panels9.png,Open_JBs_and_Panels10.png 120V 15A junction boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_JBs_and_Panels5.png | file://x:/photopub/docs/0000000559/afb7f259-1968-4ea4-8444-61e1bc2f8993.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9A269E71_3559_45C1_AEEB_F000F396D66E
GAIN-736291-2017 | GA-434749-2016 | 1/30/2017 12:41:43 PM | ASSESS: GA: Final | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | #Furnace_vent.png The as found hazard was a unglued/sealed joint on a furnace venting system. This is a hazard because condensate from the unsealed joint could cause property damage and if the joint were to become separated products of combustion would enter the home creating a elevated risk of carbon monoxide poisoning. | 3 | Leaking or failing special venting system (Minor) | Furnace_vent.png | file://x:/photopub/docs/0000000550/ed9957fa-dda1-4437-8ab6-b5893ed8cf84.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d7d938d_9a51_42cf_b58a_20da6111f159
ELHE-748383-2017 | HE-466243-2016 | 1/30/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #Midspan.png Unapproved and disengaged mid-span points of attachment on a a residential overhead line wiring system. The wire is subject to mechanical damage from excess friction or contact from a vehicle which could lead to a short circuit or fire. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Midspan.png | file://x:/photopub/docs/0000000550/eea26175-a4ec-4e55-bda7-215d03d6de0d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62daf08e_d091_4615_af78_4abecc3b42f4
ELIN-744739-2017 | EL-463448-2016 | 1/30/2017 9:26:52 AM | ASSESS: EL: Final | png | #asFound | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 4 | #No_supports.png In a new commercial space, 3x 15amp 120volt conduits to outlets were found in an energized state with no conduit strapping or supports installed. This can lead to an "Equipment Damage" hazard. Pic attached. | 4 | Installation of electrical equipment Fixtures without suitable support. | No_supports.png | file://x:/photopub/docs/0000000550/b055f900-746b-4109-9376-b104b346b628.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5ce929d_8716_43a4_9908_6fe3f3900bd4
ELIN-747466-2017 | EL-496000-2017 | 1/30/2017 3:08:24 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Panels1.png,Panels2.png None weatherproof panels exposed to weather. Possibility for damage by rain. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Panels1.png | file://x:/photopub/docs/0000000550/97436e47-9ea6-4717-9722-ebcd207c4038.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48622f0a_fea1_4471_ba25_6e4012654483
ELIN-747466-2017 | EL-496000-2017 | 1/30/2017 3:08:24 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Panels1.png,Panels2.png None weatherproof panels exposed to weather. Possibility for damage by rain. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Panels2.png | file://x:/photopub/docs/0000000550/3130b66e-1714-447b-af17-003d54a2b6aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48622f0a_fea1_4471_ba25_6e4012654483
BPVIN-756875-2017 | BPV-500930-2017 | 2/15/2017 10:00:14 AM | ASSESS: BPV IN: Construction Boiler | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | #Where_limit_should_be_installed.png Boiler does not have high temperature manual reset safety device. Without a high temperature manual reset high temperature occurrences would automatically reset without operator knowledge of high temperature activity. High temperature manual reset alerts operators of potential over temperature and over pressure conditions before they could result in damage or injury to personnel. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | Where_limit_should_be_installed.png | file://x:/photopub/docs/0000000558/63c5308e-ebfa-4f30-94bc-6dd9d914fdf1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef971d1e_f543_4f58_a85a_c7c431b6cc9d
ELIN-755499-2017 | EL-493009-2017 | 2/14/2017 2:32:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | #No_bonding_conductor_leaving_panel_for_either_communication_demarc_or_gas_line_bond.png In a new dwelling with a 200 amp 240 volt service, the gas line in the residence was not electrically connected, or bonded, to the grounding system of the residence. This can lead to an induced voltage and current in the gas line that can lead to injury to persons or damage to property | 3 | Equipment Gas line, cast or water pipe has not been bonded | No_bonding_conductor_leaving_panel_for_either_communication_demarc_or_gas_line_bond.png | file://x:/photopub/docs/0000000557/5a66473c-1e07-4915-aa60-59bbb8be21e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b0344ba_e6eb_4805_b9c7_26d5af56d53a
BPVIN-761262-2017 | BPV-501581-2017 | 2/20/2017 5:44:23 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #HP_Boiler_without_remote_shutdown_switch.png Upon assessment of High Pressure steam electric boiler with Heating Surface (HS) of 15 square meters, Maximum Allowable Working Pressure (MAWP) 150psig, it is determined that the lockable remote shutdown switch is not installed. In the event of failure of boiler pressure retaining components, the flashing hot water and/or steam can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | HP_Boiler_without_remote_shutdown_switch.png | file://x:/photopub/docs/0000000560/2bd8c0e8-e64d-4e96-8752-48e736fd82ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__646c774c_1c02_4844_90fa_25fbe52d616e
ELIN-737854-2017 | UW-490021-2017 | 1/12/2017 3:45:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Generator_without_grounding_instlled_on_a_construction_site_1.png,Generator_without_grounding_instlled_on_a_construction_site_2.png,Generator_without_grounding_instlled_on_a_construction_site_3.png,Generator_without_grounding_instlled_on_a_construction_site_4.png,Generator_without_grounding_instlled_on_a_construction_site_5.png,Generator_without_grounding_instlled_on_a_construction_site_6.png Temporary generators used for construction and other purposes are required to be grounded. This is required to keep the electrical equipment and ground around electrical equipment at the same potential during an electrical fault condition or a lightening strike. This intended to minimize the potential difference between the equipment and the earth to reduce/remove a potential shock hazard. This installation of a 14.4 KW 120/240V generator used as temporary power for a commercial construction site does not have the generator grounded. Left uncorrected this is a shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Generator_without_grounding_instlled_on_a_construction_site_1.png | file://x:/photopub/docs/0000000542/1ae6076b-51f0-4577-a710-497024229096.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e448e31_cc5b_481f_a3a3_f83ab23ed782
ELIN-737854-2017 | UW-490021-2017 | 1/12/2017 3:45:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Generator_without_grounding_instlled_on_a_construction_site_1.png,Generator_without_grounding_instlled_on_a_construction_site_2.png,Generator_without_grounding_instlled_on_a_construction_site_3.png,Generator_without_grounding_instlled_on_a_construction_site_4.png,Generator_without_grounding_instlled_on_a_construction_site_5.png,Generator_without_grounding_instlled_on_a_construction_site_6.png Temporary generators used for construction and other purposes are required to be grounded. This is required to keep the electrical equipment and ground around electrical equipment at the same potential during an electrical fault condition or a lightening strike. This intended to minimize the potential difference between the equipment and the earth to reduce/remove a potential shock hazard. This installation of a 14.4 KW 120/240V generator used as temporary power for a commercial construction site does not have the generator grounded. Left uncorrected this is a shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Generator_without_grounding_instlled_on_a_construction_site_5.png | file://x:/photopub/docs/0000000542/bc33f22c-906a-4f06-8a57-eca89fb2aed0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e448e31_cc5b_481f_a3a3_f83ab23ed782
ELIN-737854-2017 | UW-490021-2017 | 1/12/2017 3:45:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Generator_without_grounding_instlled_on_a_construction_site_1.png,Generator_without_grounding_instlled_on_a_construction_site_2.png,Generator_without_grounding_instlled_on_a_construction_site_3.png,Generator_without_grounding_instlled_on_a_construction_site_4.png,Generator_without_grounding_instlled_on_a_construction_site_5.png,Generator_without_grounding_instlled_on_a_construction_site_6.png Temporary generators used for construction and other purposes are required to be grounded. This is required to keep the electrical equipment and ground around electrical equipment at the same potential during an electrical fault condition or a lightening strike. This intended to minimize the potential difference between the equipment and the earth to reduce/remove a potential shock hazard. This installation of a 14.4 KW 120/240V generator used as temporary power for a commercial construction site does not have the generator grounded. Left uncorrected this is a shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Generator_without_grounding_instlled_on_a_construction_site_2.png | file://x:/photopub/docs/0000000542/9b623a87-80dd-415b-a801-37269ea41e3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e448e31_cc5b_481f_a3a3_f83ab23ed782
ELIN-730281-2016 | EL-485198-2016 | 12/29/2016 12:35:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | 3" PVC service conductors conduit installed without expansion joint. Conduit could settle or expand and conductors would become damaged. | 0 | No Created Hazard Identified | No_expnsion_coup.png | file://x:/photopub/docs/0000000536/d8a41e79-d544-49ff-9318-aee1e6e815fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c152c2e1_638b_40a2_8a4a_009f138bbe1e
ELIN-737854-2017 | UW-490021-2017 | 1/12/2017 3:45:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Generator_without_grounding_instlled_on_a_construction_site_1.png,Generator_without_grounding_instlled_on_a_construction_site_2.png,Generator_without_grounding_instlled_on_a_construction_site_3.png,Generator_without_grounding_instlled_on_a_construction_site_4.png,Generator_without_grounding_instlled_on_a_construction_site_5.png,Generator_without_grounding_instlled_on_a_construction_site_6.png Temporary generators used for construction and other purposes are required to be grounded. This is required to keep the electrical equipment and ground around electrical equipment at the same potential during an electrical fault condition or a lightening strike. This intended to minimize the potential difference between the equipment and the earth to reduce/remove a potential shock hazard. This installation of a 14.4 KW 120/240V generator used as temporary power for a commercial construction site does not have the generator grounded. Left uncorrected this is a shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Generator_without_grounding_instlled_on_a_construction_site_3.png | file://x:/photopub/docs/0000000542/74c777be-9e1e-4387-99f1-97a814194092.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e448e31_cc5b_481f_a3a3_f83ab23ed782
BPVIN-748373-2017 | BPV-488313-2017 | 1/30/2017 1:56:39 PM | ASSESS: BPV IN: Final (First Certification) Boiler | pdf | #asFound START-UPS | BP001 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | 5 | 5 | #Photo.pdf During the inspection of 2 DHW Heaters with MAWP of 100 psig I found that the T&P's had the set point at 150 psig. In case of an overpressure the T&P's would not protect the vessels and rupture could occur. | 5 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | Photo.pdf | file://x:/photopub/docs/0000000550/83fbc12f-53df-43d4-976d-59b70f5216de.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62648701_7961_423f_b4cb_1ed300aeb399
EDRI-723059-2016 | ED-380743-2016 | 12/7/2016 3:13:57 PM | ASSESS: ED RI: Extension | png | #asFound | ED055 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | 4 | 4 | On building levels 23-25 there were no handrails protecting people from falling off the edge of the building near the hoist landing. Exiting off the hoist you descend a small ramp that ends adjacent to an unprotected edge of the building creating a very dangerous fall hazard. | 4 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | Unguarded_edge_of_building.png | file://x:/photopub/docs/0000000530/2ef85ec0-629c-434b-9046-a5764822a20c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__363b50ef_5b38_4bcf_b29f_d3df9124e340
ELOP-748220-2017 | 3262 | 2/22/2017 8:26:36 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 | #Storage1.png,Storage2.png,Storage3.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 1 | General Working space or dedicated space is being used for storage | Storage1.png | file://x:/photopub/docs/0000000561/f71a6a40-6445-455f-a9b8-41120ce39776.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4fe028d0_43d3_44f2_9c8d_1db1bb29c922
ELOP-748220-2017 | 3262 | 2/22/2017 8:26:36 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 | #Storage1.png,Storage2.png,Storage3.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 1 | General Working space or dedicated space is being used for storage | Storage2.png | file://x:/photopub/docs/0000000561/45452798-0251-4331-8dca-7de7599085e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4fe028d0_43d3_44f2_9c8d_1db1bb29c922
ELOP-752167-2017 | 654 | 2/22/2017 3:03:56 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | #Jb.png Box covers removed on junction boxes with energized wiring within leaving a potential shock hazard. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Jb.png | file://x:/photopub/docs/0000000561/f5a7b99f-a6b4-4e66-b4a8-5147cab8c3d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1cfe109_cd47_4928_8d80_ad52264036d8
ELOP-752167-2017 | 654 | 2/22/2017 3:03:56 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | #Jb.png Box covers removed on junction boxes with energized wiring within leaving a potential shock hazard. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | JB.png | file://x:/photopub/docs/0000000561/f8cb5f59-c2ae-4394-9bf0-0ea13f19f6f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1cfe109_cd47_4928_8d80_ad52264036d8
ELOP-748220-2017 | 3262 | 2/22/2017 8:26:36 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 | #Storage1.png,Storage2.png,Storage3.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 1 | General Working space or dedicated space is being used for storage | Storage3.png | file://x:/photopub/docs/0000000561/e80b7b4a-a4e1-4e1a-a96f-29663e3ed6c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4fe028d0_43d3_44f2_9c8d_1db1bb29c922
GAIN-742885-2017 | GA-493328-2017 | 2/9/2017 2:09:00 PM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | #Certified_connector_not_approved_for_use_.png Certified connector not approved for use. Connector hose could be damaged by conditions other than those it is certified for. | 2 | Certified appliance connector installed but not approved for application | Certified_connector_not_approved_for_use_.png | file://x:/photopub/docs/0000000555/5231bb7e-bdef-4265-b30a-79b191cedff5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__076efabe_15ee_4aed_b5b2_647aa5ee23b5
ELIN-739964-2017 | EL-490024-2017 | 1/23/2017 10:52:48 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Bad1.png,Bad2.png At time of inspection it was noted that panel covers were removed from energized panels | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Bad1.png | file://x:/photopub/docs/0000000547/534bd08e-5530-41d5-8313-15af980e5613.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f67c8c88_c048_4fe5_ba0e_ac2948d68833
ELIN-739964-2017 | EL-490024-2017 | 1/23/2017 10:52:48 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Bad1.png,Bad2.png At time of inspection it was noted that panel covers were removed from energized panels | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Bad2.png | file://x:/photopub/docs/0000000547/0b14d425-12a3-4e0e-9284-3f990f08167f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f67c8c88_c048_4fe5_ba0e_ac2948d68833
ELIN-749130-2017 | UW-496820-2017 | 1/31/2017 3:24:45 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL276 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | 2 | 2 | #Em_exit21.png,Em_exit22.png Emergency lighting and exit lighting overdue for testing. Exiting the building in the case of power failure or a fire may be prohibitive without properly tested emergency lighting exit systems. | 2 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | Em_exit21.png | file://x:/photopub/docs/0000000550/54dbe402-ba5d-41f7-854d-a25365ee22f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96ed65d9_4d23_49e2_9e0c_9efeb6d156b9
ELIN-749130-2017 | UW-496820-2017 | 1/31/2017 3:24:45 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL276 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | 2 | 2 | #Em_exit21.png,Em_exit22.png Emergency lighting and exit lighting overdue for testing. Exiting the building in the case of power failure or a fire may be prohibitive without properly tested emergency lighting exit systems. | 2 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | Em_exit22.png | file://x:/photopub/docs/0000000550/183a91d7-320a-4ebf-ac08-8ff9d262cb74.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96ed65d9_4d23_49e2_9e0c_9efeb6d156b9
BPVOP-749684-2017 | BPV-331092-2016 | 2/23/2017 10:27:44 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Power_engineer_certifcates_1.png,Power_engineer_certifcates_2.png The person in charge of the plant must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided at the time when the plant was in operation. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Power_engineer_certifcates_2.png | file://x:/photopub/docs/0000000562/2b8a8d53-d525-4b77-95a6-6f398c9fa57a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa25d5ee_e79a_403b_8141_cebe3663f1f5
ELHE-755146-2017 | HE-500156-2017 | 2/10/2017 11:55:22 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Unit a meter disconnected by utility having jurisdiction: meter tamper and neutral not connected: located in enclosed garage: tenant involved | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 4 | 4 | #Service.png 240 v 100 a oh service meter equipment enclosed in non conforming garage and meter tampering occurred: utility disconnect occurred and any interference with energized electrical equipment can lead to shock hazard. | 4 | General Location of equipment does not allow for proper access to disconnecting means | Service.png | file://x:/photopub/docs/0000000556/54363bd8-3ca5-4bf6-97d3-60838f67e79f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad3c1be4_9af9_4e37_9364_06c45f566a3a
BPVOP-749684-2017 | BPV-331092-2016 | 2/23/2017 10:27:44 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Power_engineer_certifcates_1.png,Power_engineer_certifcates_2.png The person in charge of the plant must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided at the time when the plant was in operation. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Power_engineer_certifcates_1.png | file://x:/photopub/docs/0000000562/8ae16057-26e4-4ff3-9c5c-29a7ee841d85.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa25d5ee_e79a_403b_8141_cebe3663f1f5
GAIN-757638-2017 | GA-463717-2016 | 2/20/2017 1:13:21 PM | ASSESS: GA: Rough-In | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Vent.png The as found hazard was a fireplace which had been installed utilizing a venting material which was not approved by the manufacturer. This is a hazard because it creates a risk of potential vent failure or may prohibit the fireplace from effectively venting its products of combustion to the outdoors. | 3 | Appliance not installed according to installation instructions | Vent.png | file://x:/photopub/docs/0000000559/78de1696-5fb7-49b3-a298-f5d7d4d8821e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41e3a29d_4576_4f37_afc3_ab1a02240281
BPVOP-650464-2016 | 2265565 | 2/10/2017 9:30:57 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP222 | 1.2.3 Boiler construction - Code required drain or blow off not provided. | 3 | 3 | #Leaking_blow_off_piping1.png,Leaking_blow_off_piping2.png Blowoff piping for a high pressure steam boiler is required on this system. The blowoff piping was found corroded and holed in two (2) locations. This could lead to possible injury in the boiler room due to burns. | 3 | 1.2.3 Boiler construction - Code required drain or blow off not provided. | Leaking_blow_off_piping2.png | file://x:/photopub/docs/0000000556/b42f7f75-8c5e-44e0-9abb-271793ac3a62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72d3f449_0354_4522_8fb6_e5f57a431e79
BPVOP-650464-2016 | 2265565 | 2/10/2017 9:30:57 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound Holed piping in two (2) locations. | BP222 | 1.2.3 Boiler construction - Code required drain or blow off not provided. | 3 | 3 | #Leaking_blow_off_piping1.png,Leaking_blow_off_piping2.png Blowoff piping for a high pressure steam boiler is required on this system. The blowoff piping was found corroded and holed in two (2) locations. This could lead to possible injury in the boiler room due to burns. | 3 | 1.2.3 Boiler construction - Code required drain or blow off not provided. | Leaking_blow_off_piping1.png | file://x:/photopub/docs/0000000556/763aa4e3-547d-41b9-b25b-0a666ec5b662.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72d3f449_0354_4522_8fb6_e5f57a431e79
ELIN-762708-2017 | EL-500554-2017 | 2/23/2017 2:17:21 PM | ASSESS: EL: Service Connection | png | #asFound ACWU cabling located in close proximity to exterior sheeting. | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #View01_consumer_service_raceway1.png,View01_consumer_service_raceway2.png Consumer service cabling has not been protected from mechanical damage in concealed location. This poses a serious risk of personal injury (shock) and property damage (thermal event) due to mechanical damage occurring to energized supply cabling. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | View01_consumer_service_raceway1.png | file://x:/photopub/docs/0000000562/44da5257-f223-47b4-8130-d49eeff963f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c497d6a_0765_4675_9385_c2f69b045625
ELIN-762708-2017 | EL-500554-2017 | 2/23/2017 2:17:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #View01_consumer_service_raceway1.png,View01_consumer_service_raceway2.png Consumer service cabling has not been protected from mechanical damage in concealed location. This poses a serious risk of personal injury (shock) and property damage (thermal event) due to mechanical damage occurring to energized supply cabling. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | View01_consumer_service_raceway2.png | file://x:/photopub/docs/0000000562/3cf725dc-1eb9-4943-a7db-172712acd5a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c497d6a_0765_4675_9385_c2f69b045625
BPVOP-759659-2017 | 3338529 | 2/20/2017 4:19:52 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP208 | 5.1.0 In service proc/process - Safety officer not notified of repair and repair plan or procedures not accepted by Safety Officer | 3 | 3 | #NEW_SPEED_DRIVE_CABINET.png Upon assessment it is determined that replacement of speed drive with new support structure over chiller increases external load on vessel. Review and certification of repair/alteration by professional engineer competent in design of pressure vessel, confirming repair/alteration is acceptable, is required to determine vessel is safe to operate (Review and certification of repair/alternation shall include calculation of load on vessel due to change and confirmation that load and repair method is safe for operation). Operation of vessel without review and certification as mentioned above may lead to failure of pressure boundary of vessel resulting in incident ( total loss of refrigerant, asphyxiation of personnel in the vicinity). | 3 | 5.1.0 In service proc/process - Safety officer not notified of repair and repair plan or procedures not accepted by Safety Officer | NEW_SPEED_DRIVE_CABINET.png | file://x:/photopub/docs/0000000560/6b50db01-b6a0-499a-9ac9-a5ba53df639d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4507ab77_e93d_49c7_bf56_30088fdb5986
GAHE-762674-2017 | HE-504225-2017 | 2/23/2017 11:20:48 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | #ISC_bungy1.png,ISC_bungy2.png Found the ISC in the open position when no fuel was being pumped and internal safety control (ISC) valve would not close when emergency button pushed because ISC held open with a bungee cord. In the event of a leak or release of gas, supply could not be closed in a safe manner. | 4 | Missing mandatory safety controls | ISC_bungy1.png | file://x:/photopub/docs/0000000561/fd102dc7-1c72-493e-a80c-943c65fe32b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc6b842e_bd6e_4788_86a3_76fb4d1f4315
GAHE-762674-2017 | HE-504225-2017 | 2/23/2017 11:20:48 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | #ISC_bungy1.png,ISC_bungy2.png Found the ISC in the open position when no fuel was being pumped and internal safety control (ISC) valve would not close when emergency button pushed because ISC held open with a bungee cord. In the event of a leak or release of gas, supply could not be closed in a safe manner. | 4 | Missing mandatory safety controls | ISC_bungy2.png | file://x:/photopub/docs/0000000561/3176d5dc-c907-40dd-b467-e8449e77f319.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc6b842e_bd6e_4788_86a3_76fb4d1f4315
ELIN-637781-2016 | EL-162494-2014 | 2/11/2017 3:25:47 PM | ASSESS: EL: Final | pdf | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Certificate_of_Inspection_Permit_EL-310578-2015_Insp_ELIN-474891-2015.pdf | 0 | No Created Hazard Identified | Certificate_of_Inspection_Permit_EL-310578-2015_Insp_ELIN-474891-2015.pdf | file://x:/photopub/docs/0000000557/f7d38109-8a98-47c3-88d4-adf2c1ca36af.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f9eb4e8_9b20_415f_8ae6_1c332017c604
GAIN-705972-2016 | GA-461245-2016 | 2/8/2017 9:40:40 AM | ASSESS: GA: Final | png | #asFound Exhaust and combustion air terminations. | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | #Venting_terminations.png -There is a specific set of instructions for installing BH type venting for this type of equipment and are in the manufacturers instructions and B149-1 the venting and the air intake are not terminated correctly and the exhaust is of the wrong material according to the manufacturers installation instructions. This could cause nuisance shut downs and proper operation of equipment. | 2 | Side wall vent termination not compliant with installation instructions | Venting_terminations.png | file://x:/photopub/docs/0000000555/88449be2-fcc8-4240-9335-9bf9c4b74942.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ca774a1_d0cf_48b2_9722_6584aa41f2a2
BPVOP-743744-2017 | UW-493640-2017 | 1/23/2017 3:27:21 PM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_valve_.png,Safety_valvle2.png BP131 All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve(s). Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valvle2.png | file://x:/photopub/docs/0000000550/c920f0ce-25c7-4018-9460-36b4efded4e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78751349_cdd7_47c6_af1e_f987025d7bc0
BPVOP-725741-2016 | 4969641 | 12/17/2016 1:08:12 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 4 | Safety devices protect equipment from dangerous conditions and damage. Devices must be installed according to all applicable standards. I found a safety device (pressure relief valve on a hot water storage tank) not installed. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | Relief_valve_not_installed.png | file://x:/photopub/docs/0000000532/b4033d89-ff8b-4b2b-b0b1-391eeba9582f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f2c2b3b_5ff5_4b88_be06_3e69156bbe49
ELIN-758247-2017 | EL-501709-2017 | 2/20/2017 2:04:53 PM | ASSESS: EL: Service Connection | png | #asFound No expansion joint has been added to the rigid PVC conduit. | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 2 | #No_expansion_joint_.png Service connection for a new temporary construction service. No provision for expansion of the service conduit has been made. The conduit is installed in Backfilled material and can move. This can cause the conduit to come apart exposing the service conductors. Potential for shock and fire hazard if the conduit separates. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | No_expansion_joint_.png | file://x:/photopub/docs/0000000559/2b1c92fc-ec56-4d28-8797-f497a7017dff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14d425f6_383a_4190_8669_c18c89f1ad01
ELIN-754299-2017 | EL-498886-2017 | 2/20/2017 1:29:50 PM | ASSESS: EL: Final | png | #asFound 120/240 service 100amp conductors are bent sharply over sharp edges of raceway that has no insulated throat or bushing and has no mechanical protection for conductors in pressured contact with sharp edges of service raceway | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | #Service_conductor_on_sharp_edges_of_raceway_with_no_bushing1.png,Service_conductor_on_sharp_edges_of_raceway_with_no_bushing2.png Found 120/240 service 100amp consumer's service conductors are bent sharply over sharp edges of metal service raceway that has no insulated throat or no bushing and has no mechanical protection for conductors that are under pressured contact with sharp edges of service raceway. When service raceway has no insulated mechanical protection bushing for protecting service conductors insulation from damage, the conductors could possibly short circuit to grounded metal and could cause an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Service_conductor_on_sharp_edges_of_raceway_with_no_bushing1.png | file://x:/photopub/docs/0000000560/51361feb-5260-4dc4-83a9-bc4cacda1617.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d92779be_a54c_4a32_a99d_84744851de8b
ELOP-700122-2016 | EL-464952-2016 | 2/15/2017 8:59:16 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 4 | #Wood_attachment_post_rotted_through1.png,Wood_attachment_post_rotted_through2.png Service attachment post has rotted through and failed. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Wood_attachment_post_rotted_through1.png | file://x:/photopub/docs/0000000557/bb5c9ba5-5d46-4665-af5f-a5a01806b597.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13d3a6d7_abf3_46b0_9010_3e7f90269cae
ELOP-700122-2016 | EL-464952-2016 | 2/15/2017 8:59:16 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 4 | #Wood_attachment_post_rotted_through1.png,Wood_attachment_post_rotted_through2.png Service attachment post has rotted through and failed. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Wood_attachment_post_rotted_through2.png | file://x:/photopub/docs/0000000557/ba26ecc1-882b-4715-8574-d35173030660.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13d3a6d7_abf3_46b0_9010_3e7f90269cae
GAHE-753567-2017 | HE-499234-2017 | 2/8/2017 8:37:19 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA162 | Defective appliance accessory or component with imminent risk of injury or property damage | 5 | 5 | #Furnace1.png Report of carbon monoxide poisoning to 1 individual after their CO alarm activated. Upon arrival to site, the gas fired appliances were being removed/replaced as the owner of the property had hired a licensed contractor to replace the heat exchanger and water heater. No immediate causes could be identified, gas fitter will follow up after repairs done. Potential for death had the tenant of the home had not installed a Carbon Monoxide detector. | 5 | Defective appliance accessory or component with imminent risk of injury or property damage | Furnace1.png | file://x:/photopub/docs/0000000555/a47d9640-707c-453e-942c-5e798a0353bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed35bfe7_0a78_4290_b248_1867eed057be
GAIN-723957-2016 | GA-480929-2016 | 1/31/2017 10:26:42 AM | ASSESS: GA: Final | png | #asFound | GA111 | Power vent add-on not interlocked correctly with appliance | 5 | 5 | #Power_vent_and_boiler1.png,Power_vent_and_boiler2.png The as found hazard was a power venter utilized on a pool boiler which had not been interlocked to prevent operation of the boiler in the event of a failure of the power venter. This is a hazard because if the power venter were to fail the boiler would continue to run and the products of combustion including carbon monoxide would spill into the building through the draft hood. | 5 | Power vent add-on not interlocked correctly with appliance | Power_vent_and_boiler1.png | file://x:/photopub/docs/0000000550/54f34487-4591-4822-9c6f-cb24d54d01fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d82bc793_6804_4f10_8da5_b22afb3944dd
GAIN-723957-2016 | GA-480929-2016 | 1/31/2017 10:26:42 AM | ASSESS: GA: Final | png | #asFound | GA111 | Power vent add-on not interlocked correctly with appliance | 5 | 5 | #Power_vent_and_boiler1.png,Power_vent_and_boiler2.png The as found hazard was a power venter utilized on a pool boiler which had not been interlocked to prevent operation of the boiler in the event of a failure of the power venter. This is a hazard because if the power venter were to fail the boiler would continue to run and the products of combustion including carbon monoxide would spill into the building through the draft hood. | 5 | Power vent add-on not interlocked correctly with appliance | Power_vent_and_boiler2.png | file://x:/photopub/docs/0000000550/e85d81c2-e404-4dbc-9266-75cbdfb4a42a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d82bc793_6804_4f10_8da5_b22afb3944dd
ELIN-754299-2017 | EL-498886-2017 | 2/20/2017 1:29:50 PM | ASSESS: EL: Final | png | #asFound 120/240 service 100amp conductors are bent sharply over sharp edges of raceway that has no insulated throat or bushing and has no mechanical protection for conductors in pressured contact with sharp edges of service raceway | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | #Service_conductor_on_sharp_edges_of_raceway_with_no_bushing1.png,Service_conductor_on_sharp_edges_of_raceway_with_no_bushing2.png Found 120/240 service 100amp consumer's service conductors are bent sharply over sharp edges of metal service raceway that has no insulated throat or no bushing and has no mechanical protection for conductors that are under pressured contact with sharp edges of service raceway. When service raceway has no insulated mechanical protection bushing for protecting service conductors insulation from damage, the conductors could possibly short circuit to grounded metal and could cause an electrical fire or shock hazard to people and property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Service_conductor_on_sharp_edges_of_raceway_with_no_bushing2.png | file://x:/photopub/docs/0000000560/70bf4e3e-33bb-4d95-9a4c-d741a825c9a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d92779be_a54c_4a32_a99d_84744851de8b
GAIN-755082-2017 | GA-499209-2017 | 2/17/2017 10:30:30 AM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | #Adapter.png Single wall galvanized vent was crimped and installed into double wall vent. Approved vent connector needs to be used to join single wall to double wall to prevent leaking of products of combustion | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Adapter.png | file://x:/photopub/docs/0000000559/8e0b3bab-81ee-4d2a-bf86-4b359058110a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__04e9da90_2bfd_4078_9abc_2dae33ee6f14
ELIN-756662-2017 | EL-419101-2016 | 2/17/2017 12:03:56 PM | ASSESS: EL: Final | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | #Pnl.png 120/240V 60A combination panel was installed to protect secondary suite circuits. Load calculation done on site with FSR equalled 61.4A which would overload the rating on panel board | 3 | Protection and control Loading of distribution equipment exceeded | Pnl.png | file://x:/photopub/docs/0000000559/2bb89330-472b-46b2-a8a5-a7333462a142.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55ea49ed_fd66_4760_ab78_b1133f92eaf9
GAIN-748837-2017 | GA-496620-2017 | 2/17/2017 2:45:36 PM | ASSESS: GA: Final | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | #Source2.png Propane cylinder with relief and regulator relief installed 4 feet away from source of ignition. Clearances required in the event of a release of gas, to reduce a chance of fire or explosion | 3 | Clearance to combustibles not maintained | Source2.png | file://x:/photopub/docs/0000000559/05fb707a-b9c3-41cd-9100-c9960d66dd22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0b3b51e_04f9_4c6b_8db7_3e0be721deb4
GAUP-756477-2017 | UW-500850-2017 | 2/14/2017 12:11:47 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | #Switch1.png,Switch2.png Pressure switch for combustion blower by passed, and furnace in operation In the event blockage in flue, no safety device to shut down furnace | 4 | Missing mandatory safety controls | Switch1.png | file://x:/photopub/docs/0000000557/e2d9cf6f-c93a-4705-9a9c-1b29604e8ff9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebf8adce_0cd7_438a_bf30_dafb8f625e1e
GAUP-756477-2017 | UW-500850-2017 | 2/14/2017 12:11:47 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | #Switch1.png,Switch2.png Pressure switch for combustion blower by passed, and furnace in operation In the event blockage in flue, no safety device to shut down furnace | 4 | Missing mandatory safety controls | Switch2.png | file://x:/photopub/docs/0000000557/2214fbc6-6f96-491b-9713-e224a58071b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebf8adce_0cd7_438a_bf30_dafb8f625e1e
PRIN-715785-2016 | PR-459184-2016 | 12/15/2016 12:12:51 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR043 | Safety critical monitoring bypassed or failed in manner not reasonably detectable by maintenance / operation program Lift not in operation | 4 | 4 | Conveyor was inoperable at time of inspection. Electric motor and drive controls were incompatible. | 4 | Safety critical monitoring bypassed or failed in manner not reasonably detectable by maintenance / operation program Lift not in operation | Conveyor_inoperable.png | file://x:/photopub/docs/0000000534/4ebe585c-5cb1-4f37-9939-af512bf655cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd16813c_a7f7_48f1_a2ae_791f015f065a
BPVIN-671627-2016 | BPV-442808-2016 | 12/21/2016 9:21:22 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 | Safety relief valve installed in the horizontal position contrary to code and manufacture directions. This may contribute to an incident in the event of an overpressure situation. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Boiler_overview_photo.png | file://x:/photopub/docs/0000000534/d06c809d-2ed9-4aaf-9110-15e76dcd84d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0613feb1_8cc4_41da_ab68_d5276795f1d9
BPVIN-671627-2016 | BPV-442808-2016 | 12/21/2016 9:21:22 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 | Safety relief valve installed in the horizontal position contrary to code and manufacture directions. This may contribute to an incident in the event of an overpressure situation. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Safety_relief_valve_installed_horizontal.png | file://x:/photopub/docs/0000000534/dd6b6887-acc0-49df-bb45-92ccece7aa7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0613feb1_8cc4_41da_ab68_d5276795f1d9
ELIN-753751-2017 | EL-495356-2017 | 2/10/2017 1:59:03 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL050 | Protection and control Loading of distribution equipment exceeded. | 3 | 3 | #Existing_Service_Panel1.png,Existing_Service_Panel2.png,Basement_Suite_subpanel1.png,Basement_Suite_subpanel2.png When adding loads to an existing service or feeder, a load calculation is required to ensure the rating of the existing service or feeder is sufficient to accommodate the existing and newly added loads. This requirement is to protect the electrical service from becoming overloaded. In this installation of a secondary suite added to an existing single family dwelling, a load calculation was not performed. The additional electrical loads of the suite has the potential to create an overload condition on the main electrical panel or service conductors to the the dwelling. The overloading of the electrical panel or service conductors could lead to equipment damage and a possible shock hazard to persons or a fire hazard to the dwelling. | 3 | Protection and control Loading of distribution equipment exceeded. | Existing_Service_Panel1.png | file://x:/photopub/docs/0000000556/749fb5c1-0174-4e07-9fee-2bdc0e215cbb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b55e174_30e3_4f9d_9ca9_71b6529d3018
ELIN-753751-2017 | EL-495356-2017 | 2/10/2017 1:59:03 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL050 | Protection and control Loading of distribution equipment exceeded. | 3 | 3 | #Existing_Service_Panel1.png,Existing_Service_Panel2.png,Basement_Suite_subpanel1.png,Basement_Suite_subpanel2.png When adding loads to an existing service or feeder, a load calculation is required to ensure the rating of the existing service or feeder is sufficient to accommodate the existing and newly added loads. This requirement is to protect the electrical service from becoming overloaded. In this installation of a secondary suite added to an existing single family dwelling, a load calculation was not performed. The additional electrical loads of the suite has the potential to create an overload condition on the main electrical panel or service conductors to the the dwelling. The overloading of the electrical panel or service conductors could lead to equipment damage and a possible shock hazard to persons or a fire hazard to the dwelling. | 3 | Protection and control Loading of distribution equipment exceeded. | Basement_Suite_subpanel1.png | file://x:/photopub/docs/0000000556/2fa9ee04-0bc5-4119-8851-6ead2806b9f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b55e174_30e3_4f9d_9ca9_71b6529d3018
ELIN-753751-2017 | EL-495356-2017 | 2/10/2017 1:59:03 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL050 | Protection and control Loading of distribution equipment exceeded. | 3 | 3 | #Existing_Service_Panel1.png,Existing_Service_Panel2.png,Basement_Suite_subpanel1.png,Basement_Suite_subpanel2.png When adding loads to an existing service or feeder, a load calculation is required to ensure the rating of the existing service or feeder is sufficient to accommodate the existing and newly added loads. This requirement is to protect the electrical service from becoming overloaded. In this installation of a secondary suite added to an existing single family dwelling, a load calculation was not performed. The additional electrical loads of the suite has the potential to create an overload condition on the main electrical panel or service conductors to the the dwelling. The overloading of the electrical panel or service conductors could lead to equipment damage and a possible shock hazard to persons or a fire hazard to the dwelling. | 3 | Protection and control Loading of distribution equipment exceeded. | Basement_Suite_subpanel2.png | file://x:/photopub/docs/0000000556/5e316d9f-147b-4a2f-afd7-720ef21762c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b55e174_30e3_4f9d_9ca9_71b6529d3018
ELIN-753751-2017 | EL-495356-2017 | 2/10/2017 1:59:03 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL050 | Protection and control Loading of distribution equipment exceeded. | 3 | 3 | #Existing_Service_Panel1.png,Existing_Service_Panel2.png,Basement_Suite_subpanel1.png,Basement_Suite_subpanel2.png When adding loads to an existing service or feeder, a load calculation is required to ensure the rating of the existing service or feeder is sufficient to accommodate the existing and newly added loads. This requirement is to protect the electrical service from becoming overloaded. In this installation of a secondary suite added to an existing single family dwelling, a load calculation was not performed. The additional electrical loads of the suite has the potential to create an overload condition on the main electrical panel or service conductors to the the dwelling. The overloading of the electrical panel or service conductors could lead to equipment damage and a possible shock hazard to persons or a fire hazard to the dwelling. | 3 | Protection and control Loading of distribution equipment exceeded. | Existing_Service_Panel2.png | file://x:/photopub/docs/0000000556/354b1088-93b4-4a7c-bd66-0f40c0fdb6cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b55e174_30e3_4f9d_9ca9_71b6529d3018
ELIN-756526-2017 | UW-500455-2017 | 2/10/2017 2:58:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Armoured_cable21.png,Armoured_cable22.png Armoured cables are not terminated in a box thus leaving exposed conductors for future use. While the conductors are de-energized currently they could be energized as there does not appear to be proper lockout. This would create a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Armoured_cable21.png | file://x:/photopub/docs/0000000557/ca3bc473-acf6-4181-bc4c-df33c384104b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__400e3216_3e67_477c_a10e_e823376ed969
ELIN-756525-2017 | UW-500453-2017 | 2/10/2017 3:29:30 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #No_box1.png,No_box2.png Armoured cables without proper box or lockout protection creating a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | No_box1.png | file://x:/photopub/docs/0000000557/303a9da9-5172-4607-a817-688d4845ac35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62f72ac0_be76_4fe7_8f27_c00fd20c78ee
ELIN-756526-2017 | UW-500455-2017 | 2/10/2017 2:58:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Armoured_cable21.png,Armoured_cable22.png Armoured cables are not terminated in a box thus leaving exposed conductors for future use. While the conductors are de-energized currently they could be energized as there does not appear to be proper lockout. This would create a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Armoured_cable22.png | file://x:/photopub/docs/0000000557/4716f98b-d4d9-4449-bcbd-5e2b1bbc0f1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__400e3216_3e67_477c_a10e_e823376ed969
ELIN-756525-2017 | UW-500453-2017 | 2/10/2017 3:29:30 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #No_box1.png,No_box2.png Armoured cables without proper box or lockout protection creating a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | No_box2.png | file://x:/photopub/docs/0000000557/2f096971-9c79-47e8-ba9e-51fd6b8f5799.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62f72ac0_be76_4fe7_8f27_c00fd20c78ee
BPVOP-779379-2017 | 2277712 | 3/21/2017 10:03:25 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #PRD.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 150 psig, I found a Pressure Relief Device not replaced within the last 3 years and no NDE was performed as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | PRD.png | file://x:/photopub/docs/0000000574/2ff4afa7-4c01-4516-8b8f-e35c10c781eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8a10002_0085_4626_88de_3d5032f05293
BPVOP-785325-2017 | 2251535 | 3/7/2017 11:00:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #3.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3.png | file://x:/photopub/docs/0000000579/8173234a-810d-4559-931a-c8e6410d6fca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6180cff0_2002_445c_8b4f_6accc2aa503b
BPVOP-785333-2017 | 2252125 | 3/7/2017 11:00:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #6.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 6.png | file://x:/photopub/docs/0000000579/4baa03e2-be54-40b9-b3ae-bfcf9544d802.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44326de2_71b2_4360_b324_be97918c30c2
BPVOP-785338-2017 | 2252229 | 3/7/2017 11:00:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #9.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 9.png | file://x:/photopub/docs/0000000579/59e4ac9b-0503-435e-b714-406c5b6364eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__36daeae5_6855_4cdb_bb6c_48ae92f4f854
BPVOP-785340-2017 | 2252278 | 3/7/2017 11:00:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #14.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 14.png | file://x:/photopub/docs/0000000579/3eeca901-8e00-4759-8bdd-211f0a87d88b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__902a3074_72d6_424c_bd5e_0bc0123710a5
ELHE-786697-2017 | HE-517918-2017 | 3/28/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Service_closets1.png,Service_closets2.png,Service_closets3.png All five wooden service closets housing electrical supply equipment to mobile homes within a park have deteriorated over time to the point where they are no longer providing adequate protection or support for the distribution equipment mounted within. This creates the potential for equipment damage due to weather, and allows access to unauthorized individuals creating a potential shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Service_closets3.png | file://x:/photopub/docs/0000000585/6fbec284-14d9-4a19-bbff-ef46b40141f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dff4a3fa_189a_4861_83f8_c7646841cb76
ELHE-786697-2017 | HE-517918-2017 | 3/28/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Service_closets1.png,Service_closets2.png,Service_closets3.png All five wooden service closets housing electrical supply equipment to mobile homes within a park have deteriorated over time to the point where they are no longer providing adequate protection or support for the distribution equipment mounted within. This creates the potential for equipment damage due to weather, and allows access to unauthorized individuals creating a potential shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Service_closets1.png | file://x:/photopub/docs/0000000585/33598e93-d72e-4def-b138-f5b03bed6e3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dff4a3fa_189a_4861_83f8_c7646841cb76
ELHE-786697-2017 | HE-517918-2017 | 3/28/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Service_closets1.png,Service_closets2.png,Service_closets3.png All five wooden service closets housing electrical supply equipment to mobile homes within a park have deteriorated over time to the point where they are no longer providing adequate protection or support for the distribution equipment mounted within. This creates the potential for equipment damage due to weather, and allows access to unauthorized individuals creating a potential shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Service_closets2.png | file://x:/photopub/docs/0000000585/b4d0e847-73d5-41b8-b954-438c13f341e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dff4a3fa_189a_4861_83f8_c7646841cb76
ELIN-792933-2017 | EL-481756-2016 | 4/12/2017 | ASSESS: EL: Service Connection | png | #asFound Found two utility separately supplied systems feeding to privately owned systems. One system is 25kv to 600 volts apparatus on one pole with guy wire and another pole with overhead line system is 120/240 volts. The systems are not separated or installed properly or built to CSA standard as required for installation of high voltage and low voltage systems on same property. This electrical equipment could become damaged and is a possible electrical fire or shock hazard to people and property. | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #HV_and_LV_systems_installed_in_proximity_to_each_other_are_too_close_and_not_compliant1.png,HV_and_LV_systems_installed_in_proximity_to_each_other_are_too_close_and_not_compliant2.png,HV_and_LV_systems_installed_in_proximity_to_each_other_are_too_close_and_not_compliant3.png Found two utility separately supplied systems feeding to privately owned systems. One system is 25kv to 600 volts apparatus on one pole with guy wire and another pole with overhead line system is 120/240 volts. The systems are not separated or installed properly or built to CSA standard as required for installation of high voltage and low voltage systems on same property. This electrical equipment could become damaged and is a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | HV_and_LV_systems_installed_in_proximity_to_each_other_are_too_close_and_not_compliant1.png | file://x:/photopub/docs/0000000588/6a5878ad-3e36-415b-b1e5-56299e6cf4d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b313567_8a6b_4b44_a819_0ae716d62755
GAIN-780757-2017 | GA-514927-2017 | 4/21/2017 2:11:12 PM | ASSESS: GA: Final | png | #asFound Relief vent must be piped to the outdoors. Currently it is terminated in an area where ignition sources are present. | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 5 | #Relief_style_2ndstage_regs1.png,Relief_style_2ndstage_regs2.png -Found propane regulator relief vent outlet not piped to a safe location outdoors. In the event of an overpressure situation up stream, this device could begin to vent propane inside the building where potential ignition sources are present. This has the potential for a fire or explosion scenario. | 5 | Relief style regulator/device allowed to vent within building/confined space | Relief_style_2ndstage_regs2.png | file://x:/photopub/docs/0000000590/65ebbe4d-0a96-437f-808b-1de8f9f282dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e282393_130f_4ff7_89ed_e75d0a183de7
ELIN-766798-2017 | EL-506166-2017 | 3/10/2017 11:17:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL138 | Installation of electrical equipment General: boxes are not accessible. | 3 | 3 | #JB_in_ceiling_space.png Junction boxes must remain accessible to allow for maintenance in future situations | 3 | Installation of electrical equipment General: boxes are not accessible. | JB_in_ceiling_space.png | file://x:/photopub/docs/0000000570/d7c8c495-8d0a-4862-af17-880a51cd7cc4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b947172_cac9_45eb_b5db_1d020db6557e
ELIN-750189-2017 | EL-479897-2016 | 3/13/2017 11:28:30 AM | ASSESS: EL: Final | png | #asFound | EL292 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Bv_panel.png what the code is. why the code is.what you saw. what the hazards are. Code requires all unused openings be closed with approved fillers. The main distribution panel is missing two panel fillers. These openings could allow fingers or rodents to enter the panel and cause injury or a fire. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | BV_Panel.png | file://x:/photopub/docs/0000000570/340e2c31-dd83-4a4a-98e3-0bc39d584732.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d66c70f2_8ff0_4bbf_8a06_e5c3b1820088
ELIN-750189-2017 | EL-479897-2016 | 3/13/2017 11:28:30 AM | ASSESS: EL: Final | png | #asFound | EL292 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Bv_panel.png what the code is. why the code is.what you saw. what the hazards are. Code requires all unused openings be closed with approved fillers. The main distribution panel is missing two panel fillers. These openings could allow fingers or rodents to enter the panel and cause injury or a fire. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Bv_panel.png | file://x:/photopub/docs/0000000570/5bc2932c-c379-48b5-952f-d44e0b65bfa6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d66c70f2_8ff0_4bbf_8a06_e5c3b1820088
ELIN-782773-2017 | EL-512481-2017 | 4/7/2017 1:44:11 PM | ASSESS: EL: Final | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #Pole_mounted_panel.png Pole mounted weatherproof panel located very close to grade. Though it is a weatherproof panel, any amount of snow or ice in the winter could envelope the enclosure rendering it inaccessible and potentially causing damage to it. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Pole_mounted_panel.png | file://x:/photopub/docs/0000000583/e2e0cea4-a0c7-4b93-9aad-cd2f45e5ccc4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3fea5489_6439_4cc3_b8b8_9d14580782b6
ELIN-766384-2017 | EL-377952-2016 | 3/22/2017 7:35:02 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Ppl_sched.png,Pnl.png - AFCI breaker not installed to protect circuit from arcing that could lead to fire | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Pnl.png | file://x:/photopub/docs/0000000575/c09de892-73d2-42f8-b47e-53c5340f5388.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad87b645_0649_429b_8ac2_1e656e1b0f0d
ELIN-766384-2017 | EL-377952-2016 | 3/22/2017 7:35:02 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Ppl_sched.png,Pnl.png - AFCI breaker not installed to protect circuit from arcing that could lead to fire | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Ppl_sched.png | file://x:/photopub/docs/0000000575/20bb6fc9-4f04-4dc3-9e96-7d47952a25df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad87b645_0649_429b_8ac2_1e656e1b0f0d
GAIN-788162-2017 | GA-497701-2017 | 4/12/2017 10:20:38 AM | ASSESS: GA: Final | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | #Leaking_special_venting_system.png Leaking special venting system. Improperly sealed special venting system can cause products of combustion into an occupied space leading to possible carbon monoxide exposure. | 3 | Leaking or failing special venting system (Minor) | Leaking_special_venting_system.png | file://x:/photopub/docs/0000000585/3c902379-cc88-46fd-9603-6cf5086f24a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8cce46b8_55fb_48de_816d_c8ba938f2718
BPVOP-770118-2017 | 2263618 | 3/7/2017 4:30:38 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #PRD.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver manufactured in 1953 with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 3 years and no NDT was performed as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | PRD.png | file://x:/photopub/docs/0000000569/64f3c942-cfa1-4ba0-9303-6220aa5509fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28de470e_9c6a_4f41_9e03_182707c7adc4
BPVOP-809344-2017 | 5047782 | 5/4/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Relief_Valve_.png Upon the assessment of a plate HEX with MAWP of 150 psig, was found that the Safety Relief Valve was installed in 2010 and was overdue as per CSA B51. This can contribute to the failure of the pressure vessel safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_.png | file://x:/photopub/docs/0000000597/3f3f93c8-5c4c-4a76-a119-0f4147f7e92b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4147e4bc_6292_44a1_823e_26ef551f8424
BPVOP-812179-2017 | 5047792 | 5/4/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Relief_Valve_2.png Upon the assessment of a Heat Exchanger with MAWP of 125 psig, was found that the Safety Relief Valve was installed in 2011 and was overdue as per CSA B51. This can contribute to the failure of the pressure vessel safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_2.png | file://x:/photopub/docs/0000000597/25c57a17-1d99-4461-9be3-d14b61fe5fc4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b663b0c5_0e63_4700_8be6_f450b4e0b751
ELIN-758646-2017 | EL-395175-2016 | 2/27/2017 11:04:49 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Image_1-21.png,Image_1-22.png Private pole has been notched in the field affecting its certification. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Image_1-22.png | file://x:/photopub/docs/0000000562/99736851-ab63-45fe-9068-d0c09b6cc5a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__468e92f4_d29b_43ab_9b3c_bd0861eedf78
ELIN-758646-2017 | EL-395175-2016 | 2/27/2017 11:04:49 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Image_1-21.png,Image_1-22.png Private pole has been notched in the field affecting its certification. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Image_1-21.png | file://x:/photopub/docs/0000000562/87e4b034-9b62-4f7e-b8a8-0469b270f721.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__468e92f4_d29b_43ab_9b3c_bd0861eedf78
AMOP-798462-2017 | 3194476 | 4/19/2017 8:06:10 PM | ASSESS: AM OP: Periodic | png | #asFound | AM005 | Misalignments that are: Reasonably detectable by maintenance program Likely to propagate slowly toward a derailment condition. | 2 | 2 | #Ballast_undermined_by_Marmots1.png,Ballast_undermined_by_Marmots2.png Marmots have undermined the ballast of the track, could eventually lead to track coming out of alignment. | 2 | Misalignments that are: Reasonably detectable by maintenance program Likely to propagate slowly toward a derailment condition. | Ballast_undermined_by_Marmots1.png | file://x:/photopub/docs/0000000588/a7f62ec7-3c21-4ffc-8195-83af28805b75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d93761a7_d49c_410f_8900_a9d79cef8043
AMOP-798462-2017 | 3194476 | 4/19/2017 8:06:10 PM | ASSESS: AM OP: Periodic | png | #asFound | AM005 | Misalignments that are: Reasonably detectable by maintenance program Likely to propagate slowly toward a derailment condition. | 2 | 2 | #Ballast_undermined_by_Marmots1.png,Ballast_undermined_by_Marmots2.png Marmots have undermined the ballast of the track, could eventually lead to track coming out of alignment. | 2 | Misalignments that are: Reasonably detectable by maintenance program Likely to propagate slowly toward a derailment condition. | Ballast_undermined_by_Marmots2.png | file://x:/photopub/docs/0000000588/6941d2cc-bd01-4198-8846-937da6c46611.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d93761a7_d49c_410f_8900_a9d79cef8043
GAIN-780757-2017 | GA-514927-2017 | 4/21/2017 2:11:12 PM | ASSESS: GA: Final | png | #asFound | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 5 | #Relief_style_2ndstage_regs1.png,Relief_style_2ndstage_regs2.png -Found propane regulator relief vent outlet not piped to a safe location outdoors. In the event of an overpressure situation up stream, this device could begin to vent propane inside the building where potential ignition sources are present. This has the potential for a fire or explosion scenario. | 5 | Relief style regulator/device allowed to vent within building/confined space | Relief_style_2ndstage_regs1.png | file://x:/photopub/docs/0000000590/2ece2239-13ae-44d1-ab61-f4deb514fea4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e282393_130f_4ff7_89ed_e75d0a183de7
ELIN-767058-2017 | EL-496678-2017 | 3/3/2017 1:28:14 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #EMT_within_20mm_of_stud2.png 20 amp, 120/208 volt AC90 cable, and raceways for conductors are installed and maybe subject to mechanical damage. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | EMT_within_20mm_of_stud2.png | file://x:/photopub/docs/0000000566/1e72e6a9-df36-41fe-bf54-d95bd2edf994.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5e9daa8_2659_48f6_a4e1_1e3448950864
ELOP-766650-2017 | 1655 | 3/1/2017 3:17:29 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Armoured_cable.png Shock hazard due to an energized armoured cable without a junction box but does have tape on the conductor ends. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Armoured_cable.png | file://x:/photopub/docs/0000000565/64d98fff-1230-49ff-9e2f-74c874f6cf8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6ab141f_27a2_47cf_9888_485ca79d9654
ELIN-800906-2017 | EL-519249-2017 | 4/24/2017 2:11:48 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #P61.png,P62.png Insulation damage to cables could result in fire causing property damage, injuries and death. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | P62.png | file://x:/photopub/docs/0000000590/ee801266-4a21-41c0-be61-9b70dca45742.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ce39a01_708d_4d45_a131_f46da28302e7
ELIN-800906-2017 | EL-519249-2017 | 4/24/2017 2:11:48 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Cables are not protected from mechanical damage. | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #P61.png,P62.png Insulation damage to cables could result in fire causing property damage, injuries and death. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | P61.png | file://x:/photopub/docs/0000000590/91352d19-6856-41d3-9a1e-cbf4a611e1fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ce39a01_708d_4d45_a131_f46da28302e7
ELIN-766002-2017 | EL-297827-2015 | 3/3/2017 6:22:07 AM | ASSESS: EL: Final | png | #asFound | EL089 | Continuity Bonding; conductor is not properly sized. | 3 | 3 | #Bond_conductor_used_as_ground_conductor.png 120/208 volt to 347/600 volt 75000 volt step up transformer does not have proper grounding conductor installed on the neutral point of the transformer. This is a shock hazard. | 2 | Continuity Bonding; conductor is not properly sized. | Bond_conductor_used_as_ground_conductor.png | file://x:/photopub/docs/0000000565/f2809d26-5a09-4fc9-8327-b109480f75da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9a41221_c5ee_48df_8f41_82116e915a3a
ELIN-783464-2017 | EL-449253-2016 | 3/29/2017 11:00:00 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_Branch_Circuits.png 120 volt 15 amp junction boxes, light outlets and receptacle boxes are open and have not been provided with cover plates or device in areas where the wiring and connections are not yet complete or approved to be energized. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_Branch_Circuits.png | file://x:/photopub/docs/0000000579/e996cc58-f314-4569-b35c-be20611ba321.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__05df7e76_1f4f_44fb_93ac_036aaac39586
ELIN-764306-2017 | EL-491426-2017 | 2/28/2017 12:02:13 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 2 | #H.png Parallel 4/0 aluminum used on 400 amp service. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | H.png | file://x:/photopub/docs/0000000563/74b0eb13-a484-4fa8-b090-a32ee84eff4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8c83569_ff7d_4b7f_8965_f8b1437bf54c
ELIN-765388-2017 | EL-480157-2016 | 3/1/2017 1:01:51 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Exposed_and_energized_.png An energized light switch is hanging out of the device box exposing energized terminals. This could lead to accidental contact of the energized parts and cause an electrical shock or electrocution. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Exposed_and_energized_.png | file://x:/photopub/docs/0000000565/daa9a9e8-b12b-4960-bd05-6a1efbad6fdc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e44cdce_ba7f_4f53_8c36_26cc81f77487
ELIN-810101-2017 | EL-514516-2017 | 5/10/2017 12:11:24 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Cabinet_in_sprinkled_room1.png,Cabinet_in_sprinkled_room2.png,Cabinet_in_sprinkled_room3.png Cabinet is located in a sprinkler protected room but is equipped with dry type connectors which allows water to enter the cabinet. | 0 | No Created Hazard Identified | Cabinet_in_sprinkled_room2.png | file://x:/photopub/docs/0000000599/a7f93a84-dd60-41ea-b722-4d378acef663.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6740e02f_94eb_4892_b6df_84a4b9ab8175
ELIN-810101-2017 | EL-514516-2017 | 5/10/2017 12:11:24 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Cabinet_in_sprinkled_room1.png,Cabinet_in_sprinkled_room2.png,Cabinet_in_sprinkled_room3.png Cabinet is located in a sprinkler protected room but is equipped with dry type connectors which allows water to enter the cabinet. | 0 | No Created Hazard Identified | Cabinet_in_sprinkled_room1.png | file://x:/photopub/docs/0000000599/3047dbac-1c46-4393-a215-fd44c92fc11d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6740e02f_94eb_4892_b6df_84a4b9ab8175
GAIN-760847-2017 | GA-490226-2017 | 2/24/2017 1:09:07 PM | ASSESS: GA: Final | png | #asFound Rating Plate | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Electrical_rating.png This Unit Heater appliance has a certain electrical requirement and this requirement must follow the Canadian electrical code and the manufacturers instructions, If the unit was to fail electrically causing a hazardous situation the circuit the unit heater appliance is attached to shall safely prevent the appliance from doing damage, if this unit were to fail there is no proof that the garage plug circuit it was attached to would safely work to protect damage being done to that circuit. | 3 | Appliance not installed according to installation instructions | Electrical_rating.png | file://x:/photopub/docs/0000000562/a1219811-358e-48cb-a12f-5a8016eba522.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b097b90_b3fb_446c_bd58_45e1d0443be4
ELIN-773139-2017 | EL-509913-2017 | 3/13/2017 4:11:24 PM | ASSESS: EL: Final | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | #Triplex_attached_to_modular.png At an existing commercial works yard, a new 125amp 120/240 modular office unit is installed with the site existing overhead triplex power lines. The modular and all of its internal current carrying and non-current carrying metal components are not effectively bonded to ground. This can lead to a "Shock" hazard. Pic attached | 3 | Continuity Bonding conductor is not observed or broken | Triplex_attached_to_modular.png | file://x:/photopub/docs/0000000571/1564b243-a66a-49ae-9a3b-5008f6e85bc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__069ca1ff_2153_44ea_84d4_aa2e2058cdb9
BPVIN-768065-2017 | UW-507227-2017 | 3/1/2017 1:05:54 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | pdf | #asFound Inspection photos | BP137 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | 4 | 4 | #DHWT_Inspection_Photos.pdf Domestic Hot Water Storage Tank found with a MAWP of 125 psig. Overpressure protection relief had a set pressure at 150 psig. The vessel could exceed the maximum allowable working pressure of 125 psig resulting in a rupture situation. | 4 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | DHWT_Inspection_Photos.pdf | file://x:/photopub/docs/0000000566/f094635f-2c9f-4535-b394-8c834d173688.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__903cafc3_5492_4177_b7e8_61c95b0611fa
BPVIN-768065-2017 | UW-507227-2017 | 3/1/2017 1:05:54 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | pdf | #asFound Inspection photos | BP137 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | 4 | 4 | #DHWT_Inspection_Photos.pdf Domestic Hot Water Storage Tank found with a MAWP of 125 psig. Overpressure protection relief had a set pressure at 150 psig. The vessel could exceed the maximum allowable working pressure of 125 psig resulting in a rupture situation. | 4 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | DHWT_Inspection_Photos.pdf | file://x:/photopub/docs/0000000566/bf8fb6bd-fb5f-4edc-b01e-31eb4a413563.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__903cafc3_5492_4177_b7e8_61c95b0611fa
BPVOP-767826-2017 | 3806984 | 3/1/2017 12:30:42 PM | ASSESS: BPV OP: Re-Certification REF/PV | pdf | #asFound See attached inspection photos. | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PV114266_Inspection_Photos.pdf Unknown when Safety Relief Valve protecting this pressure vessel was last serviced or lift tested. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PV114266_Inspection_Photos.pdf | file://x:/photopub/docs/0000000566/e5dbf7cb-f41b-4aa3-a0dc-4f58c0950e84.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff075ab7_177b_4a3b_b106_04591d80e02a
BPVOP-767826-2017 | 3806984 | 3/1/2017 12:30:42 PM | ASSESS: BPV OP: Re-Certification REF/PV | pdf | #asFound Inspection photos | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PV114266_Inspection_Photos.pdf Unknown when Safety Relief Valve protecting this pressure vessel was last serviced or lift tested. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PV114266_Inspection_Photos.pdf | file://x:/photopub/docs/0000000566/5f4251b2-4283-4ae7-8c3a-990cf3b1c81c.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff075ab7_177b_4a3b_b106_04591d80e02a
GAIN-743869-2017 | GA-493704-2017 | 2/8/2017 7:32:54 AM | ASSESS: GA: Final | png | #asFound Combustion Air Missing | GA122 | Combustion air supply missing | 4 | 4 | #Combustion_Air.png No combustion air could cause the water heater to spill product of combustion in the space which could expose the occupants to carbon monoxide. | 4 | Combustion air supply missing | Combustion_Air.png | file://x:/photopub/docs/0000000570/af5f29b2-f3fe-47fd-a74a-803ce84d51a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0e51fc6_894c_4d85_9352_edf96800a95f
ELIN-810101-2017 | EL-514516-2017 | 5/10/2017 12:11:24 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Cabinet_in_sprinkled_room1.png,Cabinet_in_sprinkled_room2.png,Cabinet_in_sprinkled_room3.png Cabinet is located in a sprinkler protected room but is equipped with dry type connectors which allows water to enter the cabinet. | 0 | No Created Hazard Identified | Cabinet_in_sprinkled_room3.png | file://x:/photopub/docs/0000000599/118f37d2-6ec1-4c21-9c93-f56f638e7f37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6740e02f_94eb_4892_b6df_84a4b9ab8175
ELOP-655967-2016 | EL-002474-2013 | 5/10/2017 5:39:16 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Deteriorated_wood_enclosure_and_electrical_equipment1.png,Deteriorated_wood_enclosure_and_electrical_equipment2.png,Deteriorated_wood_enclosure_and_electrical_equipment3.png,Deteriorated_wood_enclosure_and_electrical_equipment4.png,Deteriorated_wood_enclosure_and_electrical_equipment5.png,Deteriorated_wood_enclosure_and_electrical_equipment6.png Electrical equipment installed outdoors in a location where it is subject to the weather is required to be adequately protected from the weather either by being installed in an approved weather proof cabinet or being approved for installation in an outdoor location. This is required to protect the equipment from getting wet which can damage and deteriorate the equipment. This installation at a mobile home park has 60A 120/240V sub-service equipment, a light, switch, and receptacle installed inside of a wooden enclosure. The enclosure is rotten, the door has fallen off, and the roof no longer prevents water from entering the wooden enclosure. This has caused the equip | 3 | General Equipment is not approved for the specific use | Deteriorated_wood_enclosure_and_electrical_equipment2.png | file://x:/photopub/docs/0000000599/c0d4155b-ae7f-4988-8fd9-e0d8c8665e4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2029AE99_6602_4BD9_B4E2_220443DC5F82
ELOP-655967-2016 | EL-002474-2013 | 5/10/2017 5:39:16 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Deteriorated_wood_enclosure_and_electrical_equipment1.png,Deteriorated_wood_enclosure_and_electrical_equipment2.png,Deteriorated_wood_enclosure_and_electrical_equipment3.png,Deteriorated_wood_enclosure_and_electrical_equipment4.png,Deteriorated_wood_enclosure_and_electrical_equipment5.png,Deteriorated_wood_enclosure_and_electrical_equipment6.png Electrical equipment installed outdoors in a location where it is subject to the weather is required to be adequately protected from the weather either by being installed in an approved weather proof cabinet or being approved for installation in an outdoor location. This is required to protect the equipment from getting wet which can damage and deteriorate the equipment. This installation at a mobile home park has 60A 120/240V sub-service equipment, a light, switch, and receptacle installed inside of a wooden enclosure. The enclosure is rotten, the door has fallen off, and the roof no longer prevents water from entering the wooden enclosure. This has caused the equip | 3 | General Equipment is not approved for the specific use | Deteriorated_wood_enclosure_and_electrical_equipment1.png | file://x:/photopub/docs/0000000599/1f8df9ad-b7fb-4c4b-8d12-531a8760b11a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2029AE99_6602_4BD9_B4E2_220443DC5F82
ELIN-808327-2017 | EL-351160-2016 | 5/9/2017 | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Bare_lamp_fixtures_installed_in_clothes_closets1.png,Bare_lamp_fixtures_installed_in_clothes_closets2.png,Bare_lamp_fixtures_installed_in_clothes_closets3.png,Bare_lamp_fixtures_installed_in_clothes_closets4.png,Bare_lamp_fixtures_installed_in_clothes_closets5.png Light fixtures installed in clothes closets are not permitted to be bare lamp type fixtures. This is to prevent combustible materials from coming into contact with light bulbs. This installation for a new house has light fixtures installed in the clothes closets that are bare bulb type fixtures. Left uncorrected this is a fire hazard if combustible materials contact hot light bulbs inside of clothes closets. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Bare_lamp_fixtures_installed_in_clothes_closets2.png | file://x:/photopub/docs/0000000599/a8e28e64-983b-46fe-af16-682de6470eb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__86b1817f_8401_42b9_a803_48a576a855ad
ELIN-808327-2017 | EL-351160-2016 | 5/9/2017 | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Bare_lamp_fixtures_installed_in_clothes_closets1.png,Bare_lamp_fixtures_installed_in_clothes_closets2.png,Bare_lamp_fixtures_installed_in_clothes_closets3.png,Bare_lamp_fixtures_installed_in_clothes_closets4.png,Bare_lamp_fixtures_installed_in_clothes_closets5.png Light fixtures installed in clothes closets are not permitted to be bare lamp type fixtures. This is to prevent combustible materials from coming into contact with light bulbs. This installation for a new house has light fixtures installed in the clothes closets that are bare bulb type fixtures. Left uncorrected this is a fire hazard if combustible materials contact hot light bulbs inside of clothes closets. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Bare_lamp_fixtures_installed_in_clothes_closets5.png | file://x:/photopub/docs/0000000599/b6d350d9-abdc-4a8e-9abf-d62d23f5257d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__86b1817f_8401_42b9_a803_48a576a855ad
ELIN-808327-2017 | EL-351160-2016 | 5/9/2017 | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Bare_lamp_fixtures_installed_in_clothes_closets1.png,Bare_lamp_fixtures_installed_in_clothes_closets2.png,Bare_lamp_fixtures_installed_in_clothes_closets3.png,Bare_lamp_fixtures_installed_in_clothes_closets4.png,Bare_lamp_fixtures_installed_in_clothes_closets5.png Light fixtures installed in clothes closets are not permitted to be bare lamp type fixtures. This is to prevent combustible materials from coming into contact with light bulbs. This installation for a new house has light fixtures installed in the clothes closets that are bare bulb type fixtures. Left uncorrected this is a fire hazard if combustible materials contact hot light bulbs inside of clothes closets. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Bare_lamp_fixtures_installed_in_clothes_closets3.png | file://x:/photopub/docs/0000000599/af96b3fd-5ce5-40ba-b879-e4ad0407f387.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__86b1817f_8401_42b9_a803_48a576a855ad
ELOP-655967-2016 | EL-002474-2013 | 5/10/2017 5:39:16 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Deteriorated_wood_enclosure_and_electrical_equipment1.png,Deteriorated_wood_enclosure_and_electrical_equipment2.png,Deteriorated_wood_enclosure_and_electrical_equipment3.png,Deteriorated_wood_enclosure_and_electrical_equipment4.png,Deteriorated_wood_enclosure_and_electrical_equipment5.png,Deteriorated_wood_enclosure_and_electrical_equipment6.png Electrical equipment installed outdoors in a location where it is subject to the weather is required to be adequately protected from the weather either by being installed in an approved weather proof cabinet or being approved for installation in an outdoor location. This is required to protect the equipment from getting wet which can damage and deteriorate the equipment. This installation at a mobile home park has 60A 120/240V sub-service equipment, a light, switch, and receptacle installed inside of a wooden enclosure. The enclosure is rotten, the door has fallen off, and the roof no longer prevents water from entering the wooden enclosure. This has caused the equip | 3 | General Equipment is not approved for the specific use | Deteriorated_wood_enclosure_and_electrical_equipment6.png | file://x:/photopub/docs/0000000599/bfd0557d-c2df-4442-8fcb-21f28868498b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2029AE99_6602_4BD9_B4E2_220443DC5F82
GAUP-799989-2017 | UW-525087-2017 | 4/24/2017 12:49:40 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 5 | #Venting.png Plastic venting and cement unapproved for use with gas appliances. All venting must be approved to S636 standards to withstand designed temperatures and flue gas condensate. Potential for failure of the venting system which could create the possibility of CO to enter the living space. | 5 | Special venting system not glued or connected as per certified instructions | Venting.png | file://x:/photopub/docs/0000000590/0e503a77-0b57-47a7-888b-be6a29b6741d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f48e3d70_9bf6_4add_9dbf_55ba843c057c
GAIN-797665-2017 | GA-519228-2017 | 4/24/2017 1:35:55 PM | ASSESS: GA: Final | png | #asFound Blocked ventilation air opening | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Ventilation_opening.png Combustion air and ventilation air openings were blocked, this could cause improper appliance venting | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Ventilation_opening.png | file://x:/photopub/docs/0000000590/070daf6d-5d06-4629-aa31-e069c716de9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d838de2b_cc3f_46dc_9dc9_7b804a9abefc
GAIN-799392-2017 | GA-524736-2017 | 4/21/2017 1:31:02 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Vent.png The as-found-condition is that a vent serving a water heater terminates too close to a building opening. The potential hazard is that the exhaust from the water heater will enter the building, resulting in harmful products of combustion, such as Carbon Monoxide entering an occupied space. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent.png | file://x:/photopub/docs/0000000589/f8c15491-6c3e-4596-8a59-7aeb6d8627a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac5fca0d_fc9c_4cf9_bc06_bd019dac8ef3
GAUP-790393-2017 | UW-519855-2017 | 4/19/2017 12:18:19 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Close_nipple.png Observed use of an unapproved section of piping which is completely threaded in a gas piping system. Using this pipe can become hazardous as there is no safe place to place a pipe wrench on it without compromising the sealing threads of pipe creating a potential for a gas leak within the mechanical room. | 3 | Non-compliant material/fittings installed | Close_nipple.png | file://x:/photopub/docs/0000000588/552478b6-9408-4078-886b-4f049dbf4d60.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ccb1a1c8_6064_4d06_9709_50370e67e980
GAIN-792565-2017 | GA-514562-2017 | 4/19/2017 3:22:18 PM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Close_nipple1.png Observed use of an unapproved section of piping, which is completely threaded, in a gas piping system. Using this pipe can become hazardous as there is no safe place to place a pipe wrench on it without compromising the sealing threads of the pipe creating a potential for a gas leak within the mechanical room. | 3 | Non-compliant material/fittings installed | Close_nipple1.png | file://x:/photopub/docs/0000000588/1c0f7a2c-c304-4902-832f-290e23386659.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d28265b9_b90a_4437_8e91_3328c1e013fc
ELOP-655967-2016 | EL-002474-2013 | 5/10/2017 5:39:16 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Deteriorated_wood_enclosure_and_electrical_equipment1.png,Deteriorated_wood_enclosure_and_electrical_equipment2.png,Deteriorated_wood_enclosure_and_electrical_equipment3.png,Deteriorated_wood_enclosure_and_electrical_equipment4.png,Deteriorated_wood_enclosure_and_electrical_equipment5.png,Deteriorated_wood_enclosure_and_electrical_equipment6.png Electrical equipment installed outdoors in a location where it is subject to the weather is required to be adequately protected from the weather either by being installed in an approved weather proof cabinet or being approved for installation in an outdoor location. This is required to protect the equipment from getting wet which can damage and deteriorate the equipment. This installation at a mobile home park has 60A 120/240V sub-service equipment, a light, switch, and receptacle installed inside of a wooden enclosure. The enclosure is rotten, the door has fallen off, and the roof no longer prevents water from entering the wooden enclosure. This has caused the equip | 3 | General Equipment is not approved for the specific use | Deteriorated_wood_enclosure_and_electrical_equipment5.png | file://x:/photopub/docs/0000000599/ec98d6a2-61ca-4ca8-baaf-b6200bd6a0e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2029AE99_6602_4BD9_B4E2_220443DC5F82
ELOP-655967-2016 | EL-002474-2013 | 5/10/2017 5:39:16 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Deteriorated_wood_enclosure_and_electrical_equipment1.png,Deteriorated_wood_enclosure_and_electrical_equipment2.png,Deteriorated_wood_enclosure_and_electrical_equipment3.png,Deteriorated_wood_enclosure_and_electrical_equipment4.png,Deteriorated_wood_enclosure_and_electrical_equipment5.png,Deteriorated_wood_enclosure_and_electrical_equipment6.png Electrical equipment installed outdoors in a location where it is subject to the weather is required to be adequately protected from the weather either by being installed in an approved weather proof cabinet or being approved for installation in an outdoor location. This is required to protect the equipment from getting wet which can damage and deteriorate the equipment. This installation at a mobile home park has 60A 120/240V sub-service equipment, a light, switch, and receptacle installed inside of a wooden enclosure. The enclosure is rotten, the door has fallen off, and the roof no longer prevents water from entering the wooden enclosure. This has caused the equip | 3 | General Equipment is not approved for the specific use | Deteriorated_wood_enclosure_and_electrical_equipment4.png | file://x:/photopub/docs/0000000599/d64460ee-2c80-4815-812c-3cfeec38ed96.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2029AE99_6602_4BD9_B4E2_220443DC5F82
ELIN-808327-2017 | EL-351160-2016 | 5/9/2017 | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Bare_lamp_fixtures_installed_in_clothes_closets1.png,Bare_lamp_fixtures_installed_in_clothes_closets2.png,Bare_lamp_fixtures_installed_in_clothes_closets3.png,Bare_lamp_fixtures_installed_in_clothes_closets4.png,Bare_lamp_fixtures_installed_in_clothes_closets5.png Light fixtures installed in clothes closets are not permitted to be bare lamp type fixtures. This is to prevent combustible materials from coming into contact with light bulbs. This installation for a new house has light fixtures installed in the clothes closets that are bare bulb type fixtures. Left uncorrected this is a fire hazard if combustible materials contact hot light bulbs inside of clothes closets. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Bare_lamp_fixtures_installed_in_clothes_closets4.png | file://x:/photopub/docs/0000000599/937abcd6-45aa-4e7b-a602-e837f8994f12.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__86b1817f_8401_42b9_a803_48a576a855ad
ELIN-776932-2017 | UW-512719-2017 | 3/17/2017 8:09:37 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | #40_amp_BKR.png The breaker size is too large to protect the conductor terminated on the breaker. This could cause over heating and create a fire hazard. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 40_amp_BKR.png | file://x:/photopub/docs/0000000572/600ae6b8-9d64-42dc-a187-f5ffcb2e852b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__149ffe5f_facf_46dc_957d_4f90b2d4d0de
BPVOP-776310-2017 | 2293646 | 3/16/2017 11:09:01 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | #Safety_Relief_Valve_21.png,Safety_Relief_Valve_22.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 2005 and it was below the capacity required by the boiler manufacturer. This can contribute to the failure of the boiler safeties. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_Relief_Valve_21.png | file://x:/photopub/docs/0000000573/c837bf4b-de52-4f85-9f94-e9e3869f436d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab418b05_9e83_40e9_86e4_872da0ea9598
BPVOP-776312-2017 | 2251149 | 3/16/2017 11:23:20 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #SRV_D2.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 1996 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SRV_D2.png | file://x:/photopub/docs/0000000573/642b04c0-42d0-4f8c-8b63-15699ecfc014.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__701bcf9a_0f7a_49af_81e2_5cb2fd3c56af
BPVOP-776303-2017 | 2255017 | 3/16/2017 4:47:06 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #T_and_P_D_3.png Upon the assessment of a DHW Storage Tank with MAWP of 125 psig, was found that the Safety Relief Valve was installed in 2004 and was overdue as per CSA B51. This can contribute to the failure of the pressure vessel safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | T_and_P_D_3.png | file://x:/photopub/docs/0000000573/9f714f95-6a1b-4101-a87d-2ad701e279b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e4db6ec_2adc_45dd_9de2_573cbfb7cab4
BPVOP-776315-2017 | 2250880 | 3/16/2017 11:19:04 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #SRV_1.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 1996 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SRV_1.png | file://x:/photopub/docs/0000000573/62a03939-4c10-4a4e-b09f-18dd7ae56846.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46d2ebf9_9d01_4161_8be9_81fff1b884af
BPVOP-776310-2017 | 2293646 | 3/16/2017 11:09:01 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | #Safety_Relief_Valve_21.png,Safety_Relief_Valve_22.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 2005 and it was below the capacity required by the boiler manufacturer. This can contribute to the failure of the boiler safeties. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_Relief_Valve_22.png | file://x:/photopub/docs/0000000573/784e1baf-6eda-4160-8e5f-eed235cdc96a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab418b05_9e83_40e9_86e4_872da0ea9598
BPVOP-776326-2017 | 2254111 | 3/16/2017 4:14:19 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Tand_P_D_1.png Upon the assessment of a DHW Storage Tank with MAWP of 125 psig, was found that the Safety Relief Valve was installed in 2004 and was overdue as per CSA B51. This can contribute to the failure of the pressure vessel safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Tand_P_D_1.png | file://x:/photopub/docs/0000000573/efbd2154-9ce9-496a-bbbd-5c3e61906b5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74db109b_f704_446e_9937_00432b49e385
BPVOP-776301-2017 | 2252533 | 3/16/2017 11:44:28 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #SRV_D_2.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 1996 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SRV_D_2.png | file://x:/photopub/docs/0000000573/5e89d4d8-bfca-4df1-85b2-e1c924c0488b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2706db8_c3c4_4166_9749_0c57e1ab3919
BPVOP-776306-2017 | 2250787 | 3/16/2017 11:01:54 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | #Safety_Relief_Valve_1.png,Data_plate.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 2005 and it was below the capacity required by the boiler manufacturer. This can contribute to the failure of the boiler safeties. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Data_plate.png | file://x:/photopub/docs/0000000573/cf262135-92b4-4fe5-b6c5-64fae2b527c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc53b84d_63ad_4a5b_b94e_3c14f07a8a90
BPVOP-776306-2017 | 2250787 | 3/16/2017 11:01:54 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | #Safety_Relief_Valve_1.png,Data_plate.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 2005 and it was below the capacity required by the boiler manufacturer. This can contribute to the failure of the boiler safeties. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_Relief_Valve_1.png | file://x:/photopub/docs/0000000573/5909178a-5f02-4fdc-b499-33bbb2a22b92.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc53b84d_63ad_4a5b_b94e_3c14f07a8a90
BPVOP-776318-2017 | 2251990 | 3/16/2017 11:40:13 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #SRV_D1.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 1996 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SRV_D1.png | file://x:/photopub/docs/0000000573/2bc51586-f1f0-4f60-9094-6b80089b5750.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc8b8353_18d0_4720_8dbf_88b6bd7b4f03
BPVOP-776307-2017 | 2254415 | 3/16/2017 4:41:28 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #T_and_P_D_2.png Upon the assessment of a DHW Storage Tank with MAWP of 125 psig, was found that the Safety Relief Valve was installed in 2004 and was overdue as per CSA B51. This can contribute to the failure of the pressure vessel safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | T_and_P_D_2.png | file://x:/photopub/docs/0000000573/bb9adfe6-edab-4ff8-bca0-9659874ae6f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85f51511_0b81_42ae_9dfa_1cdf0acdaada
BPVOP-776319-2017 | 2250828 | 3/16/2017 3:57:34 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #SRV_D3.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 1996 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SRV_D3.png | file://x:/photopub/docs/0000000573/5f4f1e3f-647b-4694-b34a-3181273bb58e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__493fa1bc_a9d5_40e7_95ff_d083de650317
BPVOP-776299-2017 | 4089349 | 3/16/2017 12:26:03 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #SRV_Electric.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SRV_Electric.png | file://x:/photopub/docs/0000000573/2a81d91b-3dba-49f8-acf5-5c54aaa082b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e70c212_ea55_4603_a949_5c5a12452f53
BPVOP-776313-2017 | 2255828 | 3/16/2017 4:52:40 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #T_and_P_T_1.png Upon the assessment of a DHW Storage Tank with MAWP of 125 psig, was found that the Safety Relief Valve was installed in 2004 and was overdue as per CSA B51. This can contribute to the failure of the pressure vessel safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | T_and_P_T_1.png | file://x:/photopub/docs/0000000573/2a06a746-ad45-469d-a1d1-092d9c9a133b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f129f44_5426_4294_98cf_18c2e0d2e61a
BPVOP-776316-2017 | 4089340 | 3/16/2017 12:20:47 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Relief_Valve_.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_.png | file://x:/photopub/docs/0000000573/347be837-cb21-49ba-9cd0-cdf0cb5bfc14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f60d8c2b_5255_4768_a982_19783918de0c
ELIN-766532-2017 | EL-441031-2016 | 3/3/2017 5:32:13 PM | ASSESS: EL: Final | png | #asFound | EL282 | Class II, all locations Equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated | 4 | 4 | #Dust_collector_wiring1.png,Dust_collector_wiring2.png,Dust_collector_wiring3.png,Dust_collector_wiring4.png,Dust_collector_wiring5.png,Dust_collector_wiring6.png,Dust_collector_wiring7.png Woodworking shops are classified as hazardous electrical locations when the shops do not have an adequate dust collection system and good house keeping of combustible dust. This is because the accumulation of combustible dust acts as an insulator and can cause overheating of electrical equipment. Electrical equipment must be rated for these conditions when installed in a hazardous environment. This overheating of electrical equipment can cause fires within the equipment. In addition, fire or sparks from the electrical equipment can ignite the combustible dust layer on the equipment or explosive dust that is suspended in the air. The ignition of the combustible dust can produce a fire ball that will expand and create a larger fire or an explosion within the building. In this installation at a furniture manufacturing shop, | 4 | Class II, all locations Equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated | Dust_collector_wiring4.png | file://x:/photopub/docs/0000000567/580f4a39-fc73-4b16-92c1-8d4bf1eb272f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03c5905d_e0d0_4d53_ab92_c2c1a0a9333c
ELIN-766532-2017 | EL-441031-2016 | 3/3/2017 5:32:13 PM | ASSESS: EL: Final | png | #asFound | EL282 | Class II, all locations Equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated | 4 | 4 | #Dust_collector_wiring1.png,Dust_collector_wiring2.png,Dust_collector_wiring3.png,Dust_collector_wiring4.png,Dust_collector_wiring5.png,Dust_collector_wiring6.png,Dust_collector_wiring7.png Woodworking shops are classified as hazardous electrical locations when the shops do not have an adequate dust collection system and good house keeping of combustible dust. This is because the accumulation of combustible dust acts as an insulator and can cause overheating of electrical equipment. Electrical equipment must be rated for these conditions when installed in a hazardous environment. This overheating of electrical equipment can cause fires within the equipment. In addition, fire or sparks from the electrical equipment can ignite the combustible dust layer on the equipment or explosive dust that is suspended in the air. The ignition of the combustible dust can produce a fire ball that will expand and create a larger fire or an explosion within the building. In this installation at a furniture manufacturing shop, | 4 | Class II, all locations Equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated | Dust_collector_wiring6.png | file://x:/photopub/docs/0000000567/57c44377-1660-4172-b054-350dc70fee54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03c5905d_e0d0_4d53_ab92_c2c1a0a9333c
ELIN-766532-2017 | EL-441031-2016 | 3/3/2017 5:32:13 PM | ASSESS: EL: Final | png | #asFound | EL282 | Class II, all locations Equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated | 4 | 4 | #Dust_collector_wiring1.png,Dust_collector_wiring2.png,Dust_collector_wiring3.png,Dust_collector_wiring4.png,Dust_collector_wiring5.png,Dust_collector_wiring6.png,Dust_collector_wiring7.png Woodworking shops are classified as hazardous electrical locations when the shops do not have an adequate dust collection system and good house keeping of combustible dust. This is because the accumulation of combustible dust acts as an insulator and can cause overheating of electrical equipment. Electrical equipment must be rated for these conditions when installed in a hazardous environment. This overheating of electrical equipment can cause fires within the equipment. In addition, fire or sparks from the electrical equipment can ignite the combustible dust layer on the equipment or explosive dust that is suspended in the air. The ignition of the combustible dust can produce a fire ball that will expand and create a larger fire or an explosion within the building. In this installation at a furniture manufacturing shop, | 4 | Class II, all locations Equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated | Dust_collector_wiring7.png | file://x:/photopub/docs/0000000567/deec64a2-7722-484a-9612-6d1ecb10aa02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03c5905d_e0d0_4d53_ab92_c2c1a0a9333c
ELIN-766532-2017 | EL-441031-2016 | 3/3/2017 5:32:13 PM | ASSESS: EL: Final | png | #asFound | EL282 | Class II, all locations Equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated | 4 | 4 | #Dust_collector_wiring1.png,Dust_collector_wiring2.png,Dust_collector_wiring3.png,Dust_collector_wiring4.png,Dust_collector_wiring5.png,Dust_collector_wiring6.png,Dust_collector_wiring7.png Woodworking shops are classified as hazardous electrical locations when the shops do not have an adequate dust collection system and good house keeping of combustible dust. This is because the accumulation of combustible dust acts as an insulator and can cause overheating of electrical equipment. Electrical equipment must be rated for these conditions when installed in a hazardous environment. This overheating of electrical equipment can cause fires within the equipment. In addition, fire or sparks from the electrical equipment can ignite the combustible dust layer on the equipment or explosive dust that is suspended in the air. The ignition of the combustible dust can produce a fire ball that will expand and create a larger fire or an explosion within the building. In this installation at a furniture manufacturing shop, | 4 | Class II, all locations Equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated | Dust_collector_wiring3.png | file://x:/photopub/docs/0000000567/64a86fb8-fad4-4e09-99ac-71f86bb2ec2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03c5905d_e0d0_4d53_ab92_c2c1a0a9333c
ELIN-766532-2017 | EL-441031-2016 | 3/3/2017 5:32:13 PM | ASSESS: EL: Final | png | #asFound | EL282 | Class II, all locations Equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated | 4 | 4 | #Dust_collector_wiring1.png,Dust_collector_wiring2.png,Dust_collector_wiring3.png,Dust_collector_wiring4.png,Dust_collector_wiring5.png,Dust_collector_wiring6.png,Dust_collector_wiring7.png Woodworking shops are classified as hazardous electrical locations when the shops do not have an adequate dust collection system and good house keeping of combustible dust. This is because the accumulation of combustible dust acts as an insulator and can cause overheating of electrical equipment. Electrical equipment must be rated for these conditions when installed in a hazardous environment. This overheating of electrical equipment can cause fires within the equipment. In addition, fire or sparks from the electrical equipment can ignite the combustible dust layer on the equipment or explosive dust that is suspended in the air. The ignition of the combustible dust can produce a fire ball that will expand and create a larger fire or an explosion within the building. In this installation at a furniture manufacturing shop, | 4 | Class II, all locations Equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated | Dust_collector_wiring5.png | file://x:/photopub/docs/0000000567/e9ec9b23-b0fd-4d41-9b9d-5a328bd7dadc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03c5905d_e0d0_4d53_ab92_c2c1a0a9333c
ELIN-766532-2017 | EL-441031-2016 | 3/3/2017 5:32:13 PM | ASSESS: EL: Final | png | #asFound | EL282 | Class II, all locations Equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated | 4 | 4 | #Dust_collector_wiring1.png,Dust_collector_wiring2.png,Dust_collector_wiring3.png,Dust_collector_wiring4.png,Dust_collector_wiring5.png,Dust_collector_wiring6.png,Dust_collector_wiring7.png Woodworking shops are classified as hazardous electrical locations when the shops do not have an adequate dust collection system and good house keeping of combustible dust. This is because the accumulation of combustible dust acts as an insulator and can cause overheating of electrical equipment. Electrical equipment must be rated for these conditions when installed in a hazardous environment. This overheating of electrical equipment can cause fires within the equipment. In addition, fire or sparks from the electrical equipment can ignite the combustible dust layer on the equipment or explosive dust that is suspended in the air. The ignition of the combustible dust can produce a fire ball that will expand and create a larger fire or an explosion within the building. In this installation at a furniture manufacturing shop, | 4 | Class II, all locations Equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated | Dust_collector_wiring1.png | file://x:/photopub/docs/0000000567/4a2dc729-6c91-4bba-85dc-e66a11d20851.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03c5905d_e0d0_4d53_ab92_c2c1a0a9333c
ELIN-766532-2017 | EL-441031-2016 | 3/3/2017 5:32:13 PM | ASSESS: EL: Final | png | #asFound | EL282 | Class II, all locations Equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated | 4 | 4 | #Dust_collector_wiring1.png,Dust_collector_wiring2.png,Dust_collector_wiring3.png,Dust_collector_wiring4.png,Dust_collector_wiring5.png,Dust_collector_wiring6.png,Dust_collector_wiring7.png Woodworking shops are classified as hazardous electrical locations when the shops do not have an adequate dust collection system and good house keeping of combustible dust. This is because the accumulation of combustible dust acts as an insulator and can cause overheating of electrical equipment. Electrical equipment must be rated for these conditions when installed in a hazardous environment. This overheating of electrical equipment can cause fires within the equipment. In addition, fire or sparks from the electrical equipment can ignite the combustible dust layer on the equipment or explosive dust that is suspended in the air. The ignition of the combustible dust can produce a fire ball that will expand and create a larger fire or an explosion within the building. In this installation at a furniture manufacturing shop, | 4 | Class II, all locations Equipment such as motors, transformers, overcurrent devices, switches and controllers, luminaires, heaters, and appliances are not properly rated | Dust_collector_wiring2.png | file://x:/photopub/docs/0000000567/b32b65cc-9d9b-4a30-87d5-b68fa568261f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03c5905d_e0d0_4d53_ab92_c2c1a0a9333c
EDMA-774996-2017 | ED-510889-2017 | 3/15/2017 8:30:33 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED013 | Oil/Water/Other Debris found that: Is not affecting components or operation and not likely to progress | 2 | 2 | #Data_sheet1.png,Data_sheet2.png | 2 | Oil/Water/Other Debris found that: Is not affecting components or operation and not likely to progress | Data_sheet2.png | file://x:/photopub/docs/0000000572/484212bd-4709-4bb3-b20f-06b9c4a02d44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1414cc0_bd3b_4daf_a3f1_1d590106f456
EDMA-774996-2017 | ED-510889-2017 | 3/15/2017 8:30:33 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED013 | Oil/Water/Other Debris found that: Is not affecting components or operation and not likely to progress | 2 | 2 | #Data_sheet1.png,Data_sheet2.png | 2 | Oil/Water/Other Debris found that: Is not affecting components or operation and not likely to progress | Data_sheet1.png | file://x:/photopub/docs/0000000572/d5c44e39-9b54-4007-8ce4-ed0055cd2c5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1414cc0_bd3b_4daf_a3f1_1d590106f456
ELIN-787141-2017 | EL-518214-2017 | 4/3/2017 12:31:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 3 | #Service_meter1.png,Service_meter2.png The 100 amp 120/240 volt overhead (temporary) service uses knock out fillers installed incorrectly from the interior of the meterbase which both can inadvertently have the fillers fall INTO the meter enclosure exposing it to a short circuit fault with unfused Utility connections AND allow moisture to penetrate enclosure due to no weather-proofing protection. The issue is both a Shock and Thermal Hazard | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Service_meter2.png | file://x:/photopub/docs/0000000581/79b0ec3e-3b66-4d60-bd47-adb5e1f2688d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97b7b913_d036_4920_aaea_8ad58005a9fb
ELIN-787141-2017 | EL-518214-2017 | 4/3/2017 12:31:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 3 | #Service_meter1.png,Service_meter2.png The 100 amp 120/240 volt overhead (temporary) service uses knock out fillers installed incorrectly from the interior of the meterbase which both can inadvertently have the fillers fall INTO the meter enclosure exposing it to a short circuit fault with unfused Utility connections AND allow moisture to penetrate enclosure due to no weather-proofing protection. The issue is both a Shock and Thermal Hazard | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Service_meter1.png | file://x:/photopub/docs/0000000581/3a5eaf91-9fa1-4662-af75-b5cfa4d8d83c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97b7b913_d036_4920_aaea_8ad58005a9fb
EDMA-813519-2017 | ED-201132-2015 | 5/10/2017 9:11:45 PM | ASSESS: ED MA: Partial Acceptance | png | #asFound | ED052 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 2 | 2 | #Pit_ladder.png Ladder rungs does not comply with the code | 2 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | Pit_ladder.png | file://x:/photopub/docs/0000000599/7e61dc28-5966-4f5e-9cec-cbc609334107.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c49bc6d0_c5fb_479b_ad64_2c1d4a593f45
GAIN-778308-2017 | GA-502075-2017 | 3/21/2017 12:03:16 PM | ASSESS: GA: Final | png | #asFound | GA125 | Damper or louver not interlocked | 4 | 4 | #Damper.png The as found hazard was a damper responsible for providing replacement air to a repair garage when the exhaust fan are energized which was not interlocked with the appliance it was providing air for. This is a hazard because if the damper motor were to fail it would create a risk of a negative pressure in the building drawing flue products back into the building. Risk of carbon monoxide poisoning and or appliance damage. | 4 | Damper or louver not interlocked | Damper.png | file://x:/photopub/docs/0000000574/96691b9f-73dd-4ba4-ae23-4e69f86e686c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a117511_ea1d_4109_a31c_0638fed37912
GAUP-770883-2017 | UW-509050-2017 | 3/8/2017 3:00:17 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Joint.png The as found hazard was a tubing system which had been joined by soldering which has a melting point below 1000 degrees Fahrenheit. This is a hazard because in the event of a fire it creates a risk of premature failure of the joints. Additionally solder does not provide as strong a joint as brazing. | 3 | Non-compliant material/fittings installed | Joint.png | file://x:/photopub/docs/0000000568/bd1567db-8b70-4dfc-a7f6-2612c2e1d505.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa23ad5d_df10_4415_8e8f_f5ae7d166425
ELIN-770639-2017 | UW-508969-2017 | 3/7/2017 8:51:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Annunciator1.png,Annunciator2.png,Annunciator3.png,Annunciator4.png,Annunciator5.png,Annunciator6.png,Annunciator7.png,Annunciator8.png,Annunciator9.png,Annunciator10.png,Annunciator11.png,Annunciator12.png Fire alarm annunciator panel emergency life safety system equipment without evidence of approval. Unapproved annunciator may not provide accurate information to fire fighters during a fire condition. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Annunciator1.png | file://x:/photopub/docs/0000000569/46a744ab-4465-4a2c-8d40-f36590536dde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae30fbd2_6163_4abf_a935_38bd82fb1e89
ELIN-770639-2017 | UW-508969-2017 | 3/7/2017 8:51:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Annunciator1.png,Annunciator2.png,Annunciator3.png,Annunciator4.png,Annunciator5.png,Annunciator6.png,Annunciator7.png,Annunciator8.png,Annunciator9.png,Annunciator10.png,Annunciator11.png,Annunciator12.png Fire alarm annunciator panel emergency life safety system equipment without evidence of approval. Unapproved annunciator may not provide accurate information to fire fighters during a fire condition. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Annunciator12.png | file://x:/photopub/docs/0000000569/c6977834-4b79-4e5e-826d-9e3fb3638afd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae30fbd2_6163_4abf_a935_38bd82fb1e89
ELIN-770639-2017 | UW-508969-2017 | 3/7/2017 8:51:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Annunciator1.png,Annunciator2.png,Annunciator3.png,Annunciator4.png,Annunciator5.png,Annunciator6.png,Annunciator7.png,Annunciator8.png,Annunciator9.png,Annunciator10.png,Annunciator11.png,Annunciator12.png Fire alarm annunciator panel emergency life safety system equipment without evidence of approval. Unapproved annunciator may not provide accurate information to fire fighters during a fire condition. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Annunciator9.png | file://x:/photopub/docs/0000000569/0161c51b-7d94-44f0-95b5-80eabbc311dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae30fbd2_6163_4abf_a935_38bd82fb1e89
ELIN-770639-2017 | UW-508969-2017 | 3/7/2017 8:51:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Annunciator1.png,Annunciator2.png,Annunciator3.png,Annunciator4.png,Annunciator5.png,Annunciator6.png,Annunciator7.png,Annunciator8.png,Annunciator9.png,Annunciator10.png,Annunciator11.png,Annunciator12.png Fire alarm annunciator panel emergency life safety system equipment without evidence of approval. Unapproved annunciator may not provide accurate information to fire fighters during a fire condition. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Annunciator11.png | file://x:/photopub/docs/0000000569/2a953dd4-b4f7-4899-8613-240b9fa2185f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae30fbd2_6163_4abf_a935_38bd82fb1e89
ELIN-770639-2017 | UW-508969-2017 | 3/7/2017 8:51:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Annunciator1.png,Annunciator2.png,Annunciator3.png,Annunciator4.png,Annunciator5.png,Annunciator6.png,Annunciator7.png,Annunciator8.png,Annunciator9.png,Annunciator10.png,Annunciator11.png,Annunciator12.png Fire alarm annunciator panel emergency life safety system equipment without evidence of approval. Unapproved annunciator may not provide accurate information to fire fighters during a fire condition. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Annunciator5.png | file://x:/photopub/docs/0000000569/5c230afc-b170-4dda-87cc-29bf8ee5d9b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae30fbd2_6163_4abf_a935_38bd82fb1e89
ELIN-770639-2017 | UW-508969-2017 | 3/7/2017 8:51:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Annunciator1.png,Annunciator2.png,Annunciator3.png,Annunciator4.png,Annunciator5.png,Annunciator6.png,Annunciator7.png,Annunciator8.png,Annunciator9.png,Annunciator10.png,Annunciator11.png,Annunciator12.png Fire alarm annunciator panel emergency life safety system equipment without evidence of approval. Unapproved annunciator may not provide accurate information to fire fighters during a fire condition. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Annunciator7.png | file://x:/photopub/docs/0000000569/2b097300-02bb-4d7e-9d19-ae547c71c926.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae30fbd2_6163_4abf_a935_38bd82fb1e89
ELIN-770639-2017 | UW-508969-2017 | 3/7/2017 8:51:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Annunciator1.png,Annunciator2.png,Annunciator3.png,Annunciator4.png,Annunciator5.png,Annunciator6.png,Annunciator7.png,Annunciator8.png,Annunciator9.png,Annunciator10.png,Annunciator11.png,Annunciator12.png Fire alarm annunciator panel emergency life safety system equipment without evidence of approval. Unapproved annunciator may not provide accurate information to fire fighters during a fire condition. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Annunciator3.png | file://x:/photopub/docs/0000000569/ea3409ed-d68c-44d7-a869-1c8ffe69f82e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae30fbd2_6163_4abf_a935_38bd82fb1e89
BPVIN-798544-2017 | BPV-419083-2016 | 4/19/2017 | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #10.png A disconnecting means capable of being locked in the open position shall be installed in an accessible location so the heater can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided for this glycol heater, potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 10.png | file://x:/photopub/docs/0000000589/3736efde-da71-43f5-bd6a-c896065877be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d636ce6b_fa58_437f_b7fd_e1390f7a4322
ELOP-751166-2017 | EL-491055-2017 | 3/10/2017 4:30:51 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL158 | Installation of electrical equipment Inadequate ventilation is provided for equipment. | 3 | 3 | #Electrical_room.png what the code is. why the code is.what you saw. what the hazards are. The code requires access to electrical equipment . Equipment that relies on air flow for ventilation and cooling needs to be clutter free. Transformer was not accesable at time of assessment and covered. Transformer could overheat and damage could take place as well as possible fire hazard. | 3 | Installation of electrical equipment Inadequate ventilation is provided for equipment. | Electrical_room.png | file://x:/photopub/docs/0000000569/352985a3-2f23-4cd5-bf14-c14409d6e660.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55F71DA2_080B_4276_861F_2293CB78446D
GAIN-789270-2017 | GA-493327-2017 | 4/21/2017 8:05:04 AM | ASSESS: GA: Final | png | #asFound | GA100 | Hazards created by exhaust fans | 3 | 3 | #HWT.png Exhaust fans in Wash House create a hazard when door to mechanical room is not shut. The Hot water tank will not vent properly causing exhaust to be released into air possibly causing injury to person(s) using the facility. | 3 | Hazards created by exhaust fans | HWT.png | file://x:/photopub/docs/0000000598/4330b458-f308-4fce-b297-4c4c69af8836.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed6c2e50_dae5_47e4_9234_305738ec3d0b
GAHE-813223-2017 | HE-532368-2017 | 5/10/2017 10:08:28 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | #Gauge.png Minor leak detected at fill gauge. Raw gas released to atmosphere possible concentration in air could get worse if problem persists. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Gauge.png | file://x:/photopub/docs/0000000598/a97a4d84-1afe-4d6f-ad78-d84d5e8749b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__280e30ef_5da4_4249_8d19_41c37e493c88
ELIN-778120-2017 | EL-511712-2017 | 3/21/2017 12:54:31 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | #A1.png,A2.png Non heating lead not installed in a raceway. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A2.png | file://x:/photopub/docs/0000000574/ae8a25c0-a797-4071-9218-366ad1d18798.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7145286_0479_4835_991c_2fa46cafb75c
ELIN-778120-2017 | EL-511712-2017 | 3/21/2017 12:54:31 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | #A1.png,A2.png Non heating lead not installed in a raceway. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A1.png | file://x:/photopub/docs/0000000574/11aef856-8b8a-4fc2-a8e5-4ea7478942cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7145286_0479_4835_991c_2fa46cafb75c
GAIN-766900-2017 | GA-442324-2016 | 4/5/2017 2:24:46 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Wiring.png The as-found-condition is that the electrical connections to a boiler are not installed according to the manufacturer's instructions or the Canadian Electrical Code. The potential hazard is that the incorrect wiring will increase the likelihood of an electrical fire. | 3 | Appliance not installed according to installation instructions | Wiring.png | file://x:/photopub/docs/0000000584/bcfc30ad-60f4-40c9-b79a-d42a8ec6067a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b06fe673_228c_48ef_a0f4_2a1fc2870069
BPVIN-803281-2017 | BPV-035027-2013 | 4/24/2017 | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Selkirk_college.png Hot water heating plant maximum allowable working pressure 125 psi. The regulatory requirement for continuous supervision by certified operators was not being provided by the owner. Failure to provide adequate supervision increases risk and may result in circumstances that may harm personnel or damage equipment. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Selkirk_college.png | file://x:/photopub/docs/0000000591/1fc001aa-9130-4cbe-bacb-b1c2f7b2e9f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6679aaec_c3f0_420c_9eed_7704e933afcb
ELIN-770239-2017 | EL-508622-2017 | 3/10/2017 10:09:07 AM | ASSESS: EL: Final | png | #asFound | EL157 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 4 | 4 | #Pole_3.png Un approved pole is deteriorated and requires replacement or engineered support. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | Pole_3.png | file://x:/photopub/docs/0000000569/88496d1f-78de-469f-96b6-548c26e180e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39be58ed_19b3_4958_95e6_cce3131e7fee
ELIN-769714-2017 | EL-474150-2016 | 3/28/2017 8:00:00 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #Froese3.png Cables installed in wood construction should be protected with a minimum of 32 mm of wood or approved steel protection plates.This protects the cables from being damaged during the instalation of wall finishes.During the inspection it was observed that cables had not been installed with adequate protection.this presents a possible shock hazard to the installer of the wall finishes and or a short circuit that could cause a fire.12-616 | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Froese3.png | file://x:/photopub/docs/0000000577/d7c042e1-fde3-498e-8961-e6fe613f32f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67ce85e2_ffa3_4156_8bb6_437668f27022
ELIN-748759-2017 | EL-474226-2016 | 2/28/2017 10:59:12 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 2 | #AC90_into_box_approved_for_NMSC1.png,AC90_into_box_approved_for_NMSC2.png During a rough wire assessment, armoured cables were found entered into device boxes approved for non metallic sheathed cables only. These plastic boxes have no means to adequately secure the cable to prevent strain on the conductors, nor have they a means to provide bonding continuity of the metallic armour of these cables. Damage to splices within the device boxes could result leading to potential shock or fire hazards. | 3 | Conductors Equipment is not approved for the specific use. | AC90_into_box_approved_for_NMSC2.png | file://x:/photopub/docs/0000000564/b7da9fda-5093-4fcf-8138-8df3eea2544a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8c9d32f_acad_4328_852e_d274a9aa005a
ELIN-748759-2017 | EL-474226-2016 | 2/28/2017 10:59:12 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 2 | #AC90_into_box_approved_for_NMSC1.png,AC90_into_box_approved_for_NMSC2.png During a rough wire assessment, armoured cables were found entered into device boxes approved for non metallic sheathed cables only. These plastic boxes have no means to adequately secure the cable to prevent strain on the conductors, nor have they a means to provide bonding continuity of the metallic armour of these cables. Damage to splices within the device boxes could result leading to potential shock or fire hazards. | 3 | Conductors Equipment is not approved for the specific use. | AC90_into_box_approved_for_NMSC1.png | file://x:/photopub/docs/0000000564/0770b857-0b01-4960-bbdf-b0181832ca02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8c9d32f_acad_4328_852e_d274a9aa005a
ELHE-792989-2017 | HE-521290-2017 | 6/19/2017 10:40:31 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 5 | #Damage1.png,Damage2.png,Damage3.png,Damage4.png The existing 200 amp 120/240 volt service equipment has been damaged and is hanging loose on the pole, this equipment is exposed to all personnel in the area and not protected from vehicle damage. The weight of the energized service is reliant on the physical connections of the service conductors at both the upper weather-head and the meter-base connection terminals. This is an equipment damage issue that can lead to additional shock and thermal hazards | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Damage3.png | file://x:/photopub/docs/0000000585/ecfa2508-f490-426d-8ca5-c9f08c7b026d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13e4d579_8aa0_44d2_a246_bfe58664babd
ELHE-792989-2017 | HE-521290-2017 | 6/19/2017 10:40:31 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 5 | #Damage1.png,Damage2.png,Damage3.png,Damage4.png The existing 200 amp 120/240 volt service equipment has been damaged and is hanging loose on the pole, this equipment is exposed to all personnel in the area and not protected from vehicle damage. The weight of the energized service is reliant on the physical connections of the service conductors at both the upper weather-head and the meter-base connection terminals. This is an equipment damage issue that can lead to additional shock and thermal hazards | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Damage4.png | file://x:/photopub/docs/0000000585/b52beb64-4168-4ee1-bbcb-c73c07a36e37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13e4d579_8aa0_44d2_a246_bfe58664babd
ELHE-792989-2017 | HE-521290-2017 | 6/19/2017 10:40:31 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 5 | #Damage1.png,Damage2.png,Damage3.png,Damage4.png The existing 200 amp 120/240 volt service equipment has been damaged and is hanging loose on the pole, this equipment is exposed to all personnel in the area and not protected from vehicle damage. The weight of the energized service is reliant on the physical connections of the service conductors at both the upper weather-head and the meter-base connection terminals. This is an equipment damage issue that can lead to additional shock and thermal hazards | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Damage1.png | file://x:/photopub/docs/0000000585/9d53a8a9-769a-4914-b8b6-3e4db300c625.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13e4d579_8aa0_44d2_a246_bfe58664babd
ELHE-792989-2017 | HE-521290-2017 | 6/19/2017 10:40:31 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 5 | #Damage1.png,Damage2.png,Damage3.png,Damage4.png The existing 200 amp 120/240 volt service equipment has been damaged and is hanging loose on the pole, this equipment is exposed to all personnel in the area and not protected from vehicle damage. The weight of the energized service is reliant on the physical connections of the service conductors at both the upper weather-head and the meter-base connection terminals. This is an equipment damage issue that can lead to additional shock and thermal hazards | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Damage2.png | file://x:/photopub/docs/0000000585/976c01ce-9060-4a69-a220-64f24ed3d841.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13e4d579_8aa0_44d2_a246_bfe58664babd
ELIN-766892-2017 | EL-438125-2016 | 3/7/2017 11:12:11 AM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | #No_AFCI_protection_for_receptacle_circuit_in_kitchen1.png,No_AFCI_protection_for_receptacle_circuit_in_kitchen2.png,No_AFCI_protection_for_receptacle_circuit_in_kitchen3.png The code requires most receptacle branch circuits to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable equipment plugged into receptacles. This installation of a receptacle circuit in a new house was not provided with AFCI protection. The branch circuit was for a 15A 120V receptacle in the kitchen. This is a potential fire hazard if an arcing fault occurs on this receptacle branch circuit from the branch circuit wiring or the equipment that is plugged into them. | 3 | Equipment Gas line, cast or water pipe has not been bonded | No_AFCI_protection_for_receptacle_circuit_in_kitchen3.png | file://x:/photopub/docs/0000000568/431d2997-32c5-455f-b497-503e8514ab49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d663bdb2_d283_44bc_a98f_ffd1e9700572
ELIN-766892-2017 | EL-438125-2016 | 3/7/2017 11:12:11 AM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | #No_AFCI_protection_for_receptacle_circuit_in_kitchen1.png,No_AFCI_protection_for_receptacle_circuit_in_kitchen2.png,No_AFCI_protection_for_receptacle_circuit_in_kitchen3.png The code requires most receptacle branch circuits to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable equipment plugged into receptacles. This installation of a receptacle circuit in a new house was not provided with AFCI protection. The branch circuit was for a 15A 120V receptacle in the kitchen. This is a potential fire hazard if an arcing fault occurs on this receptacle branch circuit from the branch circuit wiring or the equipment that is plugged into them. | 3 | Equipment Gas line, cast or water pipe has not been bonded | No_AFCI_protection_for_receptacle_circuit_in_kitchen2.png | file://x:/photopub/docs/0000000568/696aff6e-e117-4316-aff1-fbfbcae1516a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d663bdb2_d283_44bc_a98f_ffd1e9700572
ELIN-766892-2017 | EL-438125-2016 | 3/7/2017 11:12:11 AM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | #No_AFCI_protection_for_receptacle_circuit_in_kitchen1.png,No_AFCI_protection_for_receptacle_circuit_in_kitchen2.png,No_AFCI_protection_for_receptacle_circuit_in_kitchen3.png The code requires most receptacle branch circuits to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable equipment plugged into receptacles. This installation of a receptacle circuit in a new house was not provided with AFCI protection. The branch circuit was for a 15A 120V receptacle in the kitchen. This is a potential fire hazard if an arcing fault occurs on this receptacle branch circuit from the branch circuit wiring or the equipment that is plugged into them. | 3 | Equipment Gas line, cast or water pipe has not been bonded | No_AFCI_protection_for_receptacle_circuit_in_kitchen1.png | file://x:/photopub/docs/0000000568/24f586a8-59ef-492e-92e5-bf43c1c90ddd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d663bdb2_d283_44bc_a98f_ffd1e9700572
BPVOP-778349-2017 | BPV-0000504282-2017 | 3/21/2017 10:41:23 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Boiler.png A certified individual is required to be in attendance at all times when the boiler is in operation. I found that there is no Certified Boiler Operator present when High Pressure Steam Boiler (125 PSIG) is in operation. An incident may occur due to lack of timely corrective action. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Boiler.png | file://x:/photopub/docs/0000000574/7d1275b8-7ddb-4a54-8f91-a47faf38bd03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ff73342_9bbe_4077_a788_1ad91822f36d
GAIN-800269-2017 | GA-483389-2016 | 4/26/2017 4:03:37 PM | ASSESS: GA: Final | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | #Gas_meter_reg_and_exhaust.png Low Profile Sidewall Exhaust Vent Termination installed within minimum distances of gas meter regulator. The clearances are not met therefore there is a possibility of ice accumulation on relief of regulator causing issues with gas system or in the event of over pressure the gas from regulator relief could get brought in by combustion air outlet of furnace causing over firing of furnace or gas entering home through furnace | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Gas_meter_reg_and_exhaust.png | file://x:/photopub/docs/0000000591/8304faaa-ec92-41d7-9551-305597800aab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__769ce156_7b0e_4561_94e3_f2638db154f5
GAIN-765129-2017 | GA-503663-2017 | 3/1/2017 10:49:00 AM | ASSESS: GA: Final | png | #asFound | GA045 | Gas connector passes through wall, floor, ceiling, partition or into appliance | 2 | 2 | #Gas_connector_passing_through_the_wall_of_an_appliance.png A gas connector passing through a wall of an appliance. Damage may occur to the appliance connector at the point it passes through to partition wall. | 2 | Gas connector passes through wall, floor, ceiling, partition or into appliance | Gas_connector_passing_through_the_wall_of_an_appliance.png | file://x:/photopub/docs/0000000565/5a74d195-8416-42db-ba34-f7fba2709511.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb2e683b_57f2_4e0e_aceb_e85f37c3745b
BPVOP-735753-2017 | 2797669 | 3/7/2017 10:18:00 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | #SV_1.png,SV_2.png Upon the assessment of a HP Steam Boiler with MAWP of 150 psig, was found that the Safety Relief Valve was leaking. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | SV_2.png | file://x:/photopub/docs/0000000567/78593937-8715-49c2-b893-7d29e7b2c667.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f777bac_73ba_4070_8a63_42ed0a3dc869
BPVOP-735753-2017 | 2797669 | 3/7/2017 10:18:00 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | #SV_1.png,SV_2.png Upon the assessment of a HP Steam Boiler with MAWP of 150 psig, was found that the Safety Relief Valve was leaking. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | SV_1.png | file://x:/photopub/docs/0000000567/ec1f2339-63a3-4d22-b892-a63e1c39db43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f777bac_73ba_4070_8a63_42ed0a3dc869
GAIN-784011-2017 | GA-495852-2017 | 4/11/2017 4:05:06 PM | ASSESS: GA: Rough-In | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Open_line.png Open gas line with valve in closed position. Valve could be opened unintentionally resulting in the release of fuel. Possible fire risk if source of ignition were present. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Open_line.png | file://x:/photopub/docs/0000000585/d66f81bc-e4ae-4501-b92a-db9bd2640deb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81cff83f_01f1_49bc_a470_b6f36d50e9ad
ELOP-655967-2016 | EL-002474-2013 | 5/10/2017 5:39:16 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Deteriorated_wood_enclosure_and_electrical_equipment1.png,Deteriorated_wood_enclosure_and_electrical_equipment2.png,Deteriorated_wood_enclosure_and_electrical_equipment3.png,Deteriorated_wood_enclosure_and_electrical_equipment4.png,Deteriorated_wood_enclosure_and_electrical_equipment5.png,Deteriorated_wood_enclosure_and_electrical_equipment6.png Electrical equipment installed outdoors in a location where it is subject to the weather is required to be adequately protected from the weather either by being installed in an approved weather proof cabinet or being approved for installation in an outdoor location. This is required to protect the equipment from getting wet which can damage and deteriorate the equipment. This installation at a mobile home park has 60A 120/240V sub-service equipment, a light, switch, and receptacle installed inside of a wooden enclosure. The enclosure is rotten, the door has fallen off, and the roof no longer prevents water from entering the wooden enclosure. This has caused the equip | 3 | General Equipment is not approved for the specific use | Deteriorated_wood_enclosure_and_electrical_equipment3.png | file://x:/photopub/docs/0000000599/38a1f4c4-341f-40cc-9b18-4d5d12e238ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2029AE99_6602_4BD9_B4E2_220443DC5F82
ELIN-808327-2017 | EL-351160-2016 | 5/9/2017 | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Bare_lamp_fixtures_installed_in_clothes_closets1.png,Bare_lamp_fixtures_installed_in_clothes_closets2.png,Bare_lamp_fixtures_installed_in_clothes_closets3.png,Bare_lamp_fixtures_installed_in_clothes_closets4.png,Bare_lamp_fixtures_installed_in_clothes_closets5.png Light fixtures installed in clothes closets are not permitted to be bare lamp type fixtures. This is to prevent combustible materials from coming into contact with light bulbs. This installation for a new house has light fixtures installed in the clothes closets that are bare bulb type fixtures. Left uncorrected this is a fire hazard if combustible materials contact hot light bulbs inside of clothes closets. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Bare_lamp_fixtures_installed_in_clothes_closets1.png | file://x:/photopub/docs/0000000599/42026b98-9909-448e-b064-d2d8230b1871.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__86b1817f_8401_42b9_a803_48a576a855ad
AMOP-798951-2017 | 2053232 | 4/21/2017 9:27:03 AM | ASSESS: AM OP: Periodic | png | #asFound | AM018 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | #Corroded_retaining_pin.png Retaining pin on shaft is corroded, pin could fail if shaft ere to move. | 2 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | Corroded_retaining_pin.png | file://x:/photopub/docs/0000000589/cc333fdf-3027-4b2a-ab6b-b0db615d28ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b86ac611_35d7_46f2_a554_d1ec61e6fe63
ELHE-792863-2017 | HE-521243-2017 | 4/12/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL041 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Batteries_mest_be_in_enclosure_and_vented_to_the_outdoors1.png Lead acid batteries are stored in an area that is not sealed and vented from the rest of the house. Accidental contact could occur resulting in shock injury. | 3 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Batteries_mest_be_in_enclosure_and_vented_to_the_outdoors1.png | file://x:/photopub/docs/0000000595/2cf96b6d-e523-4ca2-926d-7c51610c1ad7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d329d31_9cb0_468c_b4c1_709ac707349d
ELHE-792863-2017 | HE-521243-2017 | 4/12/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL041 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Batteries_mest_be_in_enclosure_and_vented_to_the_outdoors1.png Lead acid batteries are stored in an area that is not sealed and vented from the rest of the house. Accidental contact could occur resulting in shock injury. | 3 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Batteries_mest_be_in_enclosure_and_vented_to_the_outdoors1.png | file://x:/photopub/docs/0000000595/f634cd67-e1fd-4661-83d4-19842977edfa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d329d31_9cb0_468c_b4c1_709ac707349d
BPVOP-784779-2017 | 4875541 | 3/6/2017 11:00:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #P_relief_valve.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | P_relief_valve.png | file://x:/photopub/docs/0000000577/048018b2-416b-4ed6-b0da-6e6b7739ea56.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a42d6c6e_bce4_4ac8_8967_b15dafa9f18f
BPVOP-784775-2017 | 4875760 | 3/7/2017 11:00:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #2.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 2.png | file://x:/photopub/docs/0000000577/07607ec6-36cb-47ca-9578-f3cb97f9be87.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03b2d4f8_f29f_4416_a46f_ad57d4fe788a
ELIN-769109-2017 | EL-507835-2017 | 3/7/2017 11:31:40 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL135 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | 3 | 3 | #Unused_opening.png 30 amp, 120/240 volt outlet box installed with unused openings in box. This is a shock hazard. | 3 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | Unused_opening.png | file://x:/photopub/docs/0000000568/3a2c7804-85c0-46f3-9765-7adcc4b2ab9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__04330ee8_98e3_4482_919b_fd7011c6ef63
ELIN-770511-2017 | EL-505090-2017 | 3/9/2017 11:41:24 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_receptacles1.png,Energized_receptacles2.png The 15 amp 120 volt Temporary receptacles do not include cover plates or insulating material protecting persons from accidental contact. This can create a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_receptacles2.png | file://x:/photopub/docs/0000000569/699afda2-d010-44db-9a74-7d80efad09a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__141d756d_c2ee_479d_b69d_d83221e83778
ELIN-770511-2017 | EL-505090-2017 | 3/9/2017 11:41:24 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_receptacles1.png,Energized_receptacles2.png The 15 amp 120 volt Temporary receptacles do not include cover plates or insulating material protecting persons from accidental contact. This can create a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_receptacles1.png | file://x:/photopub/docs/0000000569/0c0ff2b4-fddb-4d4d-b4aa-6d19a0c62570.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__141d756d_c2ee_479d_b69d_d83221e83778
BPVOP-784777-2017 | 4875795 | 3/7/2017 11:00:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #4.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 4.png | file://x:/photopub/docs/0000000577/25286df5-8019-4493-bd39-09fed6326677.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f082839f_8a8d_413b_a062_a83ad610bd37
ELIN-769064-2017 | UW-507799-2017 | 3/7/2017 5:12:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound Junk stored in the electrical room. | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 | #P9.png Electrical room is being used double as a storage, thus creating working hazard around electrical equipment. | 1 | General Working space or dedicated space is being used for storage | P9.png | file://x:/photopub/docs/0000000568/53943b97-a418-4d75-82bb-05b85065a44b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e3880bf2_db6c_43db_b4f9_65a17d5a1c1e
ELIN-792933-2017 | EL-481756-2016 | 4/12/2017 | ASSESS: EL: Service Connection | png | #asFound Found two utility separately supplied systems feeding to privately owned systems. One system is 25kv to 600 volts apparatus on one pole with guy wire and another pole with overhead line system is 120/240 volts. The systems are not separated or installed properly or built to CSA standard as required for installation of high voltage and low voltage systems on same property. This electrical equipment could become damaged and is a possible electrical fire or shock hazard to people and property. | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #HV_and_LV_systems_installed_in_proximity_to_each_other_are_too_close_and_not_compliant1.png,HV_and_LV_systems_installed_in_proximity_to_each_other_are_too_close_and_not_compliant2.png,HV_and_LV_systems_installed_in_proximity_to_each_other_are_too_close_and_not_compliant3.png Found two utility separately supplied systems feeding to privately owned systems. One system is 25kv to 600 volts apparatus on one pole with guy wire and another pole with overhead line system is 120/240 volts. The systems are not separated or installed properly or built to CSA standard as required for installation of high voltage and low voltage systems on same property. This electrical equipment could become damaged and is a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | HV_and_LV_systems_installed_in_proximity_to_each_other_are_too_close_and_not_compliant2.png | file://x:/photopub/docs/0000000588/33835e49-418a-476e-a8c7-92c73c8d1a25.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b313567_8a6b_4b44_a819_0ae716d62755
GAIN-783647-2017 | GA-516318-2017 | 3/28/2017 8:56:31 AM | ASSESS: GA: Final | JPG | #asFound Non compliant vent termination | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #image1.JPG While assessing a rooftop installation i found an appliance vent terminating too close to the mechanical air intake of the adjacent unit. Should the one unit be firing while the other is taking in fresh air, products of combustion could be drawn into the occupied space and distributed through the HVAC system. This could potentially lead to carbon monoxide poisoning of the occupants within. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | image1.JPG | file://x:/photopub/docs/0000000577/bfd575a7-bc06-4412-ada7-3edfc37a6d3a.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b53efdf3_878f_49b6_aaa5_80faa281a05f
ELIN-781038-2017 | EL-507315-2017 | 3/24/2017 12:08:23 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Leg style point of attachment used at this location | EL000 | No Created Hazard Identified | 0 | 0 | #Leg_style__leg_style_point_of_attachment_used.png Leg style point of attachment used at this location | 0 | No Created Hazard Identified | Leg_style__leg_style_point_of_attachment_used.png | file://x:/photopub/docs/0000000576/f49a4348-22b5-4209-a400-6fe60d9bd50d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__185a57ab_4dba_447c_8b05_0622ee38a9ad
ELIN-796507-2017 | EL-523387-2017 | 4/25/2017 10:30:20 AM | ASSESS: EL: Final | png | #asFound | EL151 | Installation of electrical equipment Entrance to dwelling does not have light. | 3 | 3 | #No_light_at_rear_addition_entrance.png Entrance to mobile home addition does not have a light fixture to provide adequate lighting which could result in creating a hazardous scenario at night. | 1 | Installation of electrical equipment Entrance to dwelling does not have light. | No_light_at_rear_addition_entrance.png | file://x:/photopub/docs/0000000590/5340a97e-2ed5-4028-bacd-cf53a0fcc0ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7712a0a_99b4_46f7_b815_9ea1bd22b681
ELIN-792933-2017 | EL-481756-2016 | 4/12/2017 | ASSESS: EL: Service Connection | png | #asFound Found two utility separately supplied systems feeding to privately owned systems. One system is 25kv to 600 volts apparatus on one pole with guy wire and another pole with overhead line system is 120/240 volts. The systems are not separated or installed properly or built to CSA standard as required for installation of high voltage and low voltage systems on same property. This electrical equipment could become damaged and is a possible electrical fire or shock hazard to people and property. | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #HV_and_LV_systems_installed_in_proximity_to_each_other_are_too_close_and_not_compliant1.png,HV_and_LV_systems_installed_in_proximity_to_each_other_are_too_close_and_not_compliant2.png,HV_and_LV_systems_installed_in_proximity_to_each_other_are_too_close_and_not_compliant3.png Found two utility separately supplied systems feeding to privately owned systems. One system is 25kv to 600 volts apparatus on one pole with guy wire and another pole with overhead line system is 120/240 volts. The systems are not separated or installed properly or built to CSA standard as required for installation of high voltage and low voltage systems on same property. This electrical equipment could become damaged and is a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | HV_and_LV_systems_installed_in_proximity_to_each_other_are_too_close_and_not_compliant3.png | file://x:/photopub/docs/0000000588/25a8b259-740c-41a0-853c-d0713db47b18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b313567_8a6b_4b44_a819_0ae716d62755
ELOP-794442-2017 | EL-240471-2015 | 4/12/2017 9:48:01 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png Buildings located under primary power lines. The buildings have ungrounded metal roofs. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | A4.png | file://x:/photopub/docs/0000000586/30865fcc-c993-48ae-ba41-6963dfc83fbd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ef0af9c_ee3b_4dfb_8223_1dd4a81ed9f1
ELOP-794442-2017 | EL-240471-2015 | 4/12/2017 9:48:01 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png Buildings located under primary power lines. The buildings have ungrounded metal roofs. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | A5.png | file://x:/photopub/docs/0000000586/1093d4a4-63ee-4783-bfe5-bb01aef635e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ef0af9c_ee3b_4dfb_8223_1dd4a81ed9f1
ELOP-794442-2017 | EL-240471-2015 | 4/12/2017 9:48:01 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png Buildings located under primary power lines. The buildings have ungrounded metal roofs. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | A1.png | file://x:/photopub/docs/0000000586/50505b51-26d8-4010-9fa6-842a9b9524fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ef0af9c_ee3b_4dfb_8223_1dd4a81ed9f1
ELOP-794442-2017 | EL-240471-2015 | 4/12/2017 9:48:01 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png Buildings located under primary power lines. The buildings have ungrounded metal roofs. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | A2.png | file://x:/photopub/docs/0000000586/9fdf65d2-01ad-47ee-8417-84f26e210c1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ef0af9c_ee3b_4dfb_8223_1dd4a81ed9f1
ELOP-794442-2017 | EL-240471-2015 | 4/12/2017 9:48:01 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png Buildings located under primary power lines. The buildings have ungrounded metal roofs. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | A3.png | file://x:/photopub/docs/0000000586/17340482-3f00-47df-b5a3-5dbd6e1aa471.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ef0af9c_ee3b_4dfb_8223_1dd4a81ed9f1
ELIN-779648-2017 | EL-385989-2016 | 3/21/2017 9:37:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_and_exposed_electrical_conductors_subject_to_shock_hazards1.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards2.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards3.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards4.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards5.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards6.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards7.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_and_exposed_electrical_conductors_subject_to_shock_hazards8.png | file://x:/photopub/docs/0000000577/4a2464fc-059d-43ce-bba0-fd59e8e2674f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0f95d96_f949_4990_94c5_919743a7d155
ELHE-780151-2017 | HE-514438-2017 | 3/21/2017 10:59:55 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Boards with nails on top of energized flexible extension cords and workers are stepping on cables that are damaged. NMD90 cable is used outdoors on grade and on floor of building where workers are stepping on exposed energized conductors that are connected to 240 volts | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers1.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers2.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers3.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers4.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers5.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers6.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers7.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the electrical equipment is very unsafe and | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers7.png | file://x:/photopub/docs/0000000577/d988c031-14bf-4b92-81f5-3424c50b5f41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfb9a0c7_5014_4e00_a904_3cd8cf7f6aec
ELIN-779648-2017 | EL-385989-2016 | 3/21/2017 9:37:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_and_exposed_electrical_conductors_subject_to_shock_hazards1.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards2.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards3.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards4.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards5.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards6.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards7.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_and_exposed_electrical_conductors_subject_to_shock_hazards6.png | file://x:/photopub/docs/0000000577/66d09bf1-c172-4464-a27a-fcc566490e5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0f95d96_f949_4990_94c5_919743a7d155
ELIN-801711-2017 | EL-516165-2017 | 5/4/2017 1:25:49 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | #Ground_connection.png The 200 amp 120/240 volt service main systems ground conductor is terminated on the enclosure and not to the identified conductor. Any fault that may occur that is directed to earth is reliant on the bonding screw/strap and this can cause an equipment damage issue | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Ground_connection.png | file://x:/photopub/docs/0000000597/2cc645ff-4fed-4041-bec9-eb2fbd5e2b41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51e59a98_7e71_4682_a3bb_5a911c1895a7
ELIN-756247-2017 | EL-451490-2016 | 2/28/2017 3:46:50 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 4 | #No_AFCI_Protection1.png,No_AFCI_Protection2.png,No_AFCI_Protection3.png,No_AFCI_Protection4.png,No_AFCI_Protection5.png Arc-fault protection is required on most new branch circuits supplying 125 volt receptacles 20 amps or less that are installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizes the circuit when an arc-fault is detected. During a final electrical inspection of a large addition to a single family dwelling, the electrical safety officer found only four arc-fault breakers in the electrical panel. An assessment of the 15 amp, 125V receptacles revealed that many of the branch circuits for the bedrooms, common area's, and family rooms were not arc-fault protected. If a series or parallel arc was to occur in one of the branch circuit or in an appliance connected to this circuit, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and prop | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | No_AFCI_Protection2.png | file://x:/photopub/docs/0000000565/0afae57b-1cdc-4ef9-9342-0cb276a4b07f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2380d9fa_60ef_4cd3_8681_c3beb1645a17
ELIN-756247-2017 | EL-451490-2016 | 2/28/2017 3:46:50 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 4 | #No_AFCI_Protection1.png,No_AFCI_Protection2.png,No_AFCI_Protection3.png,No_AFCI_Protection4.png,No_AFCI_Protection5.png Arc-fault protection is required on most new branch circuits supplying 125 volt receptacles 20 amps or less that are installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizes the circuit when an arc-fault is detected. During a final electrical inspection of a large addition to a single family dwelling, the electrical safety officer found only four arc-fault breakers in the electrical panel. An assessment of the 15 amp, 125V receptacles revealed that many of the branch circuits for the bedrooms, common area's, and family rooms were not arc-fault protected. If a series or parallel arc was to occur in one of the branch circuit or in an appliance connected to this circuit, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and prop | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | No_AFCI_Protection4.png | file://x:/photopub/docs/0000000565/dc271a9d-1762-48a1-a3a4-7c75d7daf104.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2380d9fa_60ef_4cd3_8681_c3beb1645a17
ELIN-780166-2017 | EL-502214-2017 | 3/27/2017 12:35:21 PM | ASSESS: EL: Final | png | #asFound 400A service attached to 2" EMT/RW90 | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | #Service.png 2" EMT used to support 400A OH service. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Service.png | file://x:/photopub/docs/0000000577/7b72ec90-2aa1-476a-8fe5-a511e27b5b64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae3c3729_0c28_4908_a7b7_5c25c3d36ce1
ELIN-778744-2017 | EL-385989-2016 | 3/20/2017 5:11:41 PM | ASSESS: EL: Service Connection | png | #asFound Energized and exposed 240 volt conductors are damaged and being stepped on by workers | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_exposed_conductors_being_stepped_on_by_workers1.png,Energized_exposed_conductors_being_stepped_on_by_workers2.png,Energized_exposed_conductors_being_stepped_on_by_workers3.png,Energized_exposed_conductors_being_stepped_on_by_workers4.png,Energized_exposed_conductors_being_stepped_on_by_workers5.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the electrical equipment is very unsafe and is an imminent electrical shock or fire hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_exposed_conductors_being_stepped_on_by_workers2.png | file://x:/photopub/docs/0000000577/04e1532a-1a21-41fa-8db7-3df3ed178331.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67508dca_cd2e_4a4c_bb74_0048d538e0b2
ELIN-778744-2017 | EL-385989-2016 | 3/20/2017 5:11:41 PM | ASSESS: EL: Service Connection | png | #asFound Energized and exposed 240 volt conductors are damaged and being stepped on by workers | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_exposed_conductors_being_stepped_on_by_workers1.png,Energized_exposed_conductors_being_stepped_on_by_workers2.png,Energized_exposed_conductors_being_stepped_on_by_workers3.png,Energized_exposed_conductors_being_stepped_on_by_workers4.png,Energized_exposed_conductors_being_stepped_on_by_workers5.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the electrical equipment is very unsafe and is an imminent electrical shock or fire hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_exposed_conductors_being_stepped_on_by_workers1.png | file://x:/photopub/docs/0000000577/2aee1f4a-eb0a-4f27-b857-91f8fab6e5e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67508dca_cd2e_4a4c_bb74_0048d538e0b2
ELIN-779648-2017 | EL-385989-2016 | 3/21/2017 9:37:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_and_exposed_electrical_conductors_subject_to_shock_hazards1.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards2.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards3.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards4.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards5.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards6.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards7.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_and_exposed_electrical_conductors_subject_to_shock_hazards2.png | file://x:/photopub/docs/0000000577/09d9a327-c73a-419d-96c6-58fa7d472469.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0f95d96_f949_4990_94c5_919743a7d155
ELIN-779648-2017 | EL-385989-2016 | 3/21/2017 9:37:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_and_exposed_electrical_conductors_subject_to_shock_hazards1.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards2.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards3.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards4.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards5.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards6.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards7.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_and_exposed_electrical_conductors_subject_to_shock_hazards5.png | file://x:/photopub/docs/0000000577/a17a3fd3-493e-4566-95db-61c9aa5c3006.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0f95d96_f949_4990_94c5_919743a7d155
ELIN-765807-2017 | EL-505703-2017 | 3/1/2017 11:00:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Weatherproofing.png Equipment is not weatherproof. Potential for damage and shock. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Weatherproofing.png | file://x:/photopub/docs/0000000564/c3ec1ea7-a002-45b4-9ede-8f5e7d3cce64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f5c7f9b_c819_469e_8bad_7a159b58b0c2
ELIN-765054-2017 | EL-505704-2017 | 3/1/2017 12:17:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Tarp_only_and_no_lockable_door.png No lovable door on temporary service. Service can be accessed by public creating a hazard for shock. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Tarp_only_and_no_lockable_door.png | file://x:/photopub/docs/0000000564/41009c21-57fb-4947-9c54-08213fb53e6f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6352551_3aae_496f_97da_3b2b43911e0f
ELHE-780151-2017 | HE-514438-2017 | 3/21/2017 10:59:55 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Boards with nails on top of energized flexible extension cords and workers are stepping on cables that are damaged. NMD90 cable is used outdoors on grade and on floor of building where workers are stepping on exposed energized conductors that are connected to 240 volts | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers1.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers2.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers3.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers4.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers5.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers6.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers7.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the electrical equipment is very unsafe and | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers8.png | file://x:/photopub/docs/0000000577/d1636fc1-d2d9-404b-a1bd-256ac98c3ef0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfb9a0c7_5014_4e00_a904_3cd8cf7f6aec
ELIN-764931-2017 | EL-439454-2016 | 2/28/2017 9:02:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 4 | #Termination_on_load_side_of_top_ct_not_tightened1.png,Termination_on_load_side_of_top_ct_not_tightened2.png Termination of electrical conductors must be made up tight according to the manufactures torque specifications related to the equipment involved. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation of a new 400A 120/208V 3 phase service in a commercial building had one of the conductor terminations at a current transformer installed for the utility metering that was not properly tightened. The termination lug had a hex type fastener that is intended to fasten the conductor into the lug. The fastener was not tightened properly and left in a finger tight state. Left uncorrected this is a fire and arc flash hazard if the conductor termination becomes over heated due to a high impedance connection. This can cause the conductor insulation to melt or soften and contact the metal enclosure, cond | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Termination_on_load_side_of_top_ct_not_tightened1.png | file://x:/photopub/docs/0000000564/c15fe220-c90a-4245-9819-f677c162cfb7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3adb4802_aede_4bbb_8226_90b2c9cd9a4d
ELIN-764931-2017 | EL-439454-2016 | 2/28/2017 9:02:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 4 | #Termination_on_load_side_of_top_ct_not_tightened1.png,Termination_on_load_side_of_top_ct_not_tightened2.png Termination of electrical conductors must be made up tight according to the manufactures torque specifications related to the equipment involved. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation of a new 400A 120/208V 3 phase service in a commercial building had one of the conductor terminations at a current transformer installed for the utility metering that was not properly tightened. The termination lug had a hex type fastener that is intended to fasten the conductor into the lug. The fastener was not tightened properly and left in a finger tight state. Left uncorrected this is a fire and arc flash hazard if the conductor termination becomes over heated due to a high impedance connection. This can cause the conductor insulation to melt or soften and contact the metal enclosure, cond | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Termination_on_load_side_of_top_ct_not_tightened2.png | file://x:/photopub/docs/0000000564/569b977a-906c-404a-ac3f-77939e9e4fa5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3adb4802_aede_4bbb_8226_90b2c9cd9a4d
ELIN-756247-2017 | EL-451490-2016 | 2/28/2017 3:46:50 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 4 | #No_AFCI_Protection1.png,No_AFCI_Protection2.png,No_AFCI_Protection3.png,No_AFCI_Protection4.png,No_AFCI_Protection5.png Arc-fault protection is required on most new branch circuits supplying 125 volt receptacles 20 amps or less that are installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizes the circuit when an arc-fault is detected. During a final electrical inspection of a large addition to a single family dwelling, the electrical safety officer found only four arc-fault breakers in the electrical panel. An assessment of the 15 amp, 125V receptacles revealed that many of the branch circuits for the bedrooms, common area's, and family rooms were not arc-fault protected. If a series or parallel arc was to occur in one of the branch circuit or in an appliance connected to this circuit, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and prop | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | No_AFCI_Protection5.png | file://x:/photopub/docs/0000000565/83d357b2-63c4-478b-a999-25839af0c448.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2380d9fa_60ef_4cd3_8681_c3beb1645a17
ELIN-756247-2017 | EL-451490-2016 | 2/28/2017 3:46:50 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 4 | #No_AFCI_Protection1.png,No_AFCI_Protection2.png,No_AFCI_Protection3.png,No_AFCI_Protection4.png,No_AFCI_Protection5.png Arc-fault protection is required on most new branch circuits supplying 125 volt receptacles 20 amps or less that are installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizes the circuit when an arc-fault is detected. During a final electrical inspection of a large addition to a single family dwelling, the electrical safety officer found only four arc-fault breakers in the electrical panel. An assessment of the 15 amp, 125V receptacles revealed that many of the branch circuits for the bedrooms, common area's, and family rooms were not arc-fault protected. If a series or parallel arc was to occur in one of the branch circuit or in an appliance connected to this circuit, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and prop | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | No_AFCI_Protection1.png | file://x:/photopub/docs/0000000565/6d558c7b-d838-4dc8-8c80-29ce8a90af6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2380d9fa_60ef_4cd3_8681_c3beb1645a17
ELIN-756247-2017 | EL-451490-2016 | 2/28/2017 3:46:50 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 4 | #No_AFCI_Protection1.png,No_AFCI_Protection2.png,No_AFCI_Protection3.png,No_AFCI_Protection4.png,No_AFCI_Protection5.png Arc-fault protection is required on most new branch circuits supplying 125 volt receptacles 20 amps or less that are installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizes the circuit when an arc-fault is detected. During a final electrical inspection of a large addition to a single family dwelling, the electrical safety officer found only four arc-fault breakers in the electrical panel. An assessment of the 15 amp, 125V receptacles revealed that many of the branch circuits for the bedrooms, common area's, and family rooms were not arc-fault protected. If a series or parallel arc was to occur in one of the branch circuit or in an appliance connected to this circuit, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and prop | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | No_AFCI_Protection3.png | file://x:/photopub/docs/0000000565/5225987e-6785-412e-bfd6-b157619bfe87.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2380d9fa_60ef_4cd3_8681_c3beb1645a17
EDIN-762234-2017 | ED-459000-2016 | 2/24/2017 3:17:23 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | #In-car_autodialler.png The emergency 2-way emergency communication in the elevator is a means of communication to a 24 hours/day monitored station. During an acceptance inspection it was found the 2-way emergency communication was not functioning properly because the monitoring station was not able to tell us our location. Without a properly functioning 2-way emergency communication in the elevator it may be difficult to get help in case of an entrapment in the elevator. This may result in a serious situation if panic sets in or if a person had a medical emergency and was trapped in the elevator. This is a 3 stop MRL traction elevator located in a commercial building. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | In-car_autodialler.png | file://x:/photopub/docs/0000000562/c949c4f0-c9d8-4349-9c16-071b59d3edf8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c28dfc28_98a4_4746_adef_fe32dd890992
ELIN-738350-2017 | UW-241931-2015 | 2/24/2017 3:35:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_in_massage_therapy_environment1.png,Unapproved_electrical_equipment_in_massage_therapy_environment2.png,Unapproved_electrical_equipment_in_massage_therapy_environment3.png,Unapproved_electrical_equipment_in_massage_therapy_environment4.png,Unapproved_electrical_equipment_in_massage_therapy_environment5.png,Unapproved_electrical_equipment_in_massage_therapy_environment6.png,Unapproved_electrical_equipment_in_massage_therapy_environment7.png Found electrical product marked as 120 volt rated and has no recognized approval or certification mark/label attached to electrical equipment as required in INFORMATION BULLETIN No. B-E3 071019 3. The electrical equipment is connected, energized and is intended for being used in contact with a patient having massage therapy done with medical doctor on staff. Electrical equipment/products which are not approved or certified as required by regulations and not tested to meet required standards for this environment could pose to be an electrical | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_in_massage_therapy_environment1.png | file://x:/photopub/docs/0000000562/ed172415-400e-41a3-ba69-033b3902cc02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d560c2fb_7718_41d8_b34d_1243de6fcd8c
ELIN-738350-2017 | UW-241931-2015 | 2/24/2017 3:35:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_in_massage_therapy_environment1.png,Unapproved_electrical_equipment_in_massage_therapy_environment2.png,Unapproved_electrical_equipment_in_massage_therapy_environment3.png,Unapproved_electrical_equipment_in_massage_therapy_environment4.png,Unapproved_electrical_equipment_in_massage_therapy_environment5.png,Unapproved_electrical_equipment_in_massage_therapy_environment6.png,Unapproved_electrical_equipment_in_massage_therapy_environment7.png Found electrical product marked as 120 volt rated and has no recognized approval or certification mark/label attached to electrical equipment as required in INFORMATION BULLETIN No. B-E3 071019 3. The electrical equipment is connected, energized and is intended for being used in contact with a patient having massage therapy done with medical doctor on staff. Electrical equipment/products which are not approved or certified as required by regulations and not tested to meet required standards for this environment could pose to be an electrical | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_in_massage_therapy_environment7.png | file://x:/photopub/docs/0000000562/72d43ed4-08e6-4636-9494-fe75dfa05395.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d560c2fb_7718_41d8_b34d_1243de6fcd8c
ELIN-738350-2017 | UW-241931-2015 | 2/24/2017 3:35:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_in_massage_therapy_environment1.png,Unapproved_electrical_equipment_in_massage_therapy_environment2.png,Unapproved_electrical_equipment_in_massage_therapy_environment3.png,Unapproved_electrical_equipment_in_massage_therapy_environment4.png,Unapproved_electrical_equipment_in_massage_therapy_environment5.png,Unapproved_electrical_equipment_in_massage_therapy_environment6.png,Unapproved_electrical_equipment_in_massage_therapy_environment7.png Found electrical product marked as 120 volt rated and has no recognized approval or certification mark/label attached to electrical equipment as required in INFORMATION BULLETIN No. B-E3 071019 3. The electrical equipment is connected, energized and is intended for being used in contact with a patient having massage therapy done with medical doctor on staff. Electrical equipment/products which are not approved or certified as required by regulations and not tested to meet required standards for this environment could pose to be an electrical | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_in_massage_therapy_environment4.png | file://x:/photopub/docs/0000000562/ffcbf276-f607-4595-a676-221f51df14d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d560c2fb_7718_41d8_b34d_1243de6fcd8c
ELIN-779648-2017 | EL-385989-2016 | 3/21/2017 9:37:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_and_exposed_electrical_conductors_subject_to_shock_hazards1.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards2.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards3.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards4.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards5.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards6.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards7.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_and_exposed_electrical_conductors_subject_to_shock_hazards7.png | file://x:/photopub/docs/0000000577/fbe9bef5-48a7-4bb0-be04-73cbe86cb1cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0f95d96_f949_4990_94c5_919743a7d155
ELIN-779648-2017 | EL-385989-2016 | 3/21/2017 9:37:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_and_exposed_electrical_conductors_subject_to_shock_hazards1.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards2.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards3.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards4.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards5.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards6.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards7.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_and_exposed_electrical_conductors_subject_to_shock_hazards1.png | file://x:/photopub/docs/0000000577/a5937423-b05a-4788-97ec-ef1bc60b010e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0f95d96_f949_4990_94c5_919743a7d155
ELIN-779648-2017 | EL-385989-2016 | 3/21/2017 9:37:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_and_exposed_electrical_conductors_subject_to_shock_hazards1.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards2.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards3.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards4.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards5.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards6.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards7.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_and_exposed_electrical_conductors_subject_to_shock_hazards3.png | file://x:/photopub/docs/0000000577/2ae95485-6b9d-4624-a1eb-9c949be30787.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0f95d96_f949_4990_94c5_919743a7d155
ELHE-780151-2017 | HE-514438-2017 | 3/21/2017 10:59:55 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Boards with nails on top of energized flexible extension cords and workers are stepping on cables that are damaged | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers1.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers2.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers3.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers4.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers5.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers6.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers7.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the electrical equipment is very unsafe and | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers1.png | file://x:/photopub/docs/0000000577/e5f47580-dda9-4f7c-a439-aba32c9c04ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfb9a0c7_5014_4e00_a904_3cd8cf7f6aec
ELIN-779648-2017 | EL-385989-2016 | 3/21/2017 9:37:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_and_exposed_electrical_conductors_subject_to_shock_hazards1.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards2.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards3.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards4.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards5.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards6.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards7.png,Energized_and_exposed_electrical_conductors_subject_to_shock_hazards8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_and_exposed_electrical_conductors_subject_to_shock_hazards4.png | file://x:/photopub/docs/0000000577/0fa2e641-7e1c-4150-ab99-12bc132f45c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0f95d96_f949_4990_94c5_919743a7d155
ELIN-808376-2017 | EL-529545-2017 | 5/3/2017 10:59:36 AM | ASSESS: EL: Service Connection | png | #asFound Service conduit incorrectly bent | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Service_conduit.png Temporary construction service in poor and neglected condition. EMT conduit incorrectly bent, allowing the weatherproof connecter at the top of the metre base to not work as intended, allowing water to ingress into electrical metre base equipment | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Service_conduit.png | file://x:/photopub/docs/0000000595/a0972dea-58c7-4e45-bdf2-bab9d59b21c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2821d42_1ed0_4835_9b0b_c244bc6dbdb5
BPVIN-777020-2017 | UW-512747-2017 | 3/14/2017 8:33:51 AM | ASSESS: BPV IN: Installation REF/PV | pdf | #asFound Inspection photos | BP002 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | 5 | 5 | #BPV-032676_Expansion_Tank_Inspection_photos.pdf Regulated Cushion Expansion tank replaced without notification or inspection by Safety Officer and installed pressure vessel not manufactured to ASME Section VIII-1. If vessel not constructed to appropriate code, unit could rupture if subjected to over temperature or pressure condition. | 5 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | BPV-032676_Expansion_Tank_Inspection_photos.pdf | file://x:/photopub/docs/0000000576/551cff70-ca4d-4be2-b80f-1eab1956b1dc.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b909e6ea_ac3a_476b_b89f_78ce7c9aae42
BPVIN-777020-2017 | UW-512747-2017 | 3/14/2017 8:33:51 AM | ASSESS: BPV IN: Installation REF/PV | pdf | #asFound Photo package attached. | BP002 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | 5 | 5 | #BPV-032676_Expansion_Tank_Inspection_photos.pdf Regulated Cushion Expansion tank replaced without notification or inspection by Safety Officer and installed pressure vessel not manufactured to ASME Section VIII-1. If vessel not constructed to appropriate code, unit could rupture if subjected to over temperature or pressure condition. | 5 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | BPV-032676_Expansion_Tank_Inspection_photos.pdf | file://x:/photopub/docs/0000000576/ce8b249a-f36d-4eb4-902a-48eaac9a732c.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b909e6ea_ac3a_476b_b89f_78ce7c9aae42
ELIN-792889-2017 | EL-452703-2016 | 4/11/2017 3:08:19 PM | ASSESS: EL: Service Connection | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | #Underground_ACWU_no_termination.png Underground Service conductor is not bonded or mechanical connected to meter base. Potential for damage to meter base lugs from cable settling or shifting resulting in an electrical fault, shock hazard or fire. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Underground_ACWU_no_termination.png | file://x:/photopub/docs/0000000585/6e14e3d4-51ec-4f84-beb1-5432b368bf8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5429c302_5e0d_43a1_a235_6619fd9a9e37
ELIN-738350-2017 | UW-241931-2015 | 2/24/2017 3:35:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_in_massage_therapy_environment1.png,Unapproved_electrical_equipment_in_massage_therapy_environment2.png,Unapproved_electrical_equipment_in_massage_therapy_environment3.png,Unapproved_electrical_equipment_in_massage_therapy_environment4.png,Unapproved_electrical_equipment_in_massage_therapy_environment5.png,Unapproved_electrical_equipment_in_massage_therapy_environment6.png,Unapproved_electrical_equipment_in_massage_therapy_environment7.png Found electrical product marked as 120 volt rated and has no recognized approval or certification mark/label attached to electrical equipment as required in INFORMATION BULLETIN No. B-E3 071019 3. The electrical equipment is connected, energized and is intended for being used in contact with a patient having massage therapy done with medical doctor on staff. Electrical equipment/products which are not approved or certified as required by regulations and not tested to meet required standards for this environment could pose to be an electrical | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_in_massage_therapy_environment6.png | file://x:/photopub/docs/0000000562/c70ffb16-a07e-4638-9b12-f7e4b1cf29df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d560c2fb_7718_41d8_b34d_1243de6fcd8c
ELIN-738350-2017 | UW-241931-2015 | 2/24/2017 3:35:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_in_massage_therapy_environment1.png,Unapproved_electrical_equipment_in_massage_therapy_environment2.png,Unapproved_electrical_equipment_in_massage_therapy_environment3.png,Unapproved_electrical_equipment_in_massage_therapy_environment4.png,Unapproved_electrical_equipment_in_massage_therapy_environment5.png,Unapproved_electrical_equipment_in_massage_therapy_environment6.png,Unapproved_electrical_equipment_in_massage_therapy_environment7.png Found electrical product marked as 120 volt rated and has no recognized approval or certification mark/label attached to electrical equipment as required in INFORMATION BULLETIN No. B-E3 071019 3. The electrical equipment is connected, energized and is intended for being used in contact with a patient having massage therapy done with medical doctor on staff. Electrical equipment/products which are not approved or certified as required by regulations and not tested to meet required standards for this environment could pose to be an electrical | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_in_massage_therapy_environment5.png | file://x:/photopub/docs/0000000562/c674692e-1ac5-497d-b425-8f687784728c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d560c2fb_7718_41d8_b34d_1243de6fcd8c
ELIN-738350-2017 | UW-241931-2015 | 2/24/2017 3:35:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_in_massage_therapy_environment1.png,Unapproved_electrical_equipment_in_massage_therapy_environment2.png,Unapproved_electrical_equipment_in_massage_therapy_environment3.png,Unapproved_electrical_equipment_in_massage_therapy_environment4.png,Unapproved_electrical_equipment_in_massage_therapy_environment5.png,Unapproved_electrical_equipment_in_massage_therapy_environment6.png,Unapproved_electrical_equipment_in_massage_therapy_environment7.png Found electrical product marked as 120 volt rated and has no recognized approval or certification mark/label attached to electrical equipment as required in INFORMATION BULLETIN No. B-E3 071019 3. The electrical equipment is connected, energized and is intended for being used in contact with a patient having massage therapy done with medical doctor on staff. Electrical equipment/products which are not approved or certified as required by regulations and not tested to meet required standards for this environment could pose to be an electrical | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_in_massage_therapy_environment3.png | file://x:/photopub/docs/0000000562/1d1a817d-80e1-4fb3-9525-1b298bda0901.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d560c2fb_7718_41d8_b34d_1243de6fcd8c
ELIN-738350-2017 | UW-241931-2015 | 2/24/2017 3:35:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_in_massage_therapy_environment1.png,Unapproved_electrical_equipment_in_massage_therapy_environment2.png,Unapproved_electrical_equipment_in_massage_therapy_environment3.png,Unapproved_electrical_equipment_in_massage_therapy_environment4.png,Unapproved_electrical_equipment_in_massage_therapy_environment5.png,Unapproved_electrical_equipment_in_massage_therapy_environment6.png,Unapproved_electrical_equipment_in_massage_therapy_environment7.png Found electrical product marked as 120 volt rated and has no recognized approval or certification mark/label attached to electrical equipment as required in INFORMATION BULLETIN No. B-E3 071019 3. The electrical equipment is connected, energized and is intended for being used in contact with a patient having massage therapy done with medical doctor on staff. Electrical equipment/products which are not approved or certified as required by regulations and not tested to meet required standards for this environment could pose to be an electrical | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_in_massage_therapy_environment2.png | file://x:/photopub/docs/0000000562/df85b21c-2b07-4e68-97d4-4a3558681b57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d560c2fb_7718_41d8_b34d_1243de6fcd8c
ELHE-780151-2017 | HE-514438-2017 | 3/21/2017 10:59:55 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Boards with nails on top of energized flexible extension cords and workers are stepping on cables that are damaged. NMD90 cable is used outdoors on grade and on floor of building where workers are stepping on exposed energized conductors that are connected to 240 volts | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers1.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers2.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers3.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers4.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers5.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers6.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers7.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the electrical equipment is very unsafe and | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers5.png | file://x:/photopub/docs/0000000577/0d363073-72d4-4a5e-a656-553d83bce047.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfb9a0c7_5014_4e00_a904_3cd8cf7f6aec
BPVOP-805425-2017 | 2254120 | 4/28/2017 1:23:20 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_relief_valve.png Upon assessment it is determined that heat exchanger (1.3m long and .50m diameter) with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 375*Fahrenheit, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject heat exchanger to pressure above MAWP if operating control fails. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_valve.png | file://x:/photopub/docs/0000000592/a449efd3-b4dd-427b-93ea-019d46c049f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__478da314_693a_4709_8a24_502b5adfd40c
ELIN-785694-2017 | EL-462811-2016 | 3/31/2017 12:47:47 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Numerous outlets boxes found energized and without devices/covers installed | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Outlets1.png,Outlets2.png,Outlets3.png Numerous outlets boxes found energized and without devices/covers installed | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outlets1.png | file://x:/photopub/docs/0000000579/6453ab31-1245-4f45-a83b-d618b33571c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69b1c5a1_779d_484d_8e7a_d5e2e106032b
ELIN-785694-2017 | EL-462811-2016 | 3/31/2017 12:47:47 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Outlets1.png,Outlets2.png,Outlets3.png Numerous outlets boxes found energized and without devices/covers installed | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outlets2.png | file://x:/photopub/docs/0000000579/cb59e8c9-01f8-406b-b858-7a35b6f4e110.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69b1c5a1_779d_484d_8e7a_d5e2e106032b
ELIN-785694-2017 | EL-462811-2016 | 3/31/2017 12:47:47 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Outlets1.png,Outlets2.png,Outlets3.png Numerous outlets boxes found energized and without devices/covers installed | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outlets3.png | file://x:/photopub/docs/0000000579/14a95a8d-2dd9-4c2b-b39a-9a8f19529b95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69b1c5a1_779d_484d_8e7a_d5e2e106032b
ELIN-783966-2017 | EL-495306-2017 | 3/30/2017 3:42:21 PM | ASSESS: EL: Final | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #No_covers1.png,No_covers2.png Panel covers on 200 and 100 Amp Combination panels were not installed at time of inspection. This is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | No_covers2.png | file://x:/photopub/docs/0000000579/fbffc7dd-70bf-4611-9bbe-c649fc7ad351.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f307e9e1_d709_4229_9278_a7701444d4ba
ELIN-783966-2017 | EL-495306-2017 | 3/30/2017 3:42:21 PM | ASSESS: EL: Final | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #No_covers1.png,No_covers2.png Panel covers on 200 and 100 Amp Combination panels were not installed at time of inspection. This is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | No_covers1.png | file://x:/photopub/docs/0000000579/a952db9b-a56a-486b-81cf-2e87cfc8832d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f307e9e1_d709_4229_9278_a7701444d4ba
ELIN-778744-2017 | EL-385989-2016 | 3/20/2017 5:11:41 PM | ASSESS: EL: Service Connection | png | #asFound Energized and exposed 240 volt conductors are damaged and being stepped on by workers | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_exposed_conductors_being_stepped_on_by_workers1.png,Energized_exposed_conductors_being_stepped_on_by_workers2.png,Energized_exposed_conductors_being_stepped_on_by_workers3.png,Energized_exposed_conductors_being_stepped_on_by_workers4.png,Energized_exposed_conductors_being_stepped_on_by_workers5.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the electrical equipment is very unsafe and is an imminent electrical shock or fire hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_exposed_conductors_being_stepped_on_by_workers4.png | file://x:/photopub/docs/0000000577/14a9b62e-03fa-4656-8da1-e9673fdb366c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67508dca_cd2e_4a4c_bb74_0048d538e0b2
ELHE-780151-2017 | HE-514438-2017 | 3/21/2017 10:59:55 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Boards with nails on top of energized flexible extension cords and workers are stepping on cables that are damaged. NMD90 cable is used outdoors on grade and on floor of building where workers are stepping on exposed energized conductors. | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers1.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers2.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers3.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers4.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers5.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers6.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers7.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the electrical equipment is very unsafe and | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers4.png | file://x:/photopub/docs/0000000577/c8eb2bc3-4fd0-45b6-b8e6-abf85f1a8448.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfb9a0c7_5014_4e00_a904_3cd8cf7f6aec
ELIN-778744-2017 | EL-385989-2016 | 3/20/2017 5:11:41 PM | ASSESS: EL: Service Connection | png | #asFound Energized and exposed 240 volt conductors are damaged and being stepped on by workers | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_exposed_conductors_being_stepped_on_by_workers1.png,Energized_exposed_conductors_being_stepped_on_by_workers2.png,Energized_exposed_conductors_being_stepped_on_by_workers3.png,Energized_exposed_conductors_being_stepped_on_by_workers4.png,Energized_exposed_conductors_being_stepped_on_by_workers5.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the electrical equipment is very unsafe and is an imminent electrical shock or fire hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_exposed_conductors_being_stepped_on_by_workers3.png | file://x:/photopub/docs/0000000577/4e742a57-551f-4171-8bc6-6698e8f55418.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67508dca_cd2e_4a4c_bb74_0048d538e0b2
AMOP-798924-2017 | 3004079 | 4/21/2017 10:47:35 AM | ASSESS: AM OP: Periodic | png | #asFound | AM037 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | #PCU_9_lap_bar_not_latching.png The lap bar on a passenger carrying unit did not latch when tested, lap bar could fail when used by rider. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | PCU_9_lap_bar_not_latching.png | file://x:/photopub/docs/0000000589/31386018-8b7e-4746-8fe6-112e25d1f195.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee39b75c_21bf_49ee_8c02_e387fd7455e2
BPVOP-805431-2017 | 4528377 | 4/28/2017 1:54:08 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRV.png Upon assessment it is determined that machine mounted horizontal air receiver (1.7m long and 0.80m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRV.png | file://x:/photopub/docs/0000000592/e2f95575-18ef-49ff-b452-0a0f495de6b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__326ccaa1_ab7b_4c05_9e6b_4a6457b89b09
BPVOP-805480-2017 | 4518155 | 4/28/2017 2:16:38 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #T_and_P_Relief_Valve.png Upon assessment it is determined that domestic hot water storage vessel (2m long and 0.90m diameter) with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, has a temperature and pressure (T&P) relief valve that exceeded the required 3 year interval for replacement. Failure to have T&P relief valve replaced as required may subject vessel to pressure above MAWP and/or temperature above MAWT if operating control fails. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | T_and_P_Relief_Valve.png | file://x:/photopub/docs/0000000592/1f648a68-4711-48a1-a2cc-00e8e0b8bebe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b091821_d99d_428e_95b7_cc1ee4232a8e
ELIN-769283-2017 | EL-493259-2017 | 3/7/2017 11:35:56 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Energized panel without cover or lockable door installed. | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_panel11.png,Energized_panel12.png Energized panel without cover installed and without qualified individual on site, 2 unqualified individuals installing electrical equipment without qualified supervision on site | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_panel11.png | file://x:/photopub/docs/0000000567/0395ecc9-2df8-45d1-92af-f7810d81b069.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6688335_dde7_4f56_bf93_50016a4d0579
ELIN-769283-2017 | EL-493259-2017 | 3/7/2017 11:35:56 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_panel11.png,Energized_panel12.png Energized panel without cover installed and without qualified individual on site, 2 unqualified individuals installing electrical equipment without qualified supervision on site | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_panel12.png | file://x:/photopub/docs/0000000567/96520eb9-686c-4b94-9e03-c0f124509dc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6688335_dde7_4f56_bf93_50016a4d0579
ELIN-771163-2017 | UW-509016-2017 | 3/7/2017 1:11:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Exposed_and_energized.png A cover plate was not installed on an energized receptacle. This condition could expose the occupants to accidental contact resulting in a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Exposed_and_energized.png | file://x:/photopub/docs/0000000568/ae05c9c2-fcff-4b16-ab87-510a50a53566.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd5643d8_251b_4756_8d2e_d0ef4bf2a98a
ELIN-767418-2017 | EL-506856-2017 | 3/3/2017 3:26:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #DB2__.png Exposed DB2. Possibility for damage and hi fault current resulting in potential for shock or fire. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | DB2__.png | file://x:/photopub/docs/0000000566/90a4445b-2852-4e5d-aeef-26382cc7159e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6db37a38_501c_4792_8974_ae4f522b441a
BPVOP-775544-2017 | 2271405 | 3/15/2017 11:43:04 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_relief_valve.png Upon assessment of Hot Water Boiler with Heating surface area of 12 quare meters, Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_relief_valve.png | file://x:/photopub/docs/0000000571/b8844ada-9862-4155-ab3b-ecf9146f339c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0694670f_3a97_4397_9429_342c0f952e1a
BPVOP-775592-2017 | 2258946 | 3/15/2017 4:23:47 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_relief_valve.png Upon assessment it is determined that machine mounted vertical air receiver (1.8m long and 0.80m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 5 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_valve.png | file://x:/photopub/docs/0000000571/6e59f830-6800-4b32-975a-722fe700f6e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e84fdb9d_5183_4a1f_b1ad_8a69395d5d3b
ELIN-778744-2017 | EL-385989-2016 | 3/20/2017 5:11:41 PM | ASSESS: EL: Service Connection | png | #asFound Energized and exposed 240 volt conductors are damaged and being stepped on by workers | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_exposed_conductors_being_stepped_on_by_workers1.png,Energized_exposed_conductors_being_stepped_on_by_workers2.png,Energized_exposed_conductors_being_stepped_on_by_workers3.png,Energized_exposed_conductors_being_stepped_on_by_workers4.png,Energized_exposed_conductors_being_stepped_on_by_workers5.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the electrical equipment is very unsafe and is an imminent electrical shock or fire hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_exposed_conductors_being_stepped_on_by_workers5.png | file://x:/photopub/docs/0000000577/0c27e64b-5d12-40a2-8f3d-43ba1698e442.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67508dca_cd2e_4a4c_bb74_0048d538e0b2
GAIN-784613-2017 | GA-516160-2017 | 4/5/2017 10:11:32 AM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Vent_.png The as found condition is a single wall vent pipe on a water heater found to be 3 inches from combustible material. The as found hazard is that heat from the vent when installed less than 6 inches can lead to pyrolysis of combustible material, potentially causing a fire. | 3 | Non compliant Type C Vent clearance | Vent_.png | file://x:/photopub/docs/0000000582/6c917cf3-5b7e-44cb-93fd-e449c2ddf5de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__baa15618_3ccc_4631_9f6b_ed53e3c7536f
ELOP-778554-2017 | 4321 | 4/9/2017 10:57:58 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #Water_entry_and_dead_wasps_in_bottom_of_switch.png Service conduit which are not sealed to prevent entry of water or insects can become a hazard to equipment and to the people who operate and maintain the equipment | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Water_entry_and_dead_wasps_in_bottom_of_switch.png | file://x:/photopub/docs/0000000584/1d9ff6e0-02cc-4877-bfdf-534ebe8d332c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de6db763_61fc_472b_8c05_ad9ccf682fc4
GAIN-769960-2017 | GA-508417-2017 | 3/16/2017 1:15:11 PM | ASSESS: GA: Final | png | #asFound | GA134 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | 2 | 2 | #Non_compliant_electrical_supply_to_rooftop_unit_.png Electrical supply not installed according to canadian electrical code. | 2 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | Non_compliant_electrical_supply_to_rooftop_unit_.png | file://x:/photopub/docs/0000000572/16e59f43-205d-4f65-9c94-e8f8e2271b41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f3bfb937_5a2f_4acb_b6ac_fa793c5565e7
AMOP-801709-2017 | 2053153 | 4/28/2017 10:15:04 AM | ASSESS: AM OP: Periodic | png | #asFound | AM014 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | #Broken_bolt_at_rail_joint.png Bolt was broken at a rail joint, joint could become loose during operation and affect coaster travel. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Broken_bolt_at_rail_joint.png | file://x:/photopub/docs/0000000594/c162727b-3f6e-44c6-877a-ed9e1e57dfa9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc547e8c_76e5_471a_8677_38419c9cec94
ELIN-808961-2017 | EL-497601-2017 | 5/3/2017 8:33:09 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #Storage_materials1.png,Storage_materials2.png,Storage_materials3.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Storage_materials1.png | file://x:/photopub/docs/0000000595/3396df69-47fe-4295-b9e4-b96967dac0e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6da0cbc1_cac9_477b_9d3b_5be92af45d1a
ELIN-808961-2017 | EL-497601-2017 | 5/3/2017 8:33:09 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #Storage_materials1.png,Storage_materials2.png,Storage_materials3.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Storage_materials3.png | file://x:/photopub/docs/0000000595/662c153f-40eb-42d0-a294-3e6c637a24fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6da0cbc1_cac9_477b_9d3b_5be92af45d1a
ELIN-808961-2017 | EL-497601-2017 | 5/3/2017 8:33:09 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #Storage_materials1.png,Storage_materials2.png,Storage_materials3.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Storage_materials2.png | file://x:/photopub/docs/0000000595/b2d64295-45ad-42cb-9828-616d7eec8be6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6da0cbc1_cac9_477b_9d3b_5be92af45d1a
ELIN-810377-2017 | EL-413321-2016 | 5/8/2017 2:55:53 PM | ASSESS: EL: Final | png | #asFound Panel board is only held on by 2 of 6 screws required | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | #6.png The main panel board cover is only held in place with 2 of the required 6 screws. In the event of a arc flash in the panel the flames and arcing would not be contained in the panel. This is a fire hazard to anyone in the vicinity. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 6.png | file://x:/photopub/docs/0000000597/8ed43302-8ddf-4284-9e8d-0cb9e24c10ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d451850_25b6_4490_8c2c_1de11c8488f5
ELIN-765485-2017 | EL-346874-2016 | 3/3/2017 12:52:57 PM | ASSESS: EL: Final | png | #asFound | EL292 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Temp_bx.png Temporary power circuit installed exposing live parts that could cause shock. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Temp_bx.png | file://x:/photopub/docs/0000000566/368a1a85-910d-4cd0-ad49-721abc0f4325.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c3ac33f_2c44_4820_baa9_6491bde7ac06
ELIN-784439-2017 | EL-516266-2017 | 3/30/2017 1:07:55 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Receptacle.png Exposed unsecured NMD90 and receptacle not mounted. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Receptacle.png | file://x:/photopub/docs/0000000578/2a93c3d0-619d-43b9-85cc-929b16b2632e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69e62ef6_d752_4e6e_9293_698910d1352c
ELIN-809320-2017 | EL-525073-2017 | 5/5/2017 12:31:27 PM | ASSESS: EL: Service Connection | png | #asFound The service attachment point has been configured to be too close to a second floor window. | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | #Attachment_point.png Service connection for new single-family dwelling. The overhead service has been configured to allow the exposed BC Hydro conductors from the street to terminate too close to a second floor window. Therefore, in the event of a fire a firefighter trying to fight the flames from a ladder or a person trying to get out of the window to escape may experience electrical shock or electrocution from contact with the exposed service conductors. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Attachment_point.png | file://x:/photopub/docs/0000000597/2a904f59-4392-4319-9c22-e2fef81618ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c7861f3_b910_4f8b_9517_1078fc97e5f8
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png | file://x:/photopub/docs/0000000565/18954993-d736-4ccd-98a3-a0883219d462.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_wiring_in_the_storage_building1.png | file://x:/photopub/docs/0000000565/1c03474f-2ee1-4a9c-bea2-8e9689f09d99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_terminals_and_wiring_at_switches5.png | file://x:/photopub/docs/0000000565/d4697698-0c2f-4a57-9ec0-85bf7ba1ba9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_wiring_terminals_and_parts_at_the_service_panel1.png | file://x:/photopub/docs/0000000565/a3eff7bb-8093-4244-94d6-f829249ad2ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_terminals_and_wiring_at_switches3.png | file://x:/photopub/docs/0000000565/114fea93-4d03-4837-8840-544683372213.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_conductors_at_lighting_and_open_cables1.png | file://x:/photopub/docs/0000000565/ca8318b3-9fb2-4bf2-b905-14f3219f46bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_wiring_in_the_storage_building2.png | file://x:/photopub/docs/0000000565/8e7fe8b7-540a-4ac1-841e-ab7e87912ee5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_wiring_at_a_light_fixture.png | file://x:/photopub/docs/0000000565/d5b15da7-3065-492a-a829-cb34fa811453.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png | file://x:/photopub/docs/0000000565/9eed1ae9-9f3b-4e61-ab20-a6cb1febac7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_conductors_at_lighting_and_open_cables2.png | file://x:/photopub/docs/0000000565/a1856b9c-31a0-4771-914f-c3e7c4ff9ce8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_wiring_and_terminals_at_receptacles2.png | file://x:/photopub/docs/0000000565/dcd56f80-7ec9-4003-86b6-aa9cfd6e3b2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_wiring_and_terminals_at_receptacles1.png | file://x:/photopub/docs/0000000565/0421f031-e3b7-41ce-bfac-917934088a10.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_wiring_and_terminals_at_receptacles3.png | file://x:/photopub/docs/0000000565/1b0b0c38-88b4-48c1-90e2-4181ece4a2a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png | file://x:/photopub/docs/0000000565/f0bbeda9-a657-41ae-93f7-09ccdfbd867a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_wiring_at_furnace_.png | file://x:/photopub/docs/0000000565/138acfe6-9a07-4927-a158-cf2ca903bae5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_wiring_and_terminals_at_hot_water_tank1.png | file://x:/photopub/docs/0000000565/a92baa1e-2047-4861-b4a0-3916186f5f14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_terminals_and_wiring_at_switches1.png | file://x:/photopub/docs/0000000565/0ae9d1e0-3b6b-4207-aff5-30f26dbaae62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_wiring_and_terminals_at_hot_water_tank2.png | file://x:/photopub/docs/0000000565/0db2913b-3c5f-408c-b21e-128ca64ad5a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_wiring_terminals_and_parts_at_the_service_panel2.png | file://x:/photopub/docs/0000000565/51d4e871-4b0d-4228-8461-193b8ecb2a18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_terminals_and_wiring_at_switches2.png | file://x:/photopub/docs/0000000565/fcbe83e3-7353-41fe-a8c9-b11e7dcc9f91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_conductors_at_lighting_and_open_cables3.png | file://x:/photopub/docs/0000000565/63a6297b-3d89-44d1-a2bd-4e11ddbe6f7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_wiring_and_terminals_at_hot_water_tank3.png | file://x:/photopub/docs/0000000565/6002615a-b76b-4f04-b715-b33896aed68a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_wiring_at_bathroom_fan.png | file://x:/photopub/docs/0000000565/00e94b0e-51b0-4485-8c5d-872fa4c86ccc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
EDOP-790150-2017 | 3655195 | 4/5/2017 | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | #Car_door_restrictor.png If the car is stopped/stuck outside of the landing, the passengers are not to open the car door and try to exit the elevator. They will be exposed to the open hoistway and may fall resulting in a fatality, the car may also move also exposing them to shearing/pinching hazards. For rider safety the manually opening of the elevator car doors when an elevator car is outside the unlocking zone (landing) is restricted to 4 inches. It was found that the car door restrictor was not adjusted correctly and therefore would allow the door to open fully. There have been many reports of fatalities due to this condition. The picture is for reference only and it's not the actual site photo. | 3 | Defects that are: Not detected by maintenance program Likely to progress | Car_door_restrictor.png | file://x:/photopub/docs/0000000583/2f8bab05-d841-4238-aa61-815367221b74.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af797446_8de1_41e4_886b_1260d6a5816f
ELHE-767824-2017 | HE-507058-2017 | 3/3/2017 10:41:59 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Damaged electrical service | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Hazard_with_main_service.png 100 amp 240 volt single phase service in a state of disrepair | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Hazard_with_main_service.png | file://x:/photopub/docs/0000000565/f2c2547f-44a6-4b08-83f7-40acc14f3e1e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067fec7a_4223_497c_8b06_c19cb8752a6a
ELHE-767824-2017 | HE-507058-2017 | 3/3/2017 10:41:59 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound As found service at property | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Hazard_with_main_service.png 100 amp 240 volt single phase service in a state of disrepair | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Hazard_with_main_service.png | file://x:/photopub/docs/0000000565/0f27e263-5509-4f78-aee1-5bb8ff7da03d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067fec7a_4223_497c_8b06_c19cb8752a6a
ELHE-767824-2017 | HE-507058-2017 | 3/3/2017 10:41:59 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Hazard_with_main_service.png 100 amp 240 volt single phase service in a state of disrepair | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Hazard_with_main_service.png | file://x:/photopub/docs/0000000565/5145c13f-f55d-48f8-8027-f8eada6bad88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067fec7a_4223_497c_8b06_c19cb8752a6a
ELIN-774551-2017 | EL-510868-2017 | 3/17/2017 4:35:32 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Smoke_alarm_wiring_splice_not_contained_in_an_outlet_box1.png,Smoke_alarm_wiring_splice_not_contained_in_an_outlet_box2.png Branch circuit wiring conductors, splices, and connections to smoke alarms or other devices intended for box mounting are required to be made in electrical outlet boxes. This is required to protect the wiring and connections, provided a means for mounting the device, and to contain thermal energy in the event that the wiring, equipment, or connections fail. This existing mobile home installation has new 15A 120V wiring for the connection of a smoke alarm. The wiring connections are not spliced in an outlet box and the smoke alarm is not fastened to an outlet box. Energized wiring and connections for the smoke alarm are open and located above the ceiling. This is a fire hazard if the connections fail or wiring is damaged and not contained in an outlet box. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Smoke_alarm_wiring_splice_not_contained_in_an_outlet_box2.png | file://x:/photopub/docs/0000000573/a173b027-7e34-44cc-98bd-83fd4f87e2bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45ca953e_3dd9_4fca_8f5a_8a93cba17a69
ELIN-774551-2017 | EL-510868-2017 | 3/17/2017 4:35:32 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Smoke_alarm_wiring_splice_not_contained_in_an_outlet_box1.png,Smoke_alarm_wiring_splice_not_contained_in_an_outlet_box2.png Branch circuit wiring conductors, splices, and connections to smoke alarms or other devices intended for box mounting are required to be made in electrical outlet boxes. This is required to protect the wiring and connections, provided a means for mounting the device, and to contain thermal energy in the event that the wiring, equipment, or connections fail. This existing mobile home installation has new 15A 120V wiring for the connection of a smoke alarm. The wiring connections are not spliced in an outlet box and the smoke alarm is not fastened to an outlet box. Energized wiring and connections for the smoke alarm are open and located above the ceiling. This is a fire hazard if the connections fail or wiring is damaged and not contained in an outlet box. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Smoke_alarm_wiring_splice_not_contained_in_an_outlet_box1.png | file://x:/photopub/docs/0000000573/dd2f3be8-77fe-40f2-b00f-4c2cc363ad57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45ca953e_3dd9_4fca_8f5a_8a93cba17a69
ELOP-778543-2017 | 2330 | 4/10/2017 9:08:17 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 3 | #Corrosion_around_equipment1.png,Corrosion_around_equipment2.png,Corrosion_around_equipment3.png Corroded electrical equipment can cause breakdown in insulation integrity creating shock or equipment hazard | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Corrosion_around_equipment2.png | file://x:/photopub/docs/0000000584/65ae8c65-22ca-4bb2-afed-e89016c43bf0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df0fa57f_c36c_4ce4_9451_d30d69114db0
ELOP-778543-2017 | 2330 | 4/10/2017 9:08:17 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 3 | #Corrosion_around_equipment1.png,Corrosion_around_equipment2.png,Corrosion_around_equipment3.png Corroded electrical equipment can cause breakdown in insulation integrity creating shock or equipment hazard | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Corrosion_around_equipment3.png | file://x:/photopub/docs/0000000584/1c4da5a9-4b4a-48da-b88c-bfe03fe3d70a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df0fa57f_c36c_4ce4_9451_d30d69114db0
ELOP-778566-2017 | 4322 | 4/10/2017 9:36:17 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL040 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 3 | 2 | #Small_labelled_ground_light_warnings.png Unmarked or unlabelled electrical equipment presents a hazard to maintenance workers and operators | 3 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | Small_labelled_ground_light_warnings.png | file://x:/photopub/docs/0000000584/15b67386-0974-4e61-aa2e-c8bf8bdb7a8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8df910a_ee10_4f43_956c_a08479a18c31
ELOP-778543-2017 | 2330 | 4/10/2017 9:08:17 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 3 | #Corrosion_around_equipment1.png,Corrosion_around_equipment2.png,Corrosion_around_equipment3.png Corroded electrical equipment can cause breakdown in insulation integrity creating shock or equipment hazard | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Corrosion_around_equipment1.png | file://x:/photopub/docs/0000000584/1b37fa30-ba7f-4558-8a86-7f7bd6c040af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df0fa57f_c36c_4ce4_9451_d30d69114db0
BPVIN-778709-2017 | BPV-506317-2017 | 3/24/2017 10:04:07 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP014 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | 1 | 1 | #Clearances.png | 1 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | Clearances.png | file://x:/photopub/docs/0000000576/3798bace-8b49-4b67-93a9-3e85d91e975c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__535d5803_716b_4efd_a59d_eecafebd8715
AMOP-788045-2017 | 2053219 | 4/3/2017 1:12:21 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Blocking_not_ollowing_best_practices1.png,Blocking_not_ollowing_best_practices2.png,Blocking_not_ollowing_best_practices3.png Blocking installed for the rides foundation not following industry best practices, If load was to shift, the device could fall off its foundation. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Blocking_not_ollowing_best_practices3.png | file://x:/photopub/docs/0000000580/56ed60f0-1507-4067-b96e-5e1be09e1219.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85010525_c079_4ead_b7b3_912ddcac8a2e
AMOP-788045-2017 | 2053219 | 4/3/2017 1:12:21 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Blocking_not_ollowing_best_practices1.png,Blocking_not_ollowing_best_practices2.png,Blocking_not_ollowing_best_practices3.png Blocking installed for the rides foundation not following industry best practices, If load was to shift, the device could fall off its foundation. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Blocking_not_ollowing_best_practices2.png | file://x:/photopub/docs/0000000580/efe182d1-687f-42cc-b3f1-e8f09dedc716.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85010525_c079_4ead_b7b3_912ddcac8a2e
AMOP-788045-2017 | 2053219 | 4/3/2017 1:12:21 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Blocking_not_ollowing_best_practices1.png,Blocking_not_ollowing_best_practices2.png,Blocking_not_ollowing_best_practices3.png Blocking installed for the rides foundation not following industry best practices, If load was to shift, the device could fall off its foundation. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Blocking_not_ollowing_best_practices1.png | file://x:/photopub/docs/0000000580/a87baa58-599c-43de-9a61-c5f02356d5b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85010525_c079_4ead_b7b3_912ddcac8a2e
GAIN-792634-2017 | GA-516359-2017 | 4/24/2017 12:24:51 PM | ASSESS: GA: Final | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | #Cloke2.png Mechanical intake installed with les than the minimum required clearance to meter regulator relief. Should regulator fail,high pressure gas could be released and drawn into appliance intake. Risk of appliance being over fired should appliance be in operation during failure event.This could result in a fire or the production of carbon monoxide. | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Cloke2.png | file://x:/photopub/docs/0000000590/b8f8b1c3-f865-4868-8d5c-49a08b4607ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7dfb0fd3_71eb_43e7_b839_8c9403e65327
GAIN-783110-2017 | GA-471953-2016 | 3/30/2017 2:31:14 PM | ASSESS: GA: Final | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | #Techie_1.png,Techie_2.png The pressure regulator could vent. This would vent into the elementary school | 3 | insufficient mechanical air intake clearance to gas regulator relief | Techie_1.png | file://x:/photopub/docs/0000000579/e90dc642-b321-4af9-9c9f-531d88da2a99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f109b8d_04e3_4cdd_ba1e_591f53a58ef3
GAIN-783110-2017 | GA-471953-2016 | 3/30/2017 2:31:14 PM | ASSESS: GA: Final | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | #Techie_1.png,Techie_2.png The pressure regulator could vent. This would vent into the elementary school | 3 | insufficient mechanical air intake clearance to gas regulator relief | Techie_2.png | file://x:/photopub/docs/0000000579/e405fa62-d191-487d-bde9-17646aabf5c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f109b8d_04e3_4cdd_ba1e_591f53a58ef3
BPVOP-796389-2017 | BPV-152473-2014 | 4/6/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #6.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 6.png | file://x:/photopub/docs/0000000587/2a176d43-cb0a-4918-97f7-7500bf1921f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2f8725c_4301_49a1_8c4f_7388ed9e57fb
BPVOP-796391-2017 | BPV-152717-2014 | 4/6/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #12.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 12.png | file://x:/photopub/docs/0000000587/cbd38514-ee66-41f0-bc2c-9d29c182949a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a97e64fa_9f5b_4282_b007_fb91d5784dfc
BPVOP-796390-2017 | BPV-152474-2014 | 4/6/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #9.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 9.png | file://x:/photopub/docs/0000000587/c1044cd1-32f8-44e3-9db6-d1594c311112.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0715c017_b335_46d4_a63a_ce08f121a6df
BPVOP-796392-2017 | BPV-152718-2014 | 4/6/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #15.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 15.png | file://x:/photopub/docs/0000000587/732cf046-8972-4cec-a58c-d04533ff7b17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7bede54_bb75_4f68_98ea_4f9422839836
ELIN-810570-2017 | 4817858 | 5/9/2017 12:07:00 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #A1.png,A2.png Armoured cable used with non metallic boxes. This is a shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | A1.png | file://x:/photopub/docs/0000000598/82308539-954c-4832-af2e-b56fbc65c852.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6bd2a6e4_b886_401f_ab4c_326397cb97d6
ELIN-810570-2017 | 4817858 | 5/9/2017 12:07:00 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #A1.png,A2.png Armoured cable used with non metallic boxes. This is a shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | A2.png | file://x:/photopub/docs/0000000598/836f7768-80dd-4f1a-933f-fd2b32cf5baf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6bd2a6e4_b886_401f_ab4c_326397cb97d6
ELHE-766429-2017 | HE-506363-2017 | 3/1/2017 4:48:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_wiring_and_terminals_at_hot_water_tank1.png,Open_energized_wiring_and_terminals_at_hot_water_tank2.png,Open_energized_wiring_and_terminals_at_hot_water_tank3.png,Open_energized_wiring_in_the_storage_building1.png,Open_energized_wiring_in_the_storage_building2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed1.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed2.png,exposed_energized_terminals_on_a_receptacle_beside_a_childs_bed3.png,Open_energized_terminals_and_wiring_at_switches1.png,Open_energized_terminals_and_wiring_at_switches2.png,Open_energized_terminals_and_wiring_at_switches3.png,Open_energized_terminals_and_wiring_at_switches4.png,Open_energized_terminals_and_wiring_at_switches5.png,Open_energized_wiring_at_bathroom_fan.png,Open_energized_wiring_and_terminals_at_receptacles1.png,Open_energized_wiring_and_terminals_at_receptacles2.png,Open_energized_wiring_and_terminals_at_receptacles3.png,Open_energized_conductors_at_lighting_and_open_cables1.png,Ope | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_terminals_and_wiring_at_switches4.png | file://x:/photopub/docs/0000000565/143a33eb-c891-4b08-9fb4-79f6db59c3fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c92d0f53_041b_4d78_b27f_42dc1a697530
ELOP-787764-2017 | 4560 | 4/24/2017 9:44:30 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Irrigation_1.png,Irrigation_2.png An extension cord has been permanently installed from a 15 amp 120 volt receptacle to feed an irrigation control box which has power cord, the connection to the cord is laying loose on the ground. This poses a shock hazard to persons and potential damage to the cord, receptacle and irrigation equipment has a proper connection and power supply has not been provided. | 4 | Conductors, Misuse of flexible cords. | Irrigation_1.png | file://x:/photopub/docs/0000000590/e8fdd9d6-fcaa-4aae-b801-186301def35b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13839323_030c_408c_b084_b87c9b358903
ELOP-787764-2017 | 4560 | 4/24/2017 9:44:30 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Irrigation_1.png,Irrigation_2.png An extension cord has been permanently installed from a 15 amp 120 volt receptacle to feed an irrigation control box which has power cord, the connection to the cord is laying loose on the ground. This poses a shock hazard to persons and potential damage to the cord, receptacle and irrigation equipment has a proper connection and power supply has not been provided. | 4 | Conductors, Misuse of flexible cords. | Irrigation_2.png | file://x:/photopub/docs/0000000590/fe562723-9133-489b-80b1-5b5955453114.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13839323_030c_408c_b084_b87c9b358903
ELIN-796828-2017 | EL-522206-2017 | 4/19/2017 10:00:28 AM | ASSESS: EL: Service Connection | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | #4_0awg_RW90_used1.png,4_0awg_RW90_used2.png In an existing residential dwelling space, a new 200amp 120/240volt 1 phase service upgrade was performed while adding an additional 2nd dwelling space and using undersized cabling and conduit. This can lead to a "Thermal Effect" condition. Pic attached | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4_0awg_RW90_used1.png | file://x:/photopub/docs/0000000588/55e3f140-3657-4d06-afc4-4ad9ea86d429.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9109892_1521_45f2_b6ae_eb3fcae27dff
ELIN-796828-2017 | EL-522206-2017 | 4/19/2017 10:00:28 AM | ASSESS: EL: Service Connection | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | #4_0awg_RW90_used1.png,4_0awg_RW90_used2.png In an existing residential dwelling space, a new 200amp 120/240volt 1 phase service upgrade was performed while adding an additional 2nd dwelling space and using undersized cabling and conduit. This can lead to a "Thermal Effect" condition. Pic attached | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4_0awg_RW90_used2.png | file://x:/photopub/docs/0000000588/738e991f-940e-4bfb-a6d4-6fc6acb2738e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9109892_1521_45f2_b6ae_eb3fcae27dff
BPVIN-812585-2017 | BPV-459919-2016 | 5/9/2017 11:43:02 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 | #Safety_relief_valve.png | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Safety_relief_valve.png | file://x:/photopub/docs/0000000598/11da7ac1-44b7-40c8-ae33-dad52f01047e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30011916_68bd_46e8_82e5_98f7b2f76554
ELIN-768237-2017 | EL-353299-2016 | 3/6/2017 12:53:21 PM | ASSESS: EL: Service Connection | png | #asFound Plate electrode laying on the earth under meter base. | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Plate_electrode.png Service connection for new single family dwelling. The grounding electrode was not buried in the earth. Therefore there would be no system ground to carry faults away from the dwelling. Shock hazard and may prevent overcurrent devices from operating in a fault condition. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Plate_electrode.png | file://x:/photopub/docs/0000000566/c5d32bb6-1c2b-4671-a20c-12f9b105cce6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df352c1e_143e_4fff_aa7a_1b695194e831
ELOP-797285-2017 | 7091 | 4/25/2017 3:02:17 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Cord.png Flexible cord misused | 4 | Conductors, Misuse of flexible cords. | Cord.png | file://x:/photopub/docs/0000000591/4ca5d5a4-6755-430b-8da1-41a129d1c5ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8EAD91A7_DA7C_4E61_BD8C_138F777C8AB9
ELOP-797102-2017 | 7095 | 4/25/2017 3:07:21 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL288 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Missing_cover_.png Missing cover on energized service conductors in area accessible to persons | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Missing_cover_.png | file://x:/photopub/docs/0000000591/6fcbec29-8416-44e3-88cb-290aee5461b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4E2D59EF_3DF9_4385_BCDC_56562F727DB9
ELIN-768760-2017 | EL-506849-2017 | 3/7/2017 8:19:13 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #122111.png,122112.png,122113.png Breakers found to be installed within main distribution panel were not of the type approved for installation within that manufactures equipment as they were of a different brand and model. | 3 | General Equipment is not approved for the specific use | 122111.png | file://x:/photopub/docs/0000000567/61417e7a-0ef8-4f64-82b4-273bd792275a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58e3eb42_3701_4e1b_ab4a_8ca4a307410a
ELIN-768760-2017 | EL-506849-2017 | 3/7/2017 8:19:13 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #122111.png,122112.png,122113.png Breakers found to be installed within main distribution panel were not of the type approved for installation within that manufactures equipment as they were of a different brand and model. | 3 | General Equipment is not approved for the specific use | 122112.png | file://x:/photopub/docs/0000000567/caffd1a4-28eb-48a7-a954-b61d8f3c53a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58e3eb42_3701_4e1b_ab4a_8ca4a307410a
ELIN-768760-2017 | EL-506849-2017 | 3/7/2017 8:19:13 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #122111.png,122112.png,122113.png Breakers found to be installed within main distribution panel were not of the type approved for installation within that manufactures equipment as they were of a different brand and model. | 3 | General Equipment is not approved for the specific use | 122113.png | file://x:/photopub/docs/0000000567/eed688ef-3fc0-4a25-9b02-ad5bb7d55807.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58e3eb42_3701_4e1b_ab4a_8ca4a307410a
ELIN-769521-2017 | EL-458783-2016 | 3/6/2017 2:46:01 PM | ASSESS: EL: Service Connection | JPG | #asFound | EL296 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #IMG_0005.JPG Temporary construction service in disrepair | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | IMG_0005.JPG | file://x:/photopub/docs/0000000566/0d9dcba3-04d4-4672-acef-3b16e386826a.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b77c0331_b4fa_42b3_b804_8dc54229d8cb
ELIN-769521-2017 | EL-458783-2016 | 3/6/2017 2:46:01 PM | ASSESS: EL: Service Connection | JPG | #asFound | EL296 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #IMG_0005.JPG Temporary construction service in disrepair | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | IMG_0005.JPG | file://x:/photopub/docs/0000000566/fa6d35b9-7168-47cb-bd58-22fce17b3242.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b77c0331_b4fa_42b3_b804_8dc54229d8cb
ELIN-769521-2017 | EL-458783-2016 | 3/6/2017 2:46:01 PM | ASSESS: EL: Service Connection | JPG | #asFound Temp service is disrepair | EL296 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #IMG_0005.JPG Temporary construction service in disrepair | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | IMG_0005.JPG | file://x:/photopub/docs/0000000566/4575a144-dd2a-4703-86bb-fc8a11f52ed0.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b77c0331_b4fa_42b3_b804_8dc54229d8cb
ELIN-803688-2017 | EL-455492-2016 | 5/1/2017 9:07:29 AM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Live_NMD1.png,Live_NMD2.png An energized 120 volt 15 amp 14/2 NMD wire has not been terminated in a junction box, the wiring and connections are accessible. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Live_NMD2.png | file://x:/photopub/docs/0000000593/46b8fda3-e6ad-4b0b-a5d8-c09fdd00bf63.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b549ef9b_d22a_464e_b736_1b6fb2acd1b8
ELIN-803688-2017 | EL-455492-2016 | 5/1/2017 9:07:29 AM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Live_NMD1.png,Live_NMD2.png An energized 120 volt 15 amp 14/2 NMD wire has not been terminated in a junction box, the wiring and connections are accessible. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Live_NMD1.png | file://x:/photopub/docs/0000000593/61bfcdac-9e43-4144-84b6-b135d1c02d6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b549ef9b_d22a_464e_b736_1b6fb2acd1b8
BPVIN-751895-2017 | BPV-352896-2016 | 3/20/2017 10:04:07 PM | ASSESS: BPV IN: Installation REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 3 | #Refrigeration_system_without_PRV_on_compressor_discharge.png Upon assessment it is determined that there is no pressure relief valve on high pressure side of refrigeration system with 130lbs of refrigerant and 157kW prime mover rating. In the event of fire, pressure boundary of system may fail due to overpressure. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | Refrigeration_system_without_PRV_on_compressor_discharge.png | file://x:/photopub/docs/0000000576/56ff7bdc-9d51-47d2-bb4d-5bc280c1b8e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee58de53_0c3a_4362_8c16_27a0ac30f0f7
ELOP-728927-2016 | 3025114 | 3/21/2017 12:10:43 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_starter_cabinets_switches_control_devices_and_splices1.png,Open_starter_cabinets_switches_control_devices_and_splices2.png,Open_starter_cabinets_switches_control_devices_and_splices3.png,Open_starter_cabinets_switches_control_devices_and_splices4.png,Open_starter_cabinets_switches_control_devices_and_splices5.png,Open_starter_cabinets_switches_control_devices_and_splices6.png,Open_starter_cabinets_switches_control_devices_and_splices7.png,Open_starter_cabinets_switches_control_devices_and_splices8.png,Open_starter_cabinets_switches_control_devices_and_splices9.png,Open_starter_cabinets_switches_control_devices_and_splices10.png,Open_starter_cabinets_switches_control_devices_and_splices11.png,Open_starter_cabinets_switches_control_devices_and_splices12.png,Open_starter_cabinets_switches_control_devices_and_splices13.png,Open_starter_cabinets_switches_control_devices_and_splices14.png,Open_starter_cabinets_switches_control_devices_and_splices15.png,Open_starter_cabinets_switches_control_devices_and_splice | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_starter_cabinets_switches_control_devices_and_splices2.png | file://x:/photopub/docs/0000000576/0ac8608a-af57-45fa-86fc-0f59f7489189.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dde0ee71_85ea_4d62_99e1_e1c181062059
ELOP-728927-2016 | 3025114 | 3/21/2017 12:10:43 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_starter_cabinets_switches_control_devices_and_splices1.png,Open_starter_cabinets_switches_control_devices_and_splices2.png,Open_starter_cabinets_switches_control_devices_and_splices3.png,Open_starter_cabinets_switches_control_devices_and_splices4.png,Open_starter_cabinets_switches_control_devices_and_splices5.png,Open_starter_cabinets_switches_control_devices_and_splices6.png,Open_starter_cabinets_switches_control_devices_and_splices7.png,Open_starter_cabinets_switches_control_devices_and_splices8.png,Open_starter_cabinets_switches_control_devices_and_splices9.png,Open_starter_cabinets_switches_control_devices_and_splices10.png,Open_starter_cabinets_switches_control_devices_and_splices11.png,Open_starter_cabinets_switches_control_devices_and_splices12.png,Open_starter_cabinets_switches_control_devices_and_splices13.png,Open_starter_cabinets_switches_control_devices_and_splices14.png,Open_starter_cabinets_switches_control_devices_and_splices15.png,Open_starter_cabinets_switches_control_devices_and_splice | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_starter_cabinets_switches_control_devices_and_splices14.png | file://x:/photopub/docs/0000000576/3eb32c12-b406-4f41-b82f-eaacf85c4973.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dde0ee71_85ea_4d62_99e1_e1c181062059
ELOP-728928-2016 | 5080114 | 3/21/2017 8:50:08 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL190 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 4 | #Deteriorated__transformer_platform_crossarms__and_poles1.png,Deteriorated__transformer_platform_crossarms__and_poles2.png,Deteriorated__transformer_platform_crossarms__and_poles3.png,Deteriorated__transformer_platform_crossarms__and_poles4.png,Deteriorated__transformer_platform_crossarms__and_poles5.png,Deteriorated__transformer_platform_crossarms__and_poles6.png,Deteriorated__transformer_platform_crossarms__and_poles7.png Poles and structures used to support transformers, conductors, and other electrical equipment rate required to be structurally solid to safely support the equipment that they are intended to support. This is required to prevent the energized equipment and components from falling from the structure or contacting other parts that they are not intended to contact. This installation at a commercial food processing plant has 3 x 250 KVA, 25KV to 480V transformers, and conductors that are supported by a pole, steel and timber structure. The wooden components that supported the conductors and the | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | Deteriorated__transformer_platform_crossarms__and_poles1.png | file://x:/photopub/docs/0000000576/57bc1a1a-ae5e-40e4-8b58-d4ada93768a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ae690d8_2d08_4287_8a79_0461dcb620ca
ELOP-728928-2016 | 5080114 | 3/21/2017 8:50:08 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL190 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 4 | #Deteriorated__transformer_platform_crossarms__and_poles1.png,Deteriorated__transformer_platform_crossarms__and_poles2.png,Deteriorated__transformer_platform_crossarms__and_poles3.png,Deteriorated__transformer_platform_crossarms__and_poles4.png,Deteriorated__transformer_platform_crossarms__and_poles5.png,Deteriorated__transformer_platform_crossarms__and_poles6.png,Deteriorated__transformer_platform_crossarms__and_poles7.png Poles and structures used to support transformers, conductors, and other electrical equipment rate required to be structurally solid to safely support the equipment that they are intended to support. This is required to prevent the energized equipment and components from falling from the structure or contacting other parts that they are not intended to contact. This installation at a commercial food processing plant has 3 x 250 KVA, 25KV to 480V transformers, and conductors that are supported by a pole, steel and timber structure. The wooden components that supported the conductors and the | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | Deteriorated__transformer_platform_crossarms__and_poles6.png | file://x:/photopub/docs/0000000576/1c958c05-d301-497b-acb0-e13cc9989578.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ae690d8_2d08_4287_8a79_0461dcb620ca
ELOP-728928-2016 | 5080114 | 3/21/2017 8:50:08 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL190 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 4 | #Deteriorated__transformer_platform_crossarms__and_poles1.png,Deteriorated__transformer_platform_crossarms__and_poles2.png,Deteriorated__transformer_platform_crossarms__and_poles3.png,Deteriorated__transformer_platform_crossarms__and_poles4.png,Deteriorated__transformer_platform_crossarms__and_poles5.png,Deteriorated__transformer_platform_crossarms__and_poles6.png,Deteriorated__transformer_platform_crossarms__and_poles7.png Poles and structures used to support transformers, conductors, and other electrical equipment rate required to be structurally solid to safely support the equipment that they are intended to support. This is required to prevent the energized equipment and components from falling from the structure or contacting other parts that they are not intended to contact. This installation at a commercial food processing plant has 3 x 250 KVA, 25KV to 480V transformers, and conductors that are supported by a pole, steel and timber structure. The wooden components that supported the conductors and the | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | Deteriorated__transformer_platform_crossarms__and_poles3.png | file://x:/photopub/docs/0000000576/37081ae3-7c23-43c3-9ac9-b995f4458885.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ae690d8_2d08_4287_8a79_0461dcb620ca
ELOP-728927-2016 | 3025114 | 3/21/2017 12:10:43 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_starter_cabinets_switches_control_devices_and_splices1.png,Open_starter_cabinets_switches_control_devices_and_splices2.png,Open_starter_cabinets_switches_control_devices_and_splices3.png,Open_starter_cabinets_switches_control_devices_and_splices4.png,Open_starter_cabinets_switches_control_devices_and_splices5.png,Open_starter_cabinets_switches_control_devices_and_splices6.png,Open_starter_cabinets_switches_control_devices_and_splices7.png,Open_starter_cabinets_switches_control_devices_and_splices8.png,Open_starter_cabinets_switches_control_devices_and_splices9.png,Open_starter_cabinets_switches_control_devices_and_splices10.png,Open_starter_cabinets_switches_control_devices_and_splices11.png,Open_starter_cabinets_switches_control_devices_and_splices12.png,Open_starter_cabinets_switches_control_devices_and_splices13.png,Open_starter_cabinets_switches_control_devices_and_splices14.png,Open_starter_cabinets_switches_control_devices_and_splices15.png,Open_starter_cabinets_switches_control_devices_and_splice | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_starter_cabinets_switches_control_devices_and_splices16.png | file://x:/photopub/docs/0000000576/cb10401a-3f03-49f5-a389-93d3f84ca5a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dde0ee71_85ea_4d62_99e1_e1c181062059
ELOP-728927-2016 | 3025114 | 3/21/2017 12:10:43 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_starter_cabinets_switches_control_devices_and_splices1.png,Open_starter_cabinets_switches_control_devices_and_splices2.png,Open_starter_cabinets_switches_control_devices_and_splices3.png,Open_starter_cabinets_switches_control_devices_and_splices4.png,Open_starter_cabinets_switches_control_devices_and_splices5.png,Open_starter_cabinets_switches_control_devices_and_splices6.png,Open_starter_cabinets_switches_control_devices_and_splices7.png,Open_starter_cabinets_switches_control_devices_and_splices8.png,Open_starter_cabinets_switches_control_devices_and_splices9.png,Open_starter_cabinets_switches_control_devices_and_splices10.png,Open_starter_cabinets_switches_control_devices_and_splices11.png,Open_starter_cabinets_switches_control_devices_and_splices12.png,Open_starter_cabinets_switches_control_devices_and_splices13.png,Open_starter_cabinets_switches_control_devices_and_splices14.png,Open_starter_cabinets_switches_control_devices_and_splices15.png,Open_starter_cabinets_switches_control_devices_and_splice | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_starter_cabinets_switches_control_devices_and_splices3.png | file://x:/photopub/docs/0000000576/539c8cce-3079-4531-b374-bad4c9239af0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dde0ee71_85ea_4d62_99e1_e1c181062059
ELOP-728928-2016 | 5080114 | 3/21/2017 8:50:08 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL190 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 4 | #Deteriorated__transformer_platform_crossarms__and_poles1.png,Deteriorated__transformer_platform_crossarms__and_poles2.png,Deteriorated__transformer_platform_crossarms__and_poles3.png,Deteriorated__transformer_platform_crossarms__and_poles4.png,Deteriorated__transformer_platform_crossarms__and_poles5.png,Deteriorated__transformer_platform_crossarms__and_poles6.png,Deteriorated__transformer_platform_crossarms__and_poles7.png Poles and structures used to support transformers, conductors, and other electrical equipment rate required to be structurally solid to safely support the equipment that they are intended to support. This is required to prevent the energized equipment and components from falling from the structure or contacting other parts that they are not intended to contact. This installation at a commercial food processing plant has 3 x 250 KVA, 25KV to 480V transformers, and conductors that are supported by a pole, steel and timber structure. The wooden components that supported the conductors and the | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | Deteriorated__transformer_platform_crossarms__and_poles2.png | file://x:/photopub/docs/0000000576/cc8d3f74-85f4-4e7b-86e9-2c1fa73ca40a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ae690d8_2d08_4287_8a79_0461dcb620ca
ELOP-728927-2016 | 3025114 | 3/21/2017 12:10:43 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_starter_cabinets_switches_control_devices_and_splices1.png,Open_starter_cabinets_switches_control_devices_and_splices2.png,Open_starter_cabinets_switches_control_devices_and_splices3.png,Open_starter_cabinets_switches_control_devices_and_splices4.png,Open_starter_cabinets_switches_control_devices_and_splices5.png,Open_starter_cabinets_switches_control_devices_and_splices6.png,Open_starter_cabinets_switches_control_devices_and_splices7.png,Open_starter_cabinets_switches_control_devices_and_splices8.png,Open_starter_cabinets_switches_control_devices_and_splices9.png,Open_starter_cabinets_switches_control_devices_and_splices10.png,Open_starter_cabinets_switches_control_devices_and_splices11.png,Open_starter_cabinets_switches_control_devices_and_splices12.png,Open_starter_cabinets_switches_control_devices_and_splices13.png,Open_starter_cabinets_switches_control_devices_and_splices14.png,Open_starter_cabinets_switches_control_devices_and_splices15.png,Open_starter_cabinets_switches_control_devices_and_splice | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_starter_cabinets_switches_control_devices_and_splices12.png | file://x:/photopub/docs/0000000576/56d44c52-bf21-4c72-bcfc-140d3c6329b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dde0ee71_85ea_4d62_99e1_e1c181062059
BPVOP-650265-2016 | 2293911 | 3/6/2017 1:17:34 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 | #scale.png | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | scale.png | file://x:/photopub/docs/0000000567/a9184f36-70dd-4999-97a7-a9cf1c815c05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6b0d58c_dcbb_4dc8_86b6_962a8bfd929d
ELIN-804940-2017 | EL-462050-2016 | 5/1/2017 2:07:17 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 3 | #7.png A conductor in the living room is not in a box. This is a potential fire hazard if the conductor becomes energized in the wall. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 7.png | file://x:/photopub/docs/0000000593/4900ae31-c849-45d1-ac27-f7b662c4ae03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e677678_2b98_4b44_ab03_a77741575d0c
GAIN-782065-2017 | GA-444605-2016 | 4/4/2017 9:43:18 AM | ASSESS: GA: Rough-In | png | #asFound | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 4 | #Regulator_.png The As found condition is a the relief vent line on a regulator is installed with the termination inside a wall. The as found hazard is in the event of relief failure the system will vent inside the building envelope | 5 | Relief style regulator/device allowed to vent within building/confined space | Regulator_.png | file://x:/photopub/docs/0000000581/151a63e5-42f9-49c8-8483-6805efed6b72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a9fc6c4_5e37_4cb9_9d64_2ea074673b4b
ELOP-728927-2016 | 3025114 | 3/21/2017 12:10:43 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_starter_cabinets_switches_control_devices_and_splices1.png,Open_starter_cabinets_switches_control_devices_and_splices2.png,Open_starter_cabinets_switches_control_devices_and_splices3.png,Open_starter_cabinets_switches_control_devices_and_splices4.png,Open_starter_cabinets_switches_control_devices_and_splices5.png,Open_starter_cabinets_switches_control_devices_and_splices6.png,Open_starter_cabinets_switches_control_devices_and_splices7.png,Open_starter_cabinets_switches_control_devices_and_splices8.png,Open_starter_cabinets_switches_control_devices_and_splices9.png,Open_starter_cabinets_switches_control_devices_and_splices10.png,Open_starter_cabinets_switches_control_devices_and_splices11.png,Open_starter_cabinets_switches_control_devices_and_splices12.png,Open_starter_cabinets_switches_control_devices_and_splices13.png,Open_starter_cabinets_switches_control_devices_and_splices14.png,Open_starter_cabinets_switches_control_devices_and_splices15.png,Open_starter_cabinets_switches_control_devices_and_splice | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_starter_cabinets_switches_control_devices_and_splices1.png | file://x:/photopub/docs/0000000576/06d64450-ab74-4531-83fb-62c41def2ad3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dde0ee71_85ea_4d62_99e1_e1c181062059
ELOP-728927-2016 | 3025114 | 3/21/2017 12:10:43 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_starter_cabinets_switches_control_devices_and_splices1.png,Open_starter_cabinets_switches_control_devices_and_splices2.png,Open_starter_cabinets_switches_control_devices_and_splices3.png,Open_starter_cabinets_switches_control_devices_and_splices4.png,Open_starter_cabinets_switches_control_devices_and_splices5.png,Open_starter_cabinets_switches_control_devices_and_splices6.png,Open_starter_cabinets_switches_control_devices_and_splices7.png,Open_starter_cabinets_switches_control_devices_and_splices8.png,Open_starter_cabinets_switches_control_devices_and_splices9.png,Open_starter_cabinets_switches_control_devices_and_splices10.png,Open_starter_cabinets_switches_control_devices_and_splices11.png,Open_starter_cabinets_switches_control_devices_and_splices12.png,Open_starter_cabinets_switches_control_devices_and_splices13.png,Open_starter_cabinets_switches_control_devices_and_splices14.png,Open_starter_cabinets_switches_control_devices_and_splices15.png,Open_starter_cabinets_switches_control_devices_and_splice | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_starter_cabinets_switches_control_devices_and_splices10.png | file://x:/photopub/docs/0000000576/7b95ea89-a00b-4b9d-8f73-818da187d4c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dde0ee71_85ea_4d62_99e1_e1c181062059
ELOP-728928-2016 | 5080114 | 3/21/2017 8:50:08 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL190 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 4 | #Deteriorated__transformer_platform_crossarms__and_poles1.png,Deteriorated__transformer_platform_crossarms__and_poles2.png,Deteriorated__transformer_platform_crossarms__and_poles3.png,Deteriorated__transformer_platform_crossarms__and_poles4.png,Deteriorated__transformer_platform_crossarms__and_poles5.png,Deteriorated__transformer_platform_crossarms__and_poles6.png,Deteriorated__transformer_platform_crossarms__and_poles7.png Poles and structures used to support transformers, conductors, and other electrical equipment rate required to be structurally solid to safely support the equipment that they are intended to support. This is required to prevent the energized equipment and components from falling from the structure or contacting other parts that they are not intended to contact. This installation at a commercial food processing plant has 3 x 250 KVA, 25KV to 480V transformers, and conductors that are supported by a pole, steel and timber structure. The wooden components that supported the conductors and the | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | Deteriorated__transformer_platform_crossarms__and_poles5.png | file://x:/photopub/docs/0000000576/cba8bd3a-fa6d-43e6-926d-2f4cdfbde2f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ae690d8_2d08_4287_8a79_0461dcb620ca
ELOP-728927-2016 | 3025114 | 3/21/2017 12:10:43 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_starter_cabinets_switches_control_devices_and_splices1.png,Open_starter_cabinets_switches_control_devices_and_splices2.png,Open_starter_cabinets_switches_control_devices_and_splices3.png,Open_starter_cabinets_switches_control_devices_and_splices4.png,Open_starter_cabinets_switches_control_devices_and_splices5.png,Open_starter_cabinets_switches_control_devices_and_splices6.png,Open_starter_cabinets_switches_control_devices_and_splices7.png,Open_starter_cabinets_switches_control_devices_and_splices8.png,Open_starter_cabinets_switches_control_devices_and_splices9.png,Open_starter_cabinets_switches_control_devices_and_splices10.png,Open_starter_cabinets_switches_control_devices_and_splices11.png,Open_starter_cabinets_switches_control_devices_and_splices12.png,Open_starter_cabinets_switches_control_devices_and_splices13.png,Open_starter_cabinets_switches_control_devices_and_splices14.png,Open_starter_cabinets_switches_control_devices_and_splices15.png,Open_starter_cabinets_switches_control_devices_and_splice | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_starter_cabinets_switches_control_devices_and_splices4.png | file://x:/photopub/docs/0000000576/5ff29581-f64b-4827-928c-a230c9b08a0e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dde0ee71_85ea_4d62_99e1_e1c181062059
ELOP-728927-2016 | 3025114 | 3/21/2017 12:10:43 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_starter_cabinets_switches_control_devices_and_splices1.png,Open_starter_cabinets_switches_control_devices_and_splices2.png,Open_starter_cabinets_switches_control_devices_and_splices3.png,Open_starter_cabinets_switches_control_devices_and_splices4.png,Open_starter_cabinets_switches_control_devices_and_splices5.png,Open_starter_cabinets_switches_control_devices_and_splices6.png,Open_starter_cabinets_switches_control_devices_and_splices7.png,Open_starter_cabinets_switches_control_devices_and_splices8.png,Open_starter_cabinets_switches_control_devices_and_splices9.png,Open_starter_cabinets_switches_control_devices_and_splices10.png,Open_starter_cabinets_switches_control_devices_and_splices11.png,Open_starter_cabinets_switches_control_devices_and_splices12.png,Open_starter_cabinets_switches_control_devices_and_splices13.png,Open_starter_cabinets_switches_control_devices_and_splices14.png,Open_starter_cabinets_switches_control_devices_and_splices15.png,Open_starter_cabinets_switches_control_devices_and_splice | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_starter_cabinets_switches_control_devices_and_splices17.png | file://x:/photopub/docs/0000000576/3be0576c-9b7c-4a17-967a-3f4bd27798ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dde0ee71_85ea_4d62_99e1_e1c181062059
ELOP-728927-2016 | 3025114 | 3/21/2017 12:10:43 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_starter_cabinets_switches_control_devices_and_splices1.png,Open_starter_cabinets_switches_control_devices_and_splices2.png,Open_starter_cabinets_switches_control_devices_and_splices3.png,Open_starter_cabinets_switches_control_devices_and_splices4.png,Open_starter_cabinets_switches_control_devices_and_splices5.png,Open_starter_cabinets_switches_control_devices_and_splices6.png,Open_starter_cabinets_switches_control_devices_and_splices7.png,Open_starter_cabinets_switches_control_devices_and_splices8.png,Open_starter_cabinets_switches_control_devices_and_splices9.png,Open_starter_cabinets_switches_control_devices_and_splices10.png,Open_starter_cabinets_switches_control_devices_and_splices11.png,Open_starter_cabinets_switches_control_devices_and_splices12.png,Open_starter_cabinets_switches_control_devices_and_splices13.png,Open_starter_cabinets_switches_control_devices_and_splices14.png,Open_starter_cabinets_switches_control_devices_and_splices15.png,Open_starter_cabinets_switches_control_devices_and_splice | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_starter_cabinets_switches_control_devices_and_splices9.png | file://x:/photopub/docs/0000000576/dfb9c5bf-b132-41f1-b1a9-ea3c5a418725.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dde0ee71_85ea_4d62_99e1_e1c181062059
ELOP-728927-2016 | 3025114 | 3/21/2017 12:10:43 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_starter_cabinets_switches_control_devices_and_splices1.png,Open_starter_cabinets_switches_control_devices_and_splices2.png,Open_starter_cabinets_switches_control_devices_and_splices3.png,Open_starter_cabinets_switches_control_devices_and_splices4.png,Open_starter_cabinets_switches_control_devices_and_splices5.png,Open_starter_cabinets_switches_control_devices_and_splices6.png,Open_starter_cabinets_switches_control_devices_and_splices7.png,Open_starter_cabinets_switches_control_devices_and_splices8.png,Open_starter_cabinets_switches_control_devices_and_splices9.png,Open_starter_cabinets_switches_control_devices_and_splices10.png,Open_starter_cabinets_switches_control_devices_and_splices11.png,Open_starter_cabinets_switches_control_devices_and_splices12.png,Open_starter_cabinets_switches_control_devices_and_splices13.png,Open_starter_cabinets_switches_control_devices_and_splices14.png,Open_starter_cabinets_switches_control_devices_and_splices15.png,Open_starter_cabinets_switches_control_devices_and_splice | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_starter_cabinets_switches_control_devices_and_splices13.png | file://x:/photopub/docs/0000000576/e6de6e43-23e6-4fb8-b60d-3aaad43e02c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dde0ee71_85ea_4d62_99e1_e1c181062059
ELOP-728928-2016 | 5080114 | 3/21/2017 8:50:08 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL190 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 4 | #Deteriorated__transformer_platform_crossarms__and_poles1.png,Deteriorated__transformer_platform_crossarms__and_poles2.png,Deteriorated__transformer_platform_crossarms__and_poles3.png,Deteriorated__transformer_platform_crossarms__and_poles4.png,Deteriorated__transformer_platform_crossarms__and_poles5.png,Deteriorated__transformer_platform_crossarms__and_poles6.png,Deteriorated__transformer_platform_crossarms__and_poles7.png Poles and structures used to support transformers, conductors, and other electrical equipment rate required to be structurally solid to safely support the equipment that they are intended to support. This is required to prevent the energized equipment and components from falling from the structure or contacting other parts that they are not intended to contact. This installation at a commercial food processing plant has 3 x 250 KVA, 25KV to 480V transformers, and conductors that are supported by a pole, steel and timber structure. The wooden components that supported the conductors and the | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | Deteriorated__transformer_platform_crossarms__and_poles7.png | file://x:/photopub/docs/0000000576/87e9b8cc-9685-43d7-ba82-efeea743780e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ae690d8_2d08_4287_8a79_0461dcb620ca
ELOP-728927-2016 | 3025114 | 3/21/2017 12:10:43 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_starter_cabinets_switches_control_devices_and_splices1.png,Open_starter_cabinets_switches_control_devices_and_splices2.png,Open_starter_cabinets_switches_control_devices_and_splices3.png,Open_starter_cabinets_switches_control_devices_and_splices4.png,Open_starter_cabinets_switches_control_devices_and_splices5.png,Open_starter_cabinets_switches_control_devices_and_splices6.png,Open_starter_cabinets_switches_control_devices_and_splices7.png,Open_starter_cabinets_switches_control_devices_and_splices8.png,Open_starter_cabinets_switches_control_devices_and_splices9.png,Open_starter_cabinets_switches_control_devices_and_splices10.png,Open_starter_cabinets_switches_control_devices_and_splices11.png,Open_starter_cabinets_switches_control_devices_and_splices12.png,Open_starter_cabinets_switches_control_devices_and_splices13.png,Open_starter_cabinets_switches_control_devices_and_splices14.png,Open_starter_cabinets_switches_control_devices_and_splices15.png,Open_starter_cabinets_switches_control_devices_and_splice | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_starter_cabinets_switches_control_devices_and_splices7.png | file://x:/photopub/docs/0000000576/f68ab749-3f59-4cca-a253-6627703dc746.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dde0ee71_85ea_4d62_99e1_e1c181062059
GAIN-751018-2017 | GA-490569-2017 | 4/25/2017 3:49:10 PM | ASSESS: GA: Final | png | #asFound | GA055 | Bonding for Corrugated Stainless Steel Tubing missing | 3 | 3 | #530_4.png Corrugated stainless steel tubing missing bond connection. Corrugated stainless steel tubing is highly susceptible to electrical fault damage which could lead to uncontrolled release of gas resulting in a possible fire or explosion. | 3 | Bonding for Corrugated Stainless Steel Tubing missing | 530_4.png | file://x:/photopub/docs/0000000591/a6b8b5ec-defd-4cfd-b530-8203d7d57027.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__35fc6206_a97e_48b9_ae08_d503925b58a1
ELOP-786976-2017 | 4070055 | 3/31/2017 12:11:49 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 4 | #P1.png,P2.png,P3.png 3 phase 208 volt electrical panel-boards in wood shop have exposed live buss exposed due to unfilled openings. Inadvertent accidental contact may lead to serious shock, arc flash and fire hazards. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | P1.png | file://x:/photopub/docs/0000000579/16d9851d-f847-42a2-a3bf-b8deb06cb223.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e807d023_fef7_4cbe_8aac_fbc5844ed72e
ELOP-786976-2017 | 4070055 | 3/31/2017 12:11:49 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 4 | #P1.png,P2.png,P3.png 3 phase 208 volt electrical panel-boards in wood shop have exposed live buss exposed due to unfilled openings. Inadvertent accidental contact may lead to serious shock, arc flash and fire hazards. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | P3.png | file://x:/photopub/docs/0000000579/319179d2-6a18-49fd-9629-c3aad53aedfe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e807d023_fef7_4cbe_8aac_fbc5844ed72e
ELOP-786976-2017 | 4070055 | 3/31/2017 12:11:49 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 4 | #P1.png,P2.png,P3.png 3 phase 208 volt electrical panel-boards in wood shop have exposed live buss exposed due to unfilled openings. Inadvertent accidental contact may lead to serious shock, arc flash and fire hazards. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | P2.png | file://x:/photopub/docs/0000000579/b8120531-6e85-4a86-83bb-4499112ac7d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e807d023_fef7_4cbe_8aac_fbc5844ed72e
ELHE-770136-2017 | HE-508563-2017 | 3/7/2017 10:43:36 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL162 | Installation of electrical equipment Visible charring of combustibles. | 5 | 5 | #Heaters1.png,Heaters2.png 240 volt/ 500 watt bathroom space heaters obstructed when door in open position: may lead to excess temperature and fire risk if left unattended. | 5 | Installation of electrical equipment Visible charring of combustibles. | Heaters2.png | file://x:/photopub/docs/0000000567/d90ac7a6-5aba-45bc-8967-afaf1d67ac18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db8f05f2_2ad5_4970_b9a1_05a841eae45a
ELHE-770136-2017 | HE-508563-2017 | 3/7/2017 10:43:36 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL162 | Installation of electrical equipment Visible charring of combustibles. | 5 | 5 | #Heaters1.png,Heaters2.png 240 volt/ 500 watt bathroom space heaters obstructed when door in open position: may lead to excess temperature and fire risk if left unattended. | 5 | Installation of electrical equipment Visible charring of combustibles. | Heaters1.png | file://x:/photopub/docs/0000000567/9e75aee3-6d92-4347-96d2-863127c79e6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db8f05f2_2ad5_4970_b9a1_05a841eae45a
ELIN-763973-2017 | EL-480784-2016 | 3/1/2017 10:36:44 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL157 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 4 | 4 | #Old_and_new_power_pole1.png,Old_and_new_power_pole2.png At an existing septic field service facility, an existing 100amp 240volt 1phase service was found mounted to a rotten and unapproved power pole. This utilization equipment installation can lead to an "Equipment Damage" situation. Pic attached. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | Old_and_new_power_pole1.png | file://x:/photopub/docs/0000000564/8de51b4c-acb2-4c39-9b46-c44571470d3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__948541bc_5485_43ea_9ba8_534112a624c6
ELIN-763973-2017 | EL-480784-2016 | 3/1/2017 10:36:44 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL157 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 4 | 4 | #Old_and_new_power_pole1.png,Old_and_new_power_pole2.png At an existing septic field service facility, an existing 100amp 240volt 1phase service was found mounted to a rotten and unapproved power pole. This utilization equipment installation can lead to an "Equipment Damage" situation. Pic attached. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | Old_and_new_power_pole2.png | file://x:/photopub/docs/0000000564/9cb9cfbe-b968-4aec-b0fb-dd5482cce0f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__948541bc_5485_43ea_9ba8_534112a624c6
ELHE-782139-2017 | HE-515689-2017 | 3/24/2017 1:46:51 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Leaning_power_shed.png Service conductors that are feeding a power shed are under tension, due to the fact that the shed that these service conductors are feeding has tipped over. The service conductors have a strain being put on them. If the conductors were to break due to tension, there would be a risk of exposed energized conductors, this would prove to be a shock or fire hazard to persons and property. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Leaning_power_shed.png | file://x:/photopub/docs/0000000576/8bac2bb8-de35-4e17-a93d-c174ff3564d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18986b40_2c6a_4bb8_a41d_99305c8527c4
ELHE-782139-2017 | HE-515689-2017 | 3/24/2017 1:46:51 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Power shed is damaged and conductors are under tension | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Leaning_power_shed.png Service conductors that are feeding a power shed are under tension, due to the fact that the shed that these service conductors are feeding has tipped over. The service conductors have a strain being put on them. If the conductors were to break due to tension, there would be a risk of exposed energized conductors, this would prove to be a shock or fire hazard to persons and property. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Leaning_power_shed.png | file://x:/photopub/docs/0000000576/8bdd872f-f4b1-4795-aa5b-0b187cdcb922.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18986b40_2c6a_4bb8_a41d_99305c8527c4
ELIN-769722-2017 | EL-508334-2017 | 3/7/2017 6:05:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Service_cables_within_reach.png This assessment found a new 200A service installed in a public campground. The cables are accessible via stairs to a flat roof and then within reach, presenting a shock hazard. This service was not energized, but connection had been requested. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Service_cables_within_reach.png | file://x:/photopub/docs/0000000567/5640f496-cadc-45b1-bdcd-fab1ee6c2045.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e7cff39_d1dc_45ed_b3db_a8fe0cf6f110
GAHE-793952-2017 | HE-522006-2017 | 4/13/2017 3:50:28 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | #Pizza_oven1.png,Pizza_oven2.png Products of combustion spilling at all times from venting system draft hood serving a gas fired pizza conveyor oven. Spillage of combustion products into the occupied space could cause people to become ill from carbon monoxide poisoning. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Pizza_oven2.png | file://x:/photopub/docs/0000000586/5aa34219-2d77-4255-af7c-a1f3ad253a07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6def15f_02ae_492c_a84f_3c403990b7ed
GAHE-793952-2017 | HE-522006-2017 | 4/13/2017 3:50:28 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | #Pizza_oven1.png,Pizza_oven2.png Products of combustion spilling at all times from venting system draft hood serving a gas fired pizza conveyor oven. Spillage of combustion products into the occupied space could cause people to become ill from carbon monoxide poisoning. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Pizza_oven1.png | file://x:/photopub/docs/0000000586/5d348709-e039-4cf5-932a-506e70273c02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6def15f_02ae_492c_a84f_3c403990b7ed
EDIN-798260-2017 | ED-435087-2016 | 4/19/2017 6:25:56 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED048 | Wear or defects that are: Likely to progress Contractor is aware of condition | 2 | 2 | #Eye_bolt_1_of_2.png,Eye_bolt_2_of_2.png The compensating chain installation does not meet the requirements as set out by the engineer of the elevator contractor. It has been recognized that inferior hardware has been used on previous installations and that a mishap almost occurred when a Eye-hook failed and the compensating chain almost fell from the bottom of the car. | 2 | Wear or defects that are: Likely to progress Contractor is aware of condition | Eye_bolt_2_of_2.png | file://x:/photopub/docs/0000000588/da9e3582-9928-4a21-98a3-2439c9328aa6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7c8619a_9f54_4c3c_bf1e_d53f668b8761
EDIN-798260-2017 | ED-435087-2016 | 4/19/2017 6:25:56 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED048 | Wear or defects that are: Likely to progress Contractor is aware of condition | 2 | 2 | #Eye_bolt_1_of_2.png,Eye_bolt_2_of_2.png The compensating chain installation does not meet the requirements as set out by the engineer of the elevator contractor. It has been recognized that inferior hardware has been used on previous installations and that a mishap almost occurred when a Eye-hook failed and the compensating chain almost fell from the bottom of the car. | 2 | Wear or defects that are: Likely to progress Contractor is aware of condition | Eye_bolt_1_of_2.png | file://x:/photopub/docs/0000000588/0f7eb623-4ac5-4251-9c84-65ee15baaa3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7c8619a_9f54_4c3c_bf1e_d53f668b8761
ELOP-653094-2016 | EL-203882-2015 | 3/10/2017 8:44:15 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Protective_covers_removed_and_breaker_fillers_not_in_place.png Multiple locations where distribution panel breakers and junction box covers have been removed. These are all in locations that are not accessible by the public.Protective covers or barriers protect persons or equipment from coming in contact with energized equipment. If accidental contact were to occur a risk of shock and fire would be present to persons or property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Protective_covers_removed_and_breaker_fillers_not_in_place.png | file://x:/photopub/docs/0000000569/80e863df-ae82-43fa-84b7-82debb471856.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DA724580_0931_4844_8001_A014535ADE79
ELIN-770639-2017 | UW-508969-2017 | 3/7/2017 8:51:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Annunciator1.png,Annunciator2.png,Annunciator3.png,Annunciator4.png,Annunciator5.png,Annunciator6.png,Annunciator7.png,Annunciator8.png,Annunciator9.png,Annunciator10.png,Annunciator11.png,Annunciator12.png Fire alarm annunciator panel emergency life safety system equipment without evidence of approval. Unapproved annunciator may not provide accurate information to fire fighters during a fire condition. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Annunciator10.png | file://x:/photopub/docs/0000000569/ca5116f8-f7e2-4bc4-af70-0be0d5752ec6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae30fbd2_6163_4abf_a935_38bd82fb1e89
ELIN-770639-2017 | UW-508969-2017 | 3/7/2017 8:51:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Annunciator1.png,Annunciator2.png,Annunciator3.png,Annunciator4.png,Annunciator5.png,Annunciator6.png,Annunciator7.png,Annunciator8.png,Annunciator9.png,Annunciator10.png,Annunciator11.png,Annunciator12.png Fire alarm annunciator panel emergency life safety system equipment without evidence of approval. Unapproved annunciator may not provide accurate information to fire fighters during a fire condition. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Annunciator8.png | file://x:/photopub/docs/0000000569/1be4f0a4-c5c3-475f-b80f-60fc61c57aa7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae30fbd2_6163_4abf_a935_38bd82fb1e89
ELIN-770639-2017 | UW-508969-2017 | 3/7/2017 8:51:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Annunciator1.png,Annunciator2.png,Annunciator3.png,Annunciator4.png,Annunciator5.png,Annunciator6.png,Annunciator7.png,Annunciator8.png,Annunciator9.png,Annunciator10.png,Annunciator11.png,Annunciator12.png Fire alarm annunciator panel emergency life safety system equipment without evidence of approval. Unapproved annunciator may not provide accurate information to fire fighters during a fire condition. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Annunciator4.png | file://x:/photopub/docs/0000000569/116e7da3-8512-4f29-9745-3a1e5d07c676.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae30fbd2_6163_4abf_a935_38bd82fb1e89
ELIN-770639-2017 | UW-508969-2017 | 3/7/2017 8:51:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Annunciator1.png,Annunciator2.png,Annunciator3.png,Annunciator4.png,Annunciator5.png,Annunciator6.png,Annunciator7.png,Annunciator8.png,Annunciator9.png,Annunciator10.png,Annunciator11.png,Annunciator12.png Fire alarm annunciator panel emergency life safety system equipment without evidence of approval. Unapproved annunciator may not provide accurate information to fire fighters during a fire condition. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Annunciator2.png | file://x:/photopub/docs/0000000569/6da600f8-cd1f-4618-946c-c1a98c838429.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae30fbd2_6163_4abf_a935_38bd82fb1e89
ELIN-770639-2017 | UW-508969-2017 | 3/7/2017 8:51:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Annunciator1.png,Annunciator2.png,Annunciator3.png,Annunciator4.png,Annunciator5.png,Annunciator6.png,Annunciator7.png,Annunciator8.png,Annunciator9.png,Annunciator10.png,Annunciator11.png,Annunciator12.png Fire alarm annunciator panel emergency life safety system equipment without evidence of approval. Unapproved annunciator may not provide accurate information to fire fighters during a fire condition. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Annunciator6.png | file://x:/photopub/docs/0000000569/2a2f6131-ab70-463f-977a-782c5757cc5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae30fbd2_6163_4abf_a935_38bd82fb1e89
ELIN-775247-2017 | EL-119065-2014 | 3/16/2017 12:27:45 PM | ASSESS: EL: Final | png | #asFound | EL020 | Damage to equipment may result in overheating. | 4 | 3 | #Some_of_the_equipment_in_the_room_found_with_high_ambient_temperatures.png A new public community centre with an 800 amp 600 volt service room was found to have ambient temperatures well in excess of 30 Degrees celcius. Electrical equipment and conductors can be damaged or overheat when subjected to over-temperature unless all equipment and conductors are specifically designed and debated for the high temperature environment. This can result in equipment of conductor failures that could lead to injury to persons or damage to property | 4 | Damage to equipment may result in overheating. | Some_of_the_equipment_in_the_room_found_with_high_ambient_temperatures.png | file://x:/photopub/docs/0000000572/a13d9bc9-7cbf-4672-b0fd-aeeec0ad8895.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f639dbf0_e938_4d50_b703_b59624a01d57
ELIN-778307-2017 | EL-493087-2017 | 3/22/2017 2:41:15 PM | ASSESS: EL: Final | png | #asFound Switch without a cover plate. | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | #P7.png Accidental contact with screw terminals of the switch without cover can deliver a electrical shock between person's fingers touching the terminals and grounded parts of the switch. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | P7.png | file://x:/photopub/docs/0000000575/c7df31dd-b0f4-489a-a56b-c9362321ed66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d27a415_5919_47fa_ba67_c5b12e555ae9
ELHE-783143-2017 | HE-516029-2017 | 3/27/2017 11:32:05 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Rotten_pole.png what the code is. why the code is.what you saw. what the hazards are. The electrical code requires that power line poles are maintained and in good repair. The pole is split and is rotted all the way through at the base. This pole will fall over soon if not replaced. | 0 | No Created Hazard Identified | Rotten_pole.png | file://x:/photopub/docs/0000000576/48f20be5-21ab-4a09-b3b4-9a2fc5af0118.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6954bd88_587d_4186_86da_b953eac6a24e
GAUP-783463-2017 | UW-516233-2017 | 3/27/2017 2:06:34 PM | ASSESS: GA UP: Regulated Work WO Permit | JPG | #asFound Non-compliant clearance between vent termination and mechanical air intake. | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #image1.JPG While assessing an unpermitted installation I found an appliance vent terminating too close to the mechanical air intake of the adjacent unit. Should the one unit be firing while the other is taking in fresh air, products of combustion could be drawn into the occupied space and distributed through the HVAC system. This could potentially lead to CO poisoning of the occupants within. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | image1.JPG | file://x:/photopub/docs/0000000577/5437acec-3a88-4e50-8036-e008dae975a5.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3db560aa_61fd_4ed3_93c0_bced6061953b
GAUP-783463-2017 | UW-516233-2017 | 3/27/2017 2:06:34 PM | ASSESS: GA UP: Regulated Work WO Permit | JPG | #asFound As found picture | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #image1.JPG While assessing an unpermitted installation I found an appliance vent terminating too close to the mechanical air intake of the adjacent unit. Should the one unit be firing while the other is taking in fresh air, products of combustion could be drawn into the occupied space and distributed through the HVAC system. This could potentially lead to CO poisoning of the occupants within. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | image1.JPG | file://x:/photopub/docs/0000000577/66d5be1b-0dd4-4f08-be3f-86fe8f721052.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3db560aa_61fd_4ed3_93c0_bced6061953b
GAIN-772036-2017 | GA-487708-2017 | 3/13/2017 10:12:28 AM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Vent.png The as found condition is a set of commonly vented category 4 water heaters are using room air for the combustion process although the manufacturer requires the system to be direct vented. The as found hazard is if the appliances are not installed according to the manufacturer's requirements, they could fail prematurely leading to possible system damage. | 3 | Appliance not installed according to installation instructions | Vent.png | file://x:/photopub/docs/0000000570/b1c36038-6aa0-49a4-9464-eaebfda9eb34.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c0fa295_e2ef_47d1_acb6_550ddd1ba1b1
EDIN-801885-2017 | ED-488786-2017 | 4/24/2017 5:10:48 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | #Missing_clip_of_a_Chain_Link.png The Chain Link is used to secure the Compensating Chain to the bottom of the elevator. The Compensating Chain is connected from the bottom of the elevator to the bottom of the counterweight and thus is quite heavy and will cause a lot of damage to the elevator equipment in the hoistway if it disconnects from the bottom of the elevator. During an acceptance assessment it was found the Chain Link was missing a center spacer clip that secures the pin that holds the ends of the Chain Link together. Over time the pin may work itself free and will cause the Compensating Chain to disconnect from the bottom of the elevator. It was found the elevator contractor failed to properly install the Chain Link. This 15 stop MachineRoomLess traction elevator is located in a newly constructed commercial hotel building. | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Missing_clip_of_a_Chain_Link.png | file://x:/photopub/docs/0000000590/ba67f60b-b3be-4d6b-b0ea-e05d7842ca04.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f1b3402_dd6e_468a_bd50_e3a9be21765f
ELIN-789753-2017 | EL-494707-2017 | 4/6/2017 10:42:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Main_distribution_.png 200 amp, 120/240 volt indoor rated main distribution panel installed in a location that is subject to outdoor elements. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_distribution_.png | file://x:/photopub/docs/0000000583/0a5d9c47-455d-4991-b07e-959bd2e5ce31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8ee92e1_44f5_40b5_9635_a31f46b4a9cc
EDMA-773692-2017 | ED-101780-2014 | 3/13/2017 10:34:25 AM | ASSESS: ED MA: Partial Acceptance | png | #asFound | ED048 | Wear or defects that are: Likely to progress Contractor is aware of condition | 2 | 2 | #Counterweight_biscuit_hold-down.png After a buffer test the inertia created by the test caused the counterweight biscuits to shift upwards. The counterweight rod and hold-down mechanism was unable to keep the biscuits from moving upwards. There is no real danger of the biscuit falling out. | 2 | Wear or defects that are: Likely to progress Contractor is aware of condition | Counterweight_biscuit_hold-down.png | file://x:/photopub/docs/0000000570/b315e45c-6f0a-4f95-a69b-55e12f5ca687.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f1e1d79_bef9_4a3f_b13e_931a4c9f5f24
ELOP-759601-2017 | 1806 | 4/6/2017 9:28:24 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 4 | #Dry_core_xfmr_120_mm_from_combustibles.png A dry core transformer operating at 600 volts and 50 amps was found installed approximately 120 mm from a combustible surface in a public building. Dry core transformers are subject to occasional sustained electrical failures that can ignite adjacent combustibles if not provided adequate separation from combustibles which can lead to property damage and injury to persons. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | Dry_core_xfmr_120_mm_from_combustibles.png | file://x:/photopub/docs/0000000582/b5288171-7673-4b38-99ae-9c9c6f4d699f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df79888b_707f_4140_820b_a3cf3487f71b
ELHE-808985-2017 | HE-530002-2017 | 4/25/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Broken_receptacle_and_cover.png Covers must be provided for electrical equipment to prevent shock injury. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Broken_receptacle_and_cover.png | file://x:/photopub/docs/0000000597/32b2ca4f-25b1-4371-9f90-8bfd3cc2acb5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d12c7c0_be77_4361_9b51_cc7fb64c0aa3
ELHE-808987-2017 | HE-530006-2017 | 4/26/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL046 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to general public. | 5 | 5 | #Open_storage_of_lead_acid_batteries1.png,Open_storage_of_lead_acid_batteries2.png Lead acid batteries are stored in an area that is not sealed and vented from the rest of the house. Accidental contact could occur resulting in shock injury. | 5 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to general public. | Open_storage_of_lead_acid_batteries2.png | file://x:/photopub/docs/0000000597/c351b39f-f295-4b0b-946c-0d5d0c43b822.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a85ad699_dff9_4fca_8ee3_c8b9a470ea36
AMOP-793342-2017 | 3765215 | 4/11/2017 7:18:24 AM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Archway_brackets_corroded1.png,Archway_brackets_corroded2.png,Archway_brackets_corroded3.png,Archway_brackets_corroded4.png Archway light brackets, over the ride flumes, are corroded. Archway could collapse onto guests | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Archway_brackets_corroded3.png | file://x:/photopub/docs/0000000585/ef834172-e823-408c-acd5-7df9f7cc8d22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08ec8e59_7b6e_42b0_9168_3658a77b4890
AMOP-793342-2017 | 3765215 | 4/11/2017 7:18:24 AM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Archway_brackets_corroded1.png,Archway_brackets_corroded2.png,Archway_brackets_corroded3.png,Archway_brackets_corroded4.png Archway light brackets, over the ride flumes, are corroded. Archway could collapse onto guests | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Archway_brackets_corroded1.png | file://x:/photopub/docs/0000000585/225ff03b-dbdc-4cf2-a7d7-6004eda95762.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08ec8e59_7b6e_42b0_9168_3658a77b4890
AMOP-793344-2017 | 3759754 | 4/11/2017 7:57:50 AM | ASSESS: AM OP: Periodic | png | #asFound | AM022 | Defect that impairs performance: Performance remains within limits Non-degenerative or very slow Reasonably detectable by the maintenance or operation program | 2 | 2 | #Rider_restraint_not_correct.png Safety restraint in PCU had missing clips, restraint was not functioning at time of inspection.passenger could fall out of ride. | 2 | Defect that impairs performance: Performance remains within limits Non-degenerative or very slow Reasonably detectable by the maintenance or operation program | Rider_restraint_not_correct.png | file://x:/photopub/docs/0000000585/4982368f-c1e8-46f5-88e7-f05a44369cba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6db019d8_f9ca_458b_8610_7158ae88f2c5
GAIN-741925-2017 | GA-445082-2016 | 4/28/2017 2:05:16 PM | ASSESS: GA: Commissioning Approval | png | #asFound | GA120 | Mechanical Air/ventilation supply present, missing interlock | 3 | 3 | #DFMUA.png Missing interlocks on exhaust system to shut down direct fired make up air in case of system failure. If interlocks are not in place and there was a system failure there is the possibility of carbon monoxide exposure leading to injury or death. | 3 | Mechanical Air/ventilation supply present, missing interlock | Dfmua.png | file://x:/photopub/docs/0000000593/ba153973-1dba-4c10-82cb-ecf10c87a20b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__763e89b1_a2af_4d04_aebc_d92e99e26117
ELIN-803351-2017 | EL-526886-2017 | 4/28/2017 11:36:52 AM | ASSESS: EL: Final | png | #asFound | EL130 | Installation of electrical equipment Arc producing electrical equipment within 1 meter of gas relief device or vent | 2 | 2 | #Heat_pump_disconnect_location1.png,Heat_pump_disconnect_location2.png This type 3R heat pump disconnect was installed directly beside two existing propane tanks. This installation has created the potential for a fire and an explosion. If an individual were to operate the disconnect under load an arc would occur, causing the propane gasses to ignite and a possible explosion. | 2 | Installation of electrical equipment Arc producing electrical equipment within 1 meter of gas relief device or vent | Heat_pump_disconnect_location2.png | file://x:/photopub/docs/0000000592/f1775b96-5dd8-40ae-929a-f1718805cee5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34b535a1_6561_4dc8_9052_781bdb2bbf82
ELIN-803351-2017 | EL-526886-2017 | 4/28/2017 11:36:52 AM | ASSESS: EL: Final | png | #asFound Heat pump disconnect is located directly beside two propane tanks | EL130 | Installation of electrical equipment Arc producing electrical equipment within 1 meter of gas relief device or vent | 2 | 2 | #Heat_pump_disconnect_location1.png,Heat_pump_disconnect_location2.png This type 3R heat pump disconnect was installed directly beside two existing propane tanks. This installation has created the potential for a fire and an explosion. If an individual were to operate the disconnect under load an arc would occur, causing the propane gasses to ignite and a possible explosion. | 2 | Installation of electrical equipment Arc producing electrical equipment within 1 meter of gas relief device or vent | Heat_pump_disconnect_location1.png | file://x:/photopub/docs/0000000592/35867326-3f94-47eb-bd00-2242a6f88ed7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34b535a1_6561_4dc8_9052_781bdb2bbf82
EDIN-763013-2017 | ED-435074-2016 | 2/27/2017 5:55:20 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | #Disconnect_Fuse1.png,Disconnect_Fuse2.png Elevator specifications required 60 amp Time Delay Fuses to be installed in the elevator main disconnect. During an inspection, it was found that 175 amp Time Delay Fuses were installed by the Electrical Contractor. Fuses were not checked by the Elevator Contractor prior to inspection. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | Disconnect_Fuse1.png | file://x:/photopub/docs/0000000563/ffaf6809-ad18-4f10-8f72-ff9f4f0a776a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dbe4d29e_9350_4ef4_b1bd_6ed1b02c691e
EDIN-763013-2017 | ED-435074-2016 | 2/27/2017 5:55:20 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | #Disconnect_Fuse1.png,Disconnect_Fuse2.png Elevator specifications required 60 amp Time Delay Fuses to be installed in the elevator main disconnect. During an inspection, it was found that 175 amp Time Delay Fuses were installed by the Electrical Contractor. Fuses were not checked by the Elevator Contractor prior to inspection. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | Disconnect_Fuse2.png | file://x:/photopub/docs/0000000563/77a2032e-9b01-4252-87f9-7183cc10224e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dbe4d29e_9350_4ef4_b1bd_6ed1b02c691e
ELIN-771179-2017 | EL-508386-2017 | 3/15/2017 7:58:28 AM | ASSESS: EL: Service Connection | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | #Ground_conductor.png At a new residential property a new 200amp 120/240volt 1phase electrical service was found with the system ground not attached to the identified conductor. This can lead to a "Shock" hazard. Pic attached | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Ground_conductor.png | file://x:/photopub/docs/0000000571/889ade8e-79c2-40be-a587-2c3334783d81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06669fff_d2f7_42c0_acfb_033045528a4f
ELIN-804544-2017 | EL-458374-2016 | 5/2/2017 4:50:03 PM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Conductor to be grounded is not grounded. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | A3.png | file://x:/photopub/docs/0000000595/a542b227-a4b1-48e1-87c7-b7a023488ce9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__88dddd86_8943_4181_9808_5b8d59193d35
ELIN-804544-2017 | EL-458374-2016 | 5/2/2017 4:50:03 PM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Conductor to be grounded is not grounded. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | A1.png | file://x:/photopub/docs/0000000595/3d340651-edae-4474-88d1-a96acae353bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__88dddd86_8943_4181_9808_5b8d59193d35
ELIN-804544-2017 | EL-458374-2016 | 5/2/2017 4:50:03 PM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Conductor to be grounded is not grounded. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | A4.png | file://x:/photopub/docs/0000000595/399e6bce-386e-4fd1-a087-dd18fefa3e02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__88dddd86_8943_4181_9808_5b8d59193d35
ELIN-804544-2017 | EL-458374-2016 | 5/2/2017 4:50:03 PM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Conductor to be grounded is not grounded. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | A2.png | file://x:/photopub/docs/0000000595/f162cbad-8586-493e-beec-e918f7be84e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__88dddd86_8943_4181_9808_5b8d59193d35
GAWP-748999-2017 | GA-422290-2016 | 3/1/2017 6:37:31 AM | ASSESS: GA Work In Progress | png | #asFound | GA024 | No protection Low traffic | 3 | 3 | #Veh2.png Vehicles parked beside and around propane tank, piping and generator at a commercial building. Vehicles parking or snow removal could damage equipment or system causing release of propane. | 3 | No protection Low traffic | Veh2.png | file://x:/photopub/docs/0000000565/50d2cea9-763b-4e58-b0cb-7c92ab790460.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e36cd3d5_3fea_4548_82a5_f7df4feab680
GAOP-638381-2016 | 3852569 | 3/2/2017 11:27:29 AM | ASSESS: GA OP: Periodic | png | #asFound | GA089 | No hydrostatic relief in liquid propane system where required | 5 | 5 | #Hydrostatic.png Hydrostatic relief device missing on a 3" liquid propane piping system between an isolation valve and the pump. In the event of system being isolated, liquid propane could be trapped and with no place to expand, causing failure or rupture to piping system. | 5 | No hydrostatic relief in liquid propane system where required | Hydrostatic.png | file://x:/photopub/docs/0000000565/37a520da-6a7e-4b16-a262-b68f934756d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8E6EF714_81AA_4D1E_903E_43E2F7897D2D
ELIN-787146-2017 | UW-518244-2017 | 4/4/2017 8:09:35 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Suite_panel_.png The 15 amp 120 volt outlet branch circuits do not include AFCI protection, this is a thermal hazard | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Suite_panel_.png | file://x:/photopub/docs/0000000581/606a4fec-2105-45f5-9078-9fec22ebf1c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34d4aa3c_6dc3_4e18_b4ae_fbfcc3c10ef5
EDRI-769152-2017 | ED-411012-2016 | 3/6/2017 11:36:47 AM | ASSESS: ED RI: Final | png | #asFound | ED055 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | 4 | 4 | #No_handrails.png Handrails need to be present at the edge of building to prevent severe fall hazards. At the new landings of the hoist there are no handrails present on slab edge beside the hoist landings. | 4 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | No_handrails.png | file://x:/photopub/docs/0000000567/72cd83bf-a4c9-4a47-ae76-5e4c385f1af7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__debf51bb_3369_4dbf_aaff_5a29f51e035f
EDRI-769153-2017 | ED-411008-2016 | 3/6/2017 11:45:45 AM | ASSESS: ED RI: Final | png | #asFound Worker was seen out on a tower brace while the hoist was in operation. Hoarding should have been in place to prevent access but they had removed the hoarding. A counterweight that weighs several tonnes passes through the brace the workers were partially suspended on which could strike them. | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Worker_in_dangerous_space.png Worker was seen out on a tower brace while the hoist was in operation. Hoarding should have been in place to prevent access but they had removed the hoarding. A counterweight that weighs several tonnes passes through the brace the workers were partially suspended on which could strike them. | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Worker_in_dangerous_space.png | file://x:/photopub/docs/0000000567/031fb74b-7124-41df-8284-6e22eb829d60.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d26e88b_e1b0_4e6c_bf08_a6634c478528
GAIN-771371-2017 | GA-474067-2016 | 4/21/2017 11:41:52 AM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | #Certified_appliance_hose_not_certified_for_application.png Certified connector not approved for application. A radiant tube heater must be connected using Type 1 hose connector to allow for movement and prevent damage to the hose. | 2 | Certified appliance connector installed but not approved for application | Certified_appliance_hose_not_certified_for_application.png | file://x:/photopub/docs/0000000590/a60db496-04d1-4588-a999-e83f858aba09.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c0916d0_cae2_41d9_b005_9f515677f31c
ELOP-789826-2017 | EL-081932-2014 | 4/5/2017 10:46:08 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL157 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 4 | 4 | #Exposed_light_standard_conductors.png Missing electrical lighted sign standard at parking lot entrance, with exposed non-energized electrical conductors that could present an electrocution hazard in the event that the conductors become energized. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | Exposed_light_standard_conductors.png | file://x:/photopub/docs/0000000582/1f579eb7-009e-432d-9380-012d09f8b4bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5c41266_dac8_44ff_9e2c_1b52fd8fc019
ELIN-797064-2017 | EL-481162-2016 | 5/2/2017 12:53:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Temporary_heater_receptacles1.png,Temporary_heater_receptacles2.png,Temporary_heater_receptacles3.png,Temporary_heater_receptacles4.png,Temporary_heater_receptacles5.png Receptacles are designed, manufactured, and approved for specific installation methods. This is done to ensure that receptacles are installed and used in a safe manner. This installation at a new house under construction has two 30A 240V receptacles that have been installed to provide power to temporary construction heaters used during construction. The receptacles are installed on the range and dryer outlet boxes and mounted to the boxes with one screw on each receptacle installed into the boxes. The receptacles are not mounted properly and do not have covers on them to prevent contact with energized terminals or damage to the receptacles and wiring. Left uncorrected this is a shock and fire hazard if energized terminals or wiring is contacted or damaged. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Temporary_heater_receptacles1.png | file://x:/photopub/docs/0000000594/d4e4893c-9166-4c25-94f7-909e9bde59fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ac17a52_57d4_4ac6_866a_22831c6eb15b
ELIN-797064-2017 | EL-481162-2016 | 5/2/2017 12:53:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Temporary_heater_receptacles1.png,Temporary_heater_receptacles2.png,Temporary_heater_receptacles3.png,Temporary_heater_receptacles4.png,Temporary_heater_receptacles5.png Receptacles are designed, manufactured, and approved for specific installation methods. This is done to ensure that receptacles are installed and used in a safe manner. This installation at a new house under construction has two 30A 240V receptacles that have been installed to provide power to temporary construction heaters used during construction. The receptacles are installed on the range and dryer outlet boxes and mounted to the boxes with one screw on each receptacle installed into the boxes. The receptacles are not mounted properly and do not have covers on them to prevent contact with energized terminals or damage to the receptacles and wiring. Left uncorrected this is a shock and fire hazard if energized terminals or wiring is contacted or damaged. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Temporary_heater_receptacles5.png | file://x:/photopub/docs/0000000594/90b1a7ce-1ee4-46f8-bbe9-10f2afae7006.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ac17a52_57d4_4ac6_866a_22831c6eb15b
ELIN-797064-2017 | EL-481162-2016 | 5/2/2017 12:53:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Temporary_heater_receptacles1.png,Temporary_heater_receptacles2.png,Temporary_heater_receptacles3.png,Temporary_heater_receptacles4.png,Temporary_heater_receptacles5.png Receptacles are designed, manufactured, and approved for specific installation methods. This is done to ensure that receptacles are installed and used in a safe manner. This installation at a new house under construction has two 30A 240V receptacles that have been installed to provide power to temporary construction heaters used during construction. The receptacles are installed on the range and dryer outlet boxes and mounted to the boxes with one screw on each receptacle installed into the boxes. The receptacles are not mounted properly and do not have covers on them to prevent contact with energized terminals or damage to the receptacles and wiring. Left uncorrected this is a shock and fire hazard if energized terminals or wiring is contacted or damaged. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Temporary_heater_receptacles4.png | file://x:/photopub/docs/0000000594/97ee69e3-1d77-4fe8-84b2-69b1ce26de7c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ac17a52_57d4_4ac6_866a_22831c6eb15b
ELIN-797064-2017 | EL-481162-2016 | 5/2/2017 12:53:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Temporary_heater_receptacles1.png,Temporary_heater_receptacles2.png,Temporary_heater_receptacles3.png,Temporary_heater_receptacles4.png,Temporary_heater_receptacles5.png Receptacles are designed, manufactured, and approved for specific installation methods. This is done to ensure that receptacles are installed and used in a safe manner. This installation at a new house under construction has two 30A 240V receptacles that have been installed to provide power to temporary construction heaters used during construction. The receptacles are installed on the range and dryer outlet boxes and mounted to the boxes with one screw on each receptacle installed into the boxes. The receptacles are not mounted properly and do not have covers on them to prevent contact with energized terminals or damage to the receptacles and wiring. Left uncorrected this is a shock and fire hazard if energized terminals or wiring is contacted or damaged. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Temporary_heater_receptacles3.png | file://x:/photopub/docs/0000000594/de8ef07d-1335-42cd-b146-24feac5dd810.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ac17a52_57d4_4ac6_866a_22831c6eb15b
ELIN-768667-2017 | EL-471060-2016 | 3/7/2017 3:12:27 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMSC_in_PVC_conduit.png Insulated conductors used for electrical installations must be suitable for the location and suitable for the conditions of use. This is so the insulation of the conductor does not break down from moisture, temperature, corrosion or mechanical damage. In this installation at a new residential dwelling, a non-metallic sheathed cable was installed in a slab on grade PVC conduit to feed kitchen island receptacles. The non-metallic sheathed cable is not approved for wet locations and is not approved for raceways. The moisture inside the PVC conduit could eventually cause the insulation of the conductors to break down and an electrical fault to occur on the circuit which could lead to electrical equipment damage. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_in_PVC_conduit.png | file://x:/photopub/docs/0000000569/26e09540-9dcf-4420-ba6a-2d609ea2e971.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__548289f3_317e_47d6_a8f4_4b285f9a3939
BPVIN-772655-2017 | BPV-259029-2015 | 3/15/2017 7:02:26 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Remote_shutdown_switch_location1.png,Remote_shutdown_switch_location2.png A disconnect means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in event of an emergency. There was no remote shutdown switch installed on the hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Remote_shutdown_switch_location2.png | file://x:/photopub/docs/0000000572/1edc0299-f7e0-49ed-9f58-92621e6ae12a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b056ec3c_40d8_4364_8a54_21076de7a30a
BPVIN-772655-2017 | BPV-259029-2015 | 3/15/2017 7:02:26 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound By boiler, not accessible by entrance door. | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Remote_shutdown_switch_location1.png,Remote_shutdown_switch_location2.png A disconnect means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in event of an emergency. There was no remote shutdown switch installed on the hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Remote_shutdown_switch_location1.png | file://x:/photopub/docs/0000000572/8aa9f264-8594-46ef-be50-828b93be6b6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b056ec3c_40d8_4364_8a54_21076de7a30a
ELIN-764869-2017 | EL-492555-2017 | 3/7/2017 8:12:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #Ground_is_not_conneted_to_neutral.png Ground is not terminated to neutral, this could create adverse effects to system by causing a difference in potential energy between to points . The hazard could be shock or thermal effects. | 4 | Installation Grounding; conductor is not continuous. | Ground_is_not_conneted_to_neutral.png | file://x:/photopub/docs/0000000568/fb8d177d-0ea2-44c3-b908-72faa3c07f03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce8173d1_6fbc_458d_8dcf_aeb65a50d18e
ELIN-766961-2017 | EL-383331-2016 | 3/8/2017 5:10:40 PM | ASSESS: EL: Final | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | #Unsupported_and_unprotected_ground_conductor1.png,Unsupported_and_unprotected_ground_conductor2.png Ground conductors are required to be installed so they are free from exposure to mechanical damage and fastened rigidly to the structure. This is required to prevent the ground conductor from becoming damaged which may leave the service ungrounded. This installation has a ground conductor installed for a new house 200A 120/240V service. The 6 awg copper ground conductor is installed in an exposed location where it passes through a concrete side walk and is unsupported and unprotected. Left uncorrected the ground conductor in this manner may become damaged or broken which would leave the service ungrounded. This is a potential shock and fire hazard if the equipment is ungrounded during a fault condition or lightning strike. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Unsupported_and_unprotected_ground_conductor2.png | file://x:/photopub/docs/0000000568/07a2ccf1-af24-49bb-8e3f-72f0755afc77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ddcab0b_582f_4277_8133_41525d6ecc24
GAIN-774428-2017 | GA-445082-2016 | 4/28/2017 2:13:22 PM | ASSESS: GA: Final | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | #Relief_to_mech_air_inatke.png | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | Relief_to_mech_air_inatke.png | file://x:/photopub/docs/0000000593/f5e5824f-a94c-4e3c-96fa-2616e1c4ac83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f98a55e_b3bd_4b70_9ebf_a05c671c293c
ELOP-735177-2017 | EL-057439-2013 | 2/27/2017 3:41:22 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Emergency_lighting1.png,Emergency_lighting2.png Emergency lighting unit without evidence of periodic testing and showing signs of failure. Without proper lighting in the case of an emergency or power outage safe egress from the facility may be limited. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Emergency_lighting2.png | file://x:/photopub/docs/0000000563/f9095c64-bda9-4f12-a32c-531e4bcb27ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec915cdc_cdcc_4c6d_b6c1_61512e42a8db
ELOP-735177-2017 | EL-057439-2013 | 2/27/2017 3:41:22 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Emergency_lighting1.png,Emergency_lighting2.png Emergency lighting unit without evidence of periodic testing and showing signs of failure. Without proper lighting in the case of an emergency or power outage safe egress from the facility may be limited. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Emergency_lighting1.png | file://x:/photopub/docs/0000000563/0840c877-bab0-4f2d-a86a-c91d27d84d0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec915cdc_cdcc_4c6d_b6c1_61512e42a8db
ELHE-780010-2017 | HE-514353-2017 | 3/22/2017 1:05:03 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Service entrance panel showing arc fault breaker's tripping. | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #Panel.png Complaints of arc Fault circuit interrupter breakers tripping. Kitchen circuits on with exterior lighting. Tripping arc Fault breakers. Danger of fire as breakers deteriorate. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Panel.png | file://x:/photopub/docs/0000000575/256457b4-3049-4d49-9f2e-d7d55d73df8d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b11c1d2_6933_4988_9dad_6cbecf060adc
ELHE-757496-2017 | HE-501273-2017 | 2/27/2017 2:05:52 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Switches_not_fastened_to_the_outlet_box1.png,Switches_not_fastened_to_the_outlet_box2.png,Switches_not_fastened_to_the_outlet_box3.png,Switches_not_fastened_to_the_outlet_box4.png Electrical devices such as switches and receptacles must be fastened to outlet boxes and have cover plates installed to prevent contact with energized parts. This installation at a single family dwelling unit has two 15A 120V single pole switches that are not fastened to the outlet box they are connected to. This has left the open energized terminals of the switch exposed to accidental contact by persons or objects. Left uncorrected this is a fire and shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Switches_not_fastened_to_the_outlet_box4.png | file://x:/photopub/docs/0000000563/ada39f23-d2d5-4d80-b3e3-99e55fc3ef1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d91d4b01_edba_4d09_a691_65e12577faad
ELHE-757496-2017 | HE-501273-2017 | 2/27/2017 2:05:52 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Switches_not_fastened_to_the_outlet_box1.png,Switches_not_fastened_to_the_outlet_box2.png,Switches_not_fastened_to_the_outlet_box3.png,Switches_not_fastened_to_the_outlet_box4.png Electrical devices such as switches and receptacles must be fastened to outlet boxes and have cover plates installed to prevent contact with energized parts. This installation at a single family dwelling unit has two 15A 120V single pole switches that are not fastened to the outlet box they are connected to. This has left the open energized terminals of the switch exposed to accidental contact by persons or objects. Left uncorrected this is a fire and shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Switches_not_fastened_to_the_outlet_box1.png | file://x:/photopub/docs/0000000563/55da4b23-25a0-4f05-9c12-c64ea322d5f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d91d4b01_edba_4d09_a691_65e12577faad
ELHE-757496-2017 | HE-501273-2017 | 2/27/2017 2:05:52 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Switches_not_fastened_to_the_outlet_box1.png,Switches_not_fastened_to_the_outlet_box2.png,Switches_not_fastened_to_the_outlet_box3.png,Switches_not_fastened_to_the_outlet_box4.png Electrical devices such as switches and receptacles must be fastened to outlet boxes and have cover plates installed to prevent contact with energized parts. This installation at a single family dwelling unit has two 15A 120V single pole switches that are not fastened to the outlet box they are connected to. This has left the open energized terminals of the switch exposed to accidental contact by persons or objects. Left uncorrected this is a fire and shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Switches_not_fastened_to_the_outlet_box3.png | file://x:/photopub/docs/0000000563/375f3cb5-ba62-4c0a-8cd2-33b28a7dac37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d91d4b01_edba_4d09_a691_65e12577faad
ELIN-797064-2017 | EL-481162-2016 | 5/2/2017 12:53:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Temporary_heater_receptacles1.png,Temporary_heater_receptacles2.png,Temporary_heater_receptacles3.png,Temporary_heater_receptacles4.png,Temporary_heater_receptacles5.png Receptacles are designed, manufactured, and approved for specific installation methods. This is done to ensure that receptacles are installed and used in a safe manner. This installation at a new house under construction has two 30A 240V receptacles that have been installed to provide power to temporary construction heaters used during construction. The receptacles are installed on the range and dryer outlet boxes and mounted to the boxes with one screw on each receptacle installed into the boxes. The receptacles are not mounted properly and do not have covers on them to prevent contact with energized terminals or damage to the receptacles and wiring. Left uncorrected this is a shock and fire hazard if energized terminals or wiring is contacted or damaged. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Temporary_heater_receptacles2.png | file://x:/photopub/docs/0000000594/c341faff-e1ea-439c-aaa1-a4ef54061c57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ac17a52_57d4_4ac6_866a_22831c6eb15b
ELIN-766961-2017 | EL-383331-2016 | 3/8/2017 5:10:40 PM | ASSESS: EL: Final | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | #Unsupported_and_unprotected_ground_conductor1.png,Unsupported_and_unprotected_ground_conductor2.png Ground conductors are required to be installed so they are free from exposure to mechanical damage and fastened rigidly to the structure. This is required to prevent the ground conductor from becoming damaged which may leave the service ungrounded. This installation has a ground conductor installed for a new house 200A 120/240V service. The 6 awg copper ground conductor is installed in an exposed location where it passes through a concrete side walk and is unsupported and unprotected. Left uncorrected the ground conductor in this manner may become damaged or broken which would leave the service ungrounded. This is a potential shock and fire hazard if the equipment is ungrounded during a fault condition or lightning strike. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Unsupported_and_unprotected_ground_conductor1.png | file://x:/photopub/docs/0000000568/9c6f9a0f-4332-4d26-8f74-cae5ebab199a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ddcab0b_582f_4277_8133_41525d6ecc24
GAOP-707808-2016 | 2172209 | 3/16/2017 11:29:26 AM | ASSESS: GA OP: Periodic | png | #asFound | GA147 | Incorrect use of safety controls (Example: bypass limit) | 4 | 4 | #ISC_in_open_postion.png A Internal Safety Control is installed on propane tanks to prevent the uncontrolled release of propane in the event of system or component failure, these safety devices are installed in such a manner that when left unattended they should be in the closed position, the bungy cord in the picture holds the safety device open when left unattended and therefore there is the potential of a uncontrolled release of propane if the propane system where to fail potentially causing property damage. | 4 | Incorrect use of safety controls (Example: bypass limit) | ISC_in_open_postion.png | file://x:/photopub/docs/0000000575/c421da2d-5957-4c96-a3e2-7448cc5c1d71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__F43BCF6D_3492_49AA_947A_2734B09FDF77
ELIN-786968-2017 | EL-506984-2017 | 4/3/2017 1:40:41 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Abrasion__and_bonding_and_use_of_approved_equipment.png A new residential service read it 200 A and 240 V has been installed. The main service cable has been installed so that the armour of the cable is protruding into the electrical equipment. This can cause an abrasion a hazard in this case in the metre base for the house leading to a potential for injury to persons or damage to property | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Abrasion__and_bonding_and_use_of_approved_equipment.png | file://x:/photopub/docs/0000000581/c284a6b2-4745-4ef2-b21d-106921682fa1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73725852_d022_4685_9e27_669768c18d86
ELHE-757496-2017 | HE-501273-2017 | 2/27/2017 2:05:52 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Switches_not_fastened_to_the_outlet_box1.png,Switches_not_fastened_to_the_outlet_box2.png,Switches_not_fastened_to_the_outlet_box3.png,Switches_not_fastened_to_the_outlet_box4.png Electrical devices such as switches and receptacles must be fastened to outlet boxes and have cover plates installed to prevent contact with energized parts. This installation at a single family dwelling unit has two 15A 120V single pole switches that are not fastened to the outlet box they are connected to. This has left the open energized terminals of the switch exposed to accidental contact by persons or objects. Left uncorrected this is a fire and shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Switches_not_fastened_to_the_outlet_box2.png | file://x:/photopub/docs/0000000563/b5a082af-f4b1-4b29-b86f-c74c31213803.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d91d4b01_edba_4d09_a691_65e12577faad
ELHE-762037-2017 | HE-490180-2017 | 2/22/2017 3:32:29 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Clearance from combustible wall not adequate. | EL187 | General Construction Outdoor: inadequate clearances. | 3 | 3 | #Transformer.png Hazard elimination. Inspection of electrical concerns in indoor grow operation requested by City of Chilliwack. Transformer installed too close to combustible wall. Heat damage noted on wall coverings. Fire hazard if not dealt with. | 3 | General Construction Outdoor: inadequate clearances. | Transformer.png | file://x:/photopub/docs/0000000563/d52e2369-fc59-4166-a090-7a415933d74a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__579cd4b7_404b_4d62_bd2f_5b8002c99a6e
ELIN-772765-2017 | UW-510254-2017 | 3/10/2017 11:04:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | #Storage_in_electrical_room1.png,Storage_in_electrical_room2.png,Storage_in_electrical_room3.png,Storage_in_electrical_room4.png,Storage_in_electrical_room5.png,Storage_in_electrical_room6.png,Storage_in_electrical_room7.png,Storage_in_electrical_room8.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Storage_in_electrical_room4.png | file://x:/photopub/docs/0000000569/725eca33-7fb3-438d-b21a-bf07b0f3c7c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9481ef89_6041_4653_ab67_f6419f51f29c
ELIN-772765-2017 | UW-510254-2017 | 3/10/2017 11:04:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | #Storage_in_electrical_room1.png,Storage_in_electrical_room2.png,Storage_in_electrical_room3.png,Storage_in_electrical_room4.png,Storage_in_electrical_room5.png,Storage_in_electrical_room6.png,Storage_in_electrical_room7.png,Storage_in_electrical_room8.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Storage_in_electrical_room2.png | file://x:/photopub/docs/0000000569/4b5ae6bd-2295-463d-9789-6abc81194c21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9481ef89_6041_4653_ab67_f6419f51f29c
ELIN-772765-2017 | UW-510254-2017 | 3/10/2017 11:04:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | #Storage_in_electrical_room1.png,Storage_in_electrical_room2.png,Storage_in_electrical_room3.png,Storage_in_electrical_room4.png,Storage_in_electrical_room5.png,Storage_in_electrical_room6.png,Storage_in_electrical_room7.png,Storage_in_electrical_room8.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Storage_in_electrical_room8.png | file://x:/photopub/docs/0000000569/bfe57f1c-889f-4dec-95a1-ac3277ec7b8e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9481ef89_6041_4653_ab67_f6419f51f29c
ELIN-772765-2017 | UW-510254-2017 | 3/10/2017 11:04:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | #Storage_in_electrical_room1.png,Storage_in_electrical_room2.png,Storage_in_electrical_room3.png,Storage_in_electrical_room4.png,Storage_in_electrical_room5.png,Storage_in_electrical_room6.png,Storage_in_electrical_room7.png,Storage_in_electrical_room8.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Storage_in_electrical_room7.png | file://x:/photopub/docs/0000000569/ebfa1bc4-653e-40be-8f26-e79360616209.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9481ef89_6041_4653_ab67_f6419f51f29c
ELIN-762174-2017 | EL-503412-2017 | 2/23/2017 1:09:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #DB_2_.png ELECTRICAL RACEWAY IMPROPERLY INSTALLED AND SUBJECT TO MECHANICAL | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | DB_2_.png | file://x:/photopub/docs/0000000562/82e4b960-ddec-42c6-9826-a4158c8fabdb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5819e435_4549_4cec_8b62_bba4bddd2501
GAIN-793768-2017 | GA-521801-2017 | 4/13/2017 8:46:11 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Vent_pipe.png The as-found-condition is that a section of plastic venting serving a furnace is not rated to S636 standards for flue gas. The potential hazard is that the vent will degrade over time and allow harmful products of combustion such as carbon monoxide into an occupied space. | 3 | Unapproved venting material | Vent_pipe.png | file://x:/photopub/docs/0000000587/b35249df-1cf3-44d6-81fe-65810c976cec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1412c58f_1311_480c_a944_4473c3d2582c
ELIN-772765-2017 | UW-510254-2017 | 3/10/2017 11:04:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | #Storage_in_electrical_room1.png,Storage_in_electrical_room2.png,Storage_in_electrical_room3.png,Storage_in_electrical_room4.png,Storage_in_electrical_room5.png,Storage_in_electrical_room6.png,Storage_in_electrical_room7.png,Storage_in_electrical_room8.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Storage_in_electrical_room3.png | file://x:/photopub/docs/0000000569/04d0ae9e-fa42-4449-9726-1bc55d3dca3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9481ef89_6041_4653_ab67_f6419f51f29c
ELIN-772765-2017 | UW-510254-2017 | 3/10/2017 11:04:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | #Storage_in_electrical_room1.png,Storage_in_electrical_room2.png,Storage_in_electrical_room3.png,Storage_in_electrical_room4.png,Storage_in_electrical_room5.png,Storage_in_electrical_room6.png,Storage_in_electrical_room7.png,Storage_in_electrical_room8.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Storage_in_electrical_room1.png | file://x:/photopub/docs/0000000569/f6c92ceb-2c46-4f79-a06f-6b748574b229.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9481ef89_6041_4653_ab67_f6419f51f29c
ELIN-772765-2017 | UW-510254-2017 | 3/10/2017 11:04:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | #Storage_in_electrical_room1.png,Storage_in_electrical_room2.png,Storage_in_electrical_room3.png,Storage_in_electrical_room4.png,Storage_in_electrical_room5.png,Storage_in_electrical_room6.png,Storage_in_electrical_room7.png,Storage_in_electrical_room8.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Storage_in_electrical_room6.png | file://x:/photopub/docs/0000000569/98c709f6-90ab-4bfd-85ce-d21884deba46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9481ef89_6041_4653_ab67_f6419f51f29c
ELIN-772765-2017 | UW-510254-2017 | 3/10/2017 11:04:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | #Storage_in_electrical_room1.png,Storage_in_electrical_room2.png,Storage_in_electrical_room3.png,Storage_in_electrical_room4.png,Storage_in_electrical_room5.png,Storage_in_electrical_room6.png,Storage_in_electrical_room7.png,Storage_in_electrical_room8.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Storage_in_electrical_room5.png | file://x:/photopub/docs/0000000569/df6e5fb6-9f81-4289-b2a2-fadc940253c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9481ef89_6041_4653_ab67_f6419f51f29c
GAIN-803629-2017 | GA-435374-2016 | 4/26/2017 2:13:06 PM | ASSESS: GA: Final | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | #Fortis_Tag2.png The as found condition was the gas utility attended an emergency call out and discovered high concentrations of natural gas inside a residential structure, verified by the meter dial continuously turning. The as found hazard is natural gas concentrations inside a structure can lead to explosion, potentially resulting in catastrophic damage or injury to participants. | 0 | No Created Hazard Identified | Fortis_Tag2.png | file://x:/photopub/docs/0000000591/082cdf72-0475-4a39-ae9c-a0acc80d4827.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__350b5acd_2939_440b_b6df_bb419efd36d2
GAIN-800299-2017 | GA-523573-2017 | 4/26/2017 10:33:04 AM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 4 | #BBQ.png Built in style BBQ installed in a wood frame enclosure. Hot surfaces of BBQ are in direct contact with combustibles as well as several inches away from vinyl siding. Manufacture requires minimum 24" clearance to combustibles. High potential for fire hazard from excessive heat contacting the wooden structure. More pictures of BBQ installation and rest of inspected appliances attached to permit | 3 | Clearance to combustible not met | BBQ.png | file://x:/photopub/docs/0000000591/9298e5e7-11a9-4377-8fbe-f65be18c69c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcb373b0_f5e0_4739_987f_a0d4c5122a4b
ELIN-762860-2017 | EL-504363-2017 | 3/8/2017 12:59:57 PM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Damaged_weatherproof_in-use_cover_.png A damaged weatherproof in-use cover on a GFCI outlet for a temporary construction service. This is a shock hazard condition. 120 Volt. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Damaged_weatherproof_in-use_cover_.png | file://x:/photopub/docs/0000000568/e512dd7c-9a5d-481a-a895-85785d1abf5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d074b886_c67f_48b5_a481_efd580d6d79c
GAUP-788496-2017 | UW-518844-2017 | 4/3/2017 6:18:27 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | #Dispenser_kiosk1.png,Dispenser_kiosk2.png,Dispenser_kiosk3.png,Dispenser_kiosk4.png | 0 | No Created Hazard Identified | Dispenser_kiosk2.png | file://x:/photopub/docs/0000000581/8b50cc8c-cf66-47f2-8edd-2807d0d1429c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94cef28d_84c2_4dfc_8f3c_aea2ab794410
GAUP-788496-2017 | UW-518844-2017 | 4/3/2017 6:18:27 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | #Dispenser_kiosk1.png,Dispenser_kiosk2.png,Dispenser_kiosk3.png,Dispenser_kiosk4.png | 0 | No Created Hazard Identified | Dispenser_kiosk1.png | file://x:/photopub/docs/0000000581/50f06e28-f1ff-45df-855f-ac61bc0373ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94cef28d_84c2_4dfc_8f3c_aea2ab794410
GAUP-788496-2017 | UW-518844-2017 | 4/3/2017 6:18:27 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | #Dispenser_kiosk1.png,Dispenser_kiosk2.png,Dispenser_kiosk3.png,Dispenser_kiosk4.png | 0 | No Created Hazard Identified | Dispenser_kiosk3.png | file://x:/photopub/docs/0000000581/b6581c0f-1bb4-4d95-aecc-380e8bab27a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94cef28d_84c2_4dfc_8f3c_aea2ab794410
GAUP-788496-2017 | UW-518844-2017 | 4/3/2017 6:18:27 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | #Dispenser_kiosk1.png,Dispenser_kiosk2.png,Dispenser_kiosk3.png,Dispenser_kiosk4.png | 0 | No Created Hazard Identified | Dispenser_kiosk4.png | file://x:/photopub/docs/0000000581/a60b4280-a5c2-4f07-bd36-fd9ee8478e1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94cef28d_84c2_4dfc_8f3c_aea2ab794410
GAIN-776443-2017 | GA-443524-2016 | 3/27/2017 5:15:31 AM | ASSESS: GA: Final | png | #asFound Vent limiter installed inside stud space. | GA082 | Vent limiter style regulator not installed in a ventilated space | 3 | 3 | #Vent_limiter.png Certain natural gas systems at residential sites are delivered at a higher pressure (2 psig) by the gas utility. These systems require a regulator to be installed to drop the pressure from 2 psig to 1/4 psig for the natural gas appliances to function properly. Due to the advances in technology we have allowed a 2psig-1/4 psig regulators to release gas in a controlled manner by way of a vent limiter due to a failure of the diaphragm, allowing only a prescribed (2.5 ft3) amount of gas through an orifice only if the space it is released into is a ventilated space. These style of regulators are common in residential applications and allow the contractor to not have to vent to outdoors. In event of the failure of the diaphragm the gas released could build up in the stud space and cause either injury or property damage if it were to ignite. | 3 | Vent limiter style regulator not installed in a ventilated space | Vent_limiter.png | file://x:/photopub/docs/0000000581/e909f67c-dba2-472f-9ada-f300cc08f7ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6945056c_fa7d_4232_9f37_0b5d623a1a14
ELIN-787618-2017 | EL-518393-2017 | 4/4/2017 9:59:07 AM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #Load_center.png Grounding conductor terminated to neutral bar in load center and not service disconnect. Neutral bar had no provision for bonding jumper installed. Improper grounding of the service could lead to an improper path of amperage during a fault causing shock risk. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Load_center.png | file://x:/photopub/docs/0000000582/36e722cc-47e7-40b8-b075-4b937e4c1188.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27c5164c_dcff_4ac3_8149_434bc6fb8cb4
GAHE-794620-2017 | HE-522334-2017 | 4/12/2017 10:19:52 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | #Underground.png,Underground2.png,Nopaint.png Fence post was installed by neighbour. Neighbour hit gas line with shovel and caused leak. Gas Line has been isolated but not capped. Someone can easily open gas valve and cause a leak with a possibility of a propane gas explosion. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Underground.png | file://x:/photopub/docs/0000000585/a04c4b11-92e9-4d30-be7b-a836896fd07a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d51ee63b_f792_4093_8044_469af8c98701
GAHE-794620-2017 | HE-522334-2017 | 4/12/2017 10:19:52 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound Or swing joint | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | #Underground.png,Underground2.png,Nopaint.png Fence post was installed by neighbour. Neighbour hit gas line with shovel and caused leak. Gas Line has been isolated but not capped. Someone can easily open gas valve and cause a leak with a possibility of a propane gas explosion. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Nopaint.png | file://x:/photopub/docs/0000000585/e46ad097-fd31-4671-ac6e-63b97dfa2169.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d51ee63b_f792_4093_8044_469af8c98701
GAHE-794620-2017 | HE-522334-2017 | 4/12/2017 10:19:52 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound Tiny hole on pipe | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | #Underground.png,Underground2.png,Nopaint.png Fence post was installed by neighbour. Neighbour hit gas line with shovel and caused leak. Gas Line has been isolated but not capped. Someone can easily open gas valve and cause a leak with a possibility of a propane gas explosion. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Underground2.png | file://x:/photopub/docs/0000000585/8ca35745-529a-44f3-a81d-e6da896330aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d51ee63b_f792_4093_8044_469af8c98701
GAHE-764863-2017 | HE-505650-2017 | 2/27/2017 7:45:44 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA064 | Gas leak readily detectable, able to pinpoint and isolate at source | 4 | 4 | #Lockout.png,Area_of_leak.png,Point_of_origin.png Gas leak detected around a riser from an underground gas line. Owner did not isolate gas line. Gas still leaking from 60PSI piping. Failure to isolate line could cause a gas explosion from source of leak. | 4 | Gas leak readily detectable, able to pinpoint and isolate at source | Area_of_leak.png | file://x:/photopub/docs/0000000563/0371ad23-e284-48c8-824e-f937a2ed0500.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b2eb0ea0_f3e3_4245_b38e_90d06f8f3464
GAHE-764863-2017 | HE-505650-2017 | 2/27/2017 7:45:44 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound 60psi gas leaking | GA064 | Gas leak readily detectable, able to pinpoint and isolate at source | 4 | 4 | #Lockout.png,Area_of_leak.png,Point_of_origin.png Gas leak detected around a riser from an underground gas line. Owner did not isolate gas line. Gas still leaking from 60PSI piping. Failure to isolate line could cause a gas explosion from source of leak. | 4 | Gas leak readily detectable, able to pinpoint and isolate at source | Point_of_origin.png | file://x:/photopub/docs/0000000563/b284ce89-6162-4d02-973d-a9cf9d91d8a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b2eb0ea0_f3e3_4245_b38e_90d06f8f3464
PRIN-782206-2017 | PR-511560-2017 | 3/30/2017 9:11:49 AM | ASSESS: PR IN: Acceptance | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | #Evacuation_drive_designated_batteries.png At the time of inspection, batteries used to start the evacuation drive engine were not designated to that system. The evacuation drive engine may not be be started in the event of a power outage, if designated batteries are not installed . | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Evacuation_drive_designated_batteries.png | file://x:/photopub/docs/0000000578/d408483c-2618-4453-9016-a6fa5e6e599d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__869bba95_766e_495a_ba7e_9f5938d1c877
ELHE-808987-2017 | HE-530006-2017 | 4/26/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL046 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to general public. | 5 | 5 | #Open_storage_of_lead_acid_batteries1.png,Open_storage_of_lead_acid_batteries2.png Lead acid batteries are stored in an area that is not sealed and vented from the rest of the house. Accidental contact could occur resulting in shock injury. | 5 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to general public. | Open_storage_of_lead_acid_batteries1.png | file://x:/photopub/docs/0000000597/581ca450-c8a6-47cf-98b8-203a4665c457.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a85ad699_dff9_4fca_8ee3_c8b9a470ea36
ELIN-775473-2017 | EL-497636-2017 | 3/21/2017 12:08:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #Meterbase_Conductors.png A 200 amp 600 volt 3 phase service has been installed with conductors that are only rated for 180 amps. This poses a shock hazard to persons and a risk of damage to the equipment has these cable could be overloaded, and they are not rated for the service size installed. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Meterbase_Conductors.png | file://x:/photopub/docs/0000000574/13c81a83-1dbb-4c8f-a375-4783fac55723.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6afceeb7_c14b_426d_9457_931d7be499ec
GAHE-764863-2017 | HE-505650-2017 | 2/27/2017 7:45:44 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA064 | Gas leak readily detectable, able to pinpoint and isolate at source | 4 | 4 | #Lockout.png,Area_of_leak.png,Point_of_origin.png Gas leak detected around a riser from an underground gas line. Owner did not isolate gas line. Gas still leaking from 60PSI piping. Failure to isolate line could cause a gas explosion from source of leak. | 4 | Gas leak readily detectable, able to pinpoint and isolate at source | Lockout.png | file://x:/photopub/docs/0000000563/ba6ab754-7fd7-41fb-8b70-a7e7210b3bcb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b2eb0ea0_f3e3_4245_b38e_90d06f8f3464
BPVOP-780258-2017 | 4084931 | 3/22/2017 10:50:37 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Boiler_.png A disconnecting means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in the event of an emergency. I found that there was no remote shutdown switch provided for this hot water heating boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_.png | file://x:/photopub/docs/0000000575/2184d2f2-5c5f-4dfa-977c-f2e2f823c235.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__35103919_8603_4e5e_93ef_c5ee791b5db6
BPVIN-770514-2017 | BPV-508856-2017 | 3/21/2017 5:21:53 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 4 | #no_pressure_relief_device_.png Every pressure retaining component of a regulated equipment or pressure piping must be provided with a suitable pressure relief device in order to protect from over pressurization and possible rupture. I could not find a the pressure relief device on a pressure vessel that was found pressurized up to 125 PSIG. Potential exists for an incident due to a missing overpressure protection device. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | no_pressure_relief_device_.png | file://x:/photopub/docs/0000000575/f549089a-5c66-49e4-9994-eeea46368043.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a79677f_5578_430a_9e5f_9e25e4ea6362
BPVOP-767177-2017 | 2293065 | 3/2/2017 9:57:50 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP218 | 5.1.2 Validation: work performed - Maintenance procedures are not documented | 2 | 2 | #nameplate_and_operaztords_certs1.png,nameplate_and_operaztords_certs2.png,nameplate_and_operaztords_certs3.png | 2 | 5.1.2 Validation: work performed - Maintenance procedures are not documented | nameplate_and_operaztords_certs3.png | file://x:/photopub/docs/0000000565/284b8b3d-f87a-4d24-a746-76bf56871941.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcad6800_a60a_4407_9b02_dcd38e1967ab
BPVOP-767177-2017 | 2293065 | 3/2/2017 9:57:50 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP218 | 5.1.2 Validation: work performed - Maintenance procedures are not documented | 2 | 2 | #nameplate_and_operaztords_certs1.png,nameplate_and_operaztords_certs2.png,nameplate_and_operaztords_certs3.png | 2 | 5.1.2 Validation: work performed - Maintenance procedures are not documented | nameplate_and_operaztords_certs2.png | file://x:/photopub/docs/0000000565/33250b1e-5a47-467a-b958-e10428a7fe57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcad6800_a60a_4407_9b02_dcd38e1967ab
BPVOP-767177-2017 | 2293065 | 3/2/2017 9:57:50 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP218 | 5.1.2 Validation: work performed - Maintenance procedures are not documented | 2 | 2 | #nameplate_and_operaztords_certs1.png,nameplate_and_operaztords_certs2.png,nameplate_and_operaztords_certs3.png | 2 | 5.1.2 Validation: work performed - Maintenance procedures are not documented | nameplate_and_operaztords_certs1.png | file://x:/photopub/docs/0000000565/677e2277-6a34-423c-88c6-a57f3c959d43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcad6800_a60a_4407_9b02_dcd38e1967ab
BPVOP-784254-2017 | 3593172 | 3/28/2017 1:24:45 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound Safety relief device servicing and testing is non compliant to the CSA B51 requirements. | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_relief_valve_1.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_valve_1.png | file://x:/photopub/docs/0000000577/49b01ec1-7723-4199-920a-69001930cebe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58e83d2e_71f3_4aaf_a7ba_b16343a75a29
BPVOP-784268-2017 | 3593192 | 1/25/2017 1:41:57 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound Safety relief device servicing and testing is non compliant to the CSA B51 requirements. | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PSV_service_missing.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PSV_service_missing.png | file://x:/photopub/docs/0000000577/9a79dd2e-4361-4deb-b380-f58dd5b6e115.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a69e05c8_e06e_4738_9588_eda6b4a4cec3
ELIN-808991-2017 | EL-263507-2015 | 5/3/2017 6:20:00 PM | ASSESS: EL: Final | png | #asFound Microwave hood fan is installed on same circuit as kitchen counter receptacles. A separate branch circuit was not supplied for the microwave hood fan, the kitchen counter is not a 5-15R split receptacle. | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | #7.png The kitchen counter receptacles are not 5-15R split as required. The microwave hood fan is tired into this branch circuit. This creates a potential fire hazard as this branch circuit could become overloaded and create a fire in the dwelling. This is due to the thermal effects on the insulation of the conductors. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 7.png | file://x:/photopub/docs/0000000595/254910a2-e371-494f-9f77-cfe83d56f95e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55020fc2_07d6_4fdf_b35c_c21384117a85
ELIN-770952-2017 | EL-500603-2017 | 3/8/2017 10:37:28 AM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #Exposed_live_buss.png There are no panel fillers installed in. Sub distribution panel. Persons may come into accidental contact with live electrical equipment. | 4 | Installation Grounding; conductor is not continuous. | Exposed_live_buss.png | file://x:/photopub/docs/0000000570/7d047435-3a5a-43e9-ae67-a6dd0071646e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de2c38a3_de45_493c_a6b2_2d39ebe94051
GAIN-778974-2017 | GA-511421-2017 | 3/23/2017 1:32:20 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Return1.png,Return2.png Furnace installed on wooden base used for return air plenum to furnace. Wooden base could rot or not rated to support furnace | 3 | Appliance not installed according to installation instructions | Return1.png | file://x:/photopub/docs/0000000576/a2f45d9e-1ccd-40a8-b837-339694b89405.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44b0934f_3a40_4994_9f80_a08f0528dd32
GAIN-778974-2017 | GA-511421-2017 | 3/23/2017 1:32:20 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Return1.png,Return2.png Furnace installed on wooden base used for return air plenum to furnace. Wooden base could rot or not rated to support furnace | 3 | Appliance not installed according to installation instructions | Return2.png | file://x:/photopub/docs/0000000576/08db14f3-4c7c-4f62-b1e7-a10c6bcefc60.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44b0934f_3a40_4994_9f80_a08f0528dd32
GAHE-770480-2017 | HE-468765-2016 | 4/21/2017 12:58:04 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA147 | Incorrect use of safety controls (Example: bypass limit) | 4 | 4 | #P650.png When propane is not being dispensed the internal safety control valve shall be in the closed position, the emergency shut off in place is a P650 safety shut off and is installed so when the cabinet door is shut it should close automatically, the P650 emergency shut off was in the open position when arrived for inspection because it was not installed in the correct position and propane was not being dispensed. This could lead to the uncontrolled release of propane if there was a catastrophic failure of the piping system. | 4 | Incorrect use of safety controls (Example: bypass limit) | P650.png | file://x:/photopub/docs/0000000590/7797744b-078b-4089-822c-ce36eddc6e94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02ccd7bb_a38e_4bab_9570_a06bd1dd15dd
GAIN-781822-2017 | GA-496409-2017 | 4/20/2017 7:35:25 PM | ASSESS: GA: Rough-In | png | #asFound Open gas lines for space heaters on patio. | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | #Open_gas_lines.png When leaving a site or appliance with a open ended gas line(s) that could accidentally cause the un-controlled release of gas it is the responsibility of the person(s) doing the regulated work to ensure that this line(s) are capped or plugged to prevent a hazardous situation, which could in turn lead to an explosion, property damage, injury or fire. | 5 | Open gas line connected to fuel supply (no cap/plug) | Open_gas_lines.png | file://x:/photopub/docs/0000000590/e1ca9ca2-e90e-48de-a5c2-5c4e6c47065f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a54fc3f2_4876_4cd1_a089_2958fdf35e89
ELHE-795840-2017 | HE-523195-2017 | 4/13/2017 4:36:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Made up on site unapproved electrical equipment used in a hazardous location where there is gas powered generator and the wiring is not approved for the use or location | EL214 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | 4 | 4 | #Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only1.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only2.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only3.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only4.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only5.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only6.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only7.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only8.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only9.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only10.png Found 120/240 volt single phase gas powered generator installed in an enclosed building structure space while there is regular dry type location electrical equipment (such as extension cords and unapproved non-co | 4 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only2.png | file://x:/photopub/docs/0000000587/6bb93b94-263f-48fc-81a4-0d0c6a70ae05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f179be25_3936_4139_80e6_4aa0db23245a
ELHE-795840-2017 | HE-523195-2017 | 4/13/2017 4:36:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Made up on site unapproved electrical equipment used in a hazardous location where there is gas powered generator and the wiring is not approved for the use or location | EL214 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | 4 | 4 | #Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only1.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only2.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only3.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only4.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only5.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only6.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only7.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only8.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only9.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only10.png Found 120/240 volt single phase gas powered generator installed in an enclosed building structure space while there is regular dry type location electrical equipment (such as extension cords and unapproved non-co | 4 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only3.png | file://x:/photopub/docs/0000000587/f8d56efb-edd3-4b9d-9756-304f0aacb177.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f179be25_3936_4139_80e6_4aa0db23245a
ELHE-795840-2017 | HE-523195-2017 | 4/13/2017 4:36:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Made up on site unapproved electrical equipment used in a hazardous location where there is gas powered generator and the wiring is not approved for the use or location. Approved installation and use instructions not complied with as required by manufacturer's approved installation and use instructions | EL214 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | 4 | 4 | #Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only1.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only2.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only3.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only4.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only5.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only6.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only7.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only8.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only9.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only10.png Found 120/240 volt single phase gas powered generator installed in an enclosed building structure space while there is regular dry type location electrical equipment (such as extension cords and unapproved non-co | 4 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only10.png | file://x:/photopub/docs/0000000587/d5a02b58-0201-42b4-a0b8-bf5ace23431c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f179be25_3936_4139_80e6_4aa0db23245a
BPVOP-804247-2017 | 4795486 | 4/27/2017 3:27:40 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRV.png Upon assessment of refrigeration system (214kW power rating with 505lbs of refrigerant R-22) has pressure relief valves those exceeded the required 5year interval for servicing or replacement. Failure to have pressure relief valve serviced or replaced as required may subject system to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressure boundary with rapid release of refrigerant and shooting/rocketing effect of flying object (caused by uncontrolled release of refrigerant) and depletion of oxygen caused by concentration of refrigerant in the vicinity may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRV.png | file://x:/photopub/docs/0000000592/1e2aa636-0ba3-4894-bc0a-25b53aeb56bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c2ad69d_3b55_492a_bff3_461766f9b142
BPVIN-804331-2017 | BPV-527440-2017 | 4/27/2017 4:13:28 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_Relief_Valve1.png,Pressure_Relief_Valve2.png Upon assessment of vessel (length-2.3m, diameter- 0.55) with Maximum Allowable Working Pressure (MAWP) of 200psig in a refrigeration system (214kW power rating with 505lbs of refrigerant R-22) has pressure relief valves those exceeded the required 5year interval for servicing or replacement. Failure to have pressure relief valve serviced or replaced as required may subject system to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressure boundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of refrigerant and shooting/rocketing effect of flying object (caused by uncontrolled release of refrigerant) and depletion of oxygen caused by concentration of refrigerant in the vicinity may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_Relief_Valve2.png | file://x:/photopub/docs/0000000592/04a4b964-a6d5-42a3-9be1-66f8ce82e6b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff71a99b_9830_42cf_b82b_26930d44eca6
BPVIN-804331-2017 | BPV-527440-2017 | 4/27/2017 4:13:28 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_Relief_Valve1.png,Pressure_Relief_Valve2.png Upon assessment of vessel (length-2.3m, diameter- 0.55) with Maximum Allowable Working Pressure (MAWP) of 200psig in a refrigeration system (214kW power rating with 505lbs of refrigerant R-22) has pressure relief valves those exceeded the required 5year interval for servicing or replacement. Failure to have pressure relief valve serviced or replaced as required may subject system to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressure boundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of refrigerant and shooting/rocketing effect of flying object (caused by uncontrolled release of refrigerant) and depletion of oxygen caused by concentration of refrigerant in the vicinity may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_Relief_Valve1.png | file://x:/photopub/docs/0000000592/56e49b2a-d01c-4d4b-b5b7-e965dc5f7ea0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff71a99b_9830_42cf_b82b_26930d44eca6
ELHE-802564-2017 | HE-526541-2017 | 4/25/2017 3:42:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png,A11.png 100A service overloaded with the addition of an electric furnace. This resulted in weakening and overheating of the meter base jaws. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A3.png | file://x:/photopub/docs/0000000591/d3e50415-ecfb-4234-9fcf-8008af887d19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c3ca0fe_133d_4511_a2b7_f66e0052a5a8
EDIN-804801-2017 | ED-459007-2016 | 4/27/2017 8:10:45 PM | ASSESS: ED IN: Construction Use | png | #asFound Main disconnect for elevator located in the elevator lobby | ED033 | Operating control installed contrary to the manufacturer instructions and/ or applicable Standards Contractor is not aware Risk Reg ED-02 | 3 | 3 | #Disconnect_2.png The main power disconnect is located in the elevator lobby. Also unable to locate the electrical disconnect for the elevator cab lighting. | 3 | Operating control installed contrary to the manufacturer instructions and/ or applicable Standards Contractor is not aware Risk Reg ED-02 | Disconnect_2.png | file://x:/photopub/docs/0000000592/5d98cde5-cebe-4321-815e-2cb80c60aa93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8d9100c_ed53_4a81_9eb2_038e28ccb4fc
BPVIN-785292-2017 | BPV-517094-2017 | 4/21/2017 10:28:19 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP014 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | 1 | 1 | #Clearances_.png,Clearances_.png | 1 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | Clearances_.png | file://x:/photopub/docs/0000000590/63c9f8b1-45c4-45e0-8c1c-c1821da32ab9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ee63366_4f48_42ff_aa4a_bb47135175ab
ELHE-802564-2017 | HE-526541-2017 | 4/25/2017 3:42:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png,A11.png 100A service overloaded with the addition of an electric furnace. This resulted in weakening and overheating of the meter base jaws. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A1.png | file://x:/photopub/docs/0000000591/0f447890-4131-4acd-9d85-b7a09deb6cf4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c3ca0fe_133d_4511_a2b7_f66e0052a5a8
ELHE-802564-2017 | HE-526541-2017 | 4/25/2017 3:42:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png,A11.png 100A service overloaded with the addition of an electric furnace. This resulted in weakening and overheating of the meter base jaws. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A8.png | file://x:/photopub/docs/0000000591/d74d4e2e-4151-4b17-b3dc-f713d6e4ab3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c3ca0fe_133d_4511_a2b7_f66e0052a5a8
ELHE-802564-2017 | HE-526541-2017 | 4/25/2017 3:42:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png,A11.png 100A service overloaded with the addition of an electric furnace. This resulted in weakening and overheating of the meter base jaws. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A10.png | file://x:/photopub/docs/0000000591/ec834afc-90e1-41f1-a6ee-c1c288066f00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c3ca0fe_133d_4511_a2b7_f66e0052a5a8
GAHE-791594-2017 | HE-520617-2017 | 4/7/2017 1:48:49 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 5 | #136_7.png Gas system full discharge relief regulator installed indoors in crawl space/basement and not vented safely to outdoors. Failure of the regulator could allow gas to escape into a confined occupied space. If a source of ignition were present, this could result in either a fire and or explosion. | 5 | Relief style regulator/device allowed to vent within building/confined space | 136_7.png | file://x:/photopub/docs/0000000584/49328635-c89a-48c5-8652-51ecb6d86856.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b289a68f_6e98_484b_8bf7_22f7362dd0f0
ELIN-765853-2017 | EL-408173-2016 | 3/3/2017 1:23:25 PM | ASSESS: EL: Final | png | #asFound Component label only attached to driver | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Led_driver_with_a_component_label.png Under counter lighting driver does not bear evidence of approval in accordance with BC safety authority information bulletin. equipment has not been approved or certified for use by the standard council of Canada, and the certification for fire in shock has not been determined | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Led_driver_with_a_component_label.png | file://x:/photopub/docs/0000000565/c1ed3c86-c593-4788-bb99-3c6315bb9225.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ccb6fe_5159_472b_8b1e_f5b6848b4aeb
BPVOP-785379-2017 | 4998469 | 3/29/2017 12:49:31 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | #Location.png The outdoor location of this pressure vessel exposes it to possible contact from heavy equipment. It is inaccessible for inspection due to being buried in Ice and snow as well as hog fuel. This also means that any liquid build up in the pressure vessel cannot be drained.The pressure vessel is also covered in rust spots. I could not see the name plate to see the minimum designed metal temperature of the receiver but I would presume being outdoors it has been exposed to temperatures below its minimum temperature. The above mentioned items can lead to failure of pressure vessel. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Location.png | file://x:/photopub/docs/0000000584/983c67e7-7a13-4667-933e-d210959e5b1e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6450b1ef_ae57_42e1_886a_9a6844f7fca7
ELIN-801083-2017 | EL-404194-2016 | 4/24/2017 | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Main_Panel1.png,Main_Panel2.png,Main_Panel3.png,Sub_panel_1.png,Sub_panel_2.png Arc-fault protection is required on new branch circuits for receptacles 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation in an existing single family dwelling, new 15 amp circuits for receptacles in the bedrooms and common area of the lower floor were installed without arc-fault protection. If a series or parallel arc was to occur in one of the branch circuits, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and property. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Main_Panel1.png | file://x:/photopub/docs/0000000591/a885aeed-13ee-433d-8a8a-29eb1ce5bbb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8277e66_7b11_49e8_bda1_ee9462b76bb7
ELIN-767773-2017 | EL-497723-2017 | 3/6/2017 4:32:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound -main 200amp consumer service cable passing through wood floor plate and within 32mm of edge of framing. | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Pic11.png,Pic12.png -Main consumer service cable is not mechanically or electrically protected which may lead to electrical shock or fire hazards. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Pic11.png | file://x:/photopub/docs/0000000569/cdbf5858-3899-4595-b802-e11d2d36788b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__871bc71f_ea45_4d91_9004_e8758f6dc628
ELIN-767773-2017 | EL-497723-2017 | 3/6/2017 4:32:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Pic11.png,Pic12.png -Main consumer service cable is not mechanically or electrically protected which may lead to electrical shock or fire hazards. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Pic12.png | file://x:/photopub/docs/0000000569/0075a0ee-64a0-4acc-843e-be96d1d22b6c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__871bc71f_ea45_4d91_9004_e8758f6dc628
BPVIN-781080-2017 | BPV-477725-2016 | 3/23/2017 12:39:24 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Boiler_room_entrance.png Code required emergency shut down switch which will allow the boiler to be shut down without entering the boiler room in an emergency was not installed. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_room_entrance.png | file://x:/photopub/docs/0000000577/2f1a66b7-f0f2-4823-abd9-0e60bb1a3aa3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c57ba4bc_091f_430b_aa52_9f501bc99241
ELIN-809442-2017 | EL-504646-2017 | 5/5/2017 12:56:42 PM | ASSESS: EL: Final | png | #asFound | EL274 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | 3 | 3 | #Patio_Lights1.png,Patio_Lights2.png A 15 amp 120 volt light fixture is located within a meter of the Hot Tub and can be easily touched or grabbed by those using the Hot Tub. This fixture is not GFCI protected and poses a shock hazard to persons. | 3 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | Patio_Lights1.png | file://x:/photopub/docs/0000000597/4c4bee82-811d-436e-a9bc-51176ce8fe0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__185b48d1_9ac6_4052_97f9_9433312e6b8d
ELIN-809442-2017 | EL-504646-2017 | 5/5/2017 12:56:42 PM | ASSESS: EL: Final | png | #asFound | EL274 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | 3 | 3 | #Patio_Lights1.png,Patio_Lights2.png A 15 amp 120 volt light fixture is located within a meter of the Hot Tub and can be easily touched or grabbed by those using the Hot Tub. This fixture is not GFCI protected and poses a shock hazard to persons. | 3 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | Patio_Lights2.png | file://x:/photopub/docs/0000000597/9a7153f9-d381-4451-909e-ca29c0337f8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__185b48d1_9ac6_4052_97f9_9433312e6b8d
ELIN-809444-2017 | EL-504645-2017 | 5/5/2017 12:35:22 PM | ASSESS: EL: Final | png | #asFound | EL274 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | 3 | 3 | #Patio_Fixture.png A 15 amp 120 volt light fixture is located within a meter of the Hot Tub and can be easily touched or grabbed by those using the Hot Tub. This fixture is not GFCI protected and poses a shock hazard to persons. | 3 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | Patio_Fixture.png | file://x:/photopub/docs/0000000597/f9e0daba-4771-43db-8390-d6492df65b52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f85b1e0_3343_4edb_9d64_9e5ec82e892b
ELIN-809439-2017 | EL-504641-2017 | 5/5/2017 1:11:47 PM | ASSESS: EL: Final | png | #asFound | EL274 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | 3 | 3 | #Deck_Lights.png A 15 amp 120 volt light fixture is located within a meter of the Hot Tub and can be easily touched or grabbed by those using the Hot Tub. This fixture is not GFCI protected and poses a shock hazard to persons. | 3 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | Deck_Lights.png | file://x:/photopub/docs/0000000597/9da03314-705e-4d9a-8abc-f5404d7f8fec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d31807d3_4611_4757_aad5_e6c43a2b91c1
GAIN-802055-2017 | GA-419839-2016 | 4/28/2017 1:50:44 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Vent_termination_mech_air_suply1.png,Vent_termination_mech_air_suply2.png -Furnace venting is terminated less than 6 feet away from fresh air intake to furnace. This could result in some of the flue gases being drawn into the air supply and exposing occupants to the products of combustion. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_termination_mech_air_suply1.png | file://x:/photopub/docs/0000000592/6cd2822c-9e1c-4c77-8967-3154900892d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__685901da_71bf_4581_905a_486935e31244
GAHE-776144-2017 | HE-512222-2017 | 3/16/2017 9:49:17 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 5 | #Furnace_vent1.png,Furnace_vent2.png Condensate was leaking from 2" exhaust fitting in mechanical room on furnace, when pulled on fitting, pipe came dislodged, furnace was in operation. Products of combustion released in dwelling while workers present can make workers sick | 5 | Special venting system not glued or connected as per certified instructions | Furnace_vent2.png | file://x:/photopub/docs/0000000572/80d9de52-343b-42b3-ae13-f4991eedffb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__391be4fe_bb98_4ca2_b8ca_cc9830a63d01
GAHE-776144-2017 | HE-512222-2017 | 3/16/2017 9:49:17 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 5 | #Furnace_vent1.png,Furnace_vent2.png Condensate was leaking from 2" exhaust fitting in mechanical room on furnace, when pulled on fitting, pipe came dislodged, furnace was in operation. Products of combustion released in dwelling while workers present can make workers sick | 5 | Special venting system not glued or connected as per certified instructions | Furnace_vent1.png | file://x:/photopub/docs/0000000572/4d2dbc10-d77f-44fd-87d6-961bbf0c0b7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__391be4fe_bb98_4ca2_b8ca_cc9830a63d01
ELIN-801083-2017 | EL-404194-2016 | 4/24/2017 | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Main_Panel1.png,Main_Panel2.png,Main_Panel3.png,Sub_panel_1.png,Sub_panel_2.png Arc-fault protection is required on new branch circuits for receptacles 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation in an existing single family dwelling, new 15 amp circuits for receptacles in the bedrooms and common area of the lower floor were installed without arc-fault protection. If a series or parallel arc was to occur in one of the branch circuits, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and property. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Sub_panel_1.png | file://x:/photopub/docs/0000000591/b7cf092b-2bfd-4580-bfb2-d2599d955515.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8277e66_7b11_49e8_bda1_ee9462b76bb7
ELIN-801083-2017 | EL-404194-2016 | 4/24/2017 | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Main_Panel1.png,Main_Panel2.png,Main_Panel3.png,Sub_panel_1.png,Sub_panel_2.png Arc-fault protection is required on new branch circuits for receptacles 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation in an existing single family dwelling, new 15 amp circuits for receptacles in the bedrooms and common area of the lower floor were installed without arc-fault protection. If a series or parallel arc was to occur in one of the branch circuits, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and property. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Sub_panel_2.png | file://x:/photopub/docs/0000000591/b91ca774-86f9-41bd-9f4f-6e4d69730191.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8277e66_7b11_49e8_bda1_ee9462b76bb7
ELIN-801083-2017 | EL-404194-2016 | 4/24/2017 | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Main_Panel1.png,Main_Panel2.png,Main_Panel3.png,Sub_panel_1.png,Sub_panel_2.png Arc-fault protection is required on new branch circuits for receptacles 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation in an existing single family dwelling, new 15 amp circuits for receptacles in the bedrooms and common area of the lower floor were installed without arc-fault protection. If a series or parallel arc was to occur in one of the branch circuits, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and property. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Main_Panel2.png | file://x:/photopub/docs/0000000591/f55986de-beb6-44c2-b788-c6340731c8fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8277e66_7b11_49e8_bda1_ee9462b76bb7
ELIN-779011-2017 | EL-513741-2017 | 3/21/2017 4:03:15 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Branch_circuits__branch_circuits1.png,Branch_circuits__branch_circuits2.png,Branch_circuits__branch_circuits3.png,Branch_circuits__branch_circuits4.png Branch circuit wiring is unsafe for example extension cords are being used for a permanent installation creating a fire hazard and possible shock hazard | 4 | Conductors, Misuse of flexible cords. | Branch_circuits__branch_circuits3.png | file://x:/photopub/docs/0000000574/619cd3a1-5d6b-42ca-b9f3-930317c6001f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0b23973_1a96_404e_a277_01f4a9a3af46
ELIN-779011-2017 | EL-513741-2017 | 3/21/2017 4:03:15 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Branch_circuits__branch_circuits1.png,Branch_circuits__branch_circuits2.png,Branch_circuits__branch_circuits3.png,Branch_circuits__branch_circuits4.png Branch circuit wiring is unsafe for example extension cords are being used for a permanent installation creating a fire hazard and possible shock hazard | 4 | Conductors, Misuse of flexible cords. | Branch_circuits__branch_circuits1.png | file://x:/photopub/docs/0000000574/5edc2d6e-9379-4c05-bac3-406ce7ef9f83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0b23973_1a96_404e_a277_01f4a9a3af46
ELIN-779011-2017 | EL-513741-2017 | 3/21/2017 4:03:15 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Branch_circuits__branch_circuits1.png,Branch_circuits__branch_circuits2.png,Branch_circuits__branch_circuits3.png,Branch_circuits__branch_circuits4.png Branch circuit wiring is unsafe for example extension cords are being used for a permanent installation creating a fire hazard and possible shock hazard | 4 | Conductors, Misuse of flexible cords. | Branch_circuits__branch_circuits2.png | file://x:/photopub/docs/0000000574/8475a45e-34f6-4024-923a-4368d48e2ec2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0b23973_1a96_404e_a277_01f4a9a3af46
ELIN-779011-2017 | EL-513741-2017 | 3/21/2017 4:03:15 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Branch_circuits__branch_circuits1.png,Branch_circuits__branch_circuits2.png,Branch_circuits__branch_circuits3.png,Branch_circuits__branch_circuits4.png Branch circuit wiring is unsafe for example extension cords are being used for a permanent installation creating a fire hazard and possible shock hazard | 4 | Conductors, Misuse of flexible cords. | Branch_circuits__branch_circuits4.png | file://x:/photopub/docs/0000000574/d62e5b5c-1af4-4be8-930d-fe6ac2697ceb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0b23973_1a96_404e_a277_01f4a9a3af46
GAIN-802055-2017 | GA-419839-2016 | 4/28/2017 1:50:44 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Vent_termination_mech_air_suply1.png,Vent_termination_mech_air_suply2.png -Furnace venting is terminated less than 6 feet away from fresh air intake to furnace. This could result in some of the flue gases being drawn into the air supply and exposing occupants to the products of combustion. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_termination_mech_air_suply2.png | file://x:/photopub/docs/0000000592/31fce07f-7f5e-41ff-b3dd-ac1160bf4385.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__685901da_71bf_4581_905a_486935e31244
ELIN-801083-2017 | EL-404194-2016 | 4/24/2017 | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Main_Panel1.png,Main_Panel2.png,Main_Panel3.png,Sub_panel_1.png,Sub_panel_2.png Arc-fault protection is required on new branch circuits for receptacles 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation in an existing single family dwelling, new 15 amp circuits for receptacles in the bedrooms and common area of the lower floor were installed without arc-fault protection. If a series or parallel arc was to occur in one of the branch circuits, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and property. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Main_Panel3.png | file://x:/photopub/docs/0000000591/cf72874f-0a69-492b-89c6-8da3ec81350d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8277e66_7b11_49e8_bda1_ee9462b76bb7
AMOP-793342-2017 | 3765215 | 4/11/2017 7:18:24 AM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Archway_brackets_corroded1.png,Archway_brackets_corroded2.png,Archway_brackets_corroded3.png,Archway_brackets_corroded4.png Archway light brackets, over the ride flumes, are corroded. Archway could collapse onto guests | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Archway_brackets_corroded4.png | file://x:/photopub/docs/0000000585/dd52bced-e4b7-43bd-afc1-04b7f02533ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08ec8e59_7b6e_42b0_9168_3658a77b4890
AMOP-793342-2017 | 3765215 | 4/11/2017 7:18:24 AM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Archway_brackets_corroded1.png,Archway_brackets_corroded2.png,Archway_brackets_corroded3.png,Archway_brackets_corroded4.png Archway light brackets, over the ride flumes, are corroded. Archway could collapse onto guests | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Archway_brackets_corroded2.png | file://x:/photopub/docs/0000000585/178e5a11-7bc1-43c4-a2e5-9fb6a3f43bd6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08ec8e59_7b6e_42b0_9168_3658a77b4890
GAIN-795575-2017 | GA-519266-2017 | 4/26/2017 1:46:36 PM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #2336_3.png Lack of the required clearance between type C vent and combustible material( PCV vent pipe) Possible fire hazard if the combustible material reaches its ignition temperature. In this instance, the intake venting could melt reducing available combustion air to the furnace causing a fuel rich condition,this could result in the production of carbon monoxide. | 3 | Non compliant Type C Vent clearance | 2336_3.png | file://x:/photopub/docs/0000000592/e40185be-9f60-47de-a532-6dba0df27063.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bfd9df1_3f03_4589_8d4f_2fcfa3e042d7
ELIN-773285-2017 | UW-510534-2017 | 3/8/2017 12:34:03 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Devices_and_Connectors_not_rated_for_Al1.png,Devices_and_Connectors_not_rated_for_Al2.png,Devices_and_Connectors_not_rated_for_Al3.png,Devices_and_Connectors_not_rated_for_Al4.png Electrical equipment must be approved for use when connected to aluminum electrical conductors. This is required because aluminum conductors expand more than copper conductors and a non-conductive oxide can form on the aluminum conductor when exposed to air. Loose connections and oxidization can create more resistance to the current flow which can cause the equipment to overheat and fail. During a hazard assessment in a single family dwelling, receptacles and switches rated for copper use only were found connected to aluminum conductors. Also, non-approved wire connectors were found for connecting copper and aluminum conductors together. The use of the non-approved devices and connectors at this dwelling has the potential to create equipment damage and a fire hazard to persons and property. | 3 | Conductors Equipment is not approved for the specific use. | Devices_and_Connectors_not_rated_for_Al4.png | file://x:/photopub/docs/0000000570/e82dff33-a3f8-4ccc-8928-ee3fb254186f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c9812dc_c5fc_4419_8357_ab16d5928365
ELIN-773285-2017 | UW-510534-2017 | 3/8/2017 12:34:03 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Devices_and_Connectors_not_rated_for_Al1.png,Devices_and_Connectors_not_rated_for_Al2.png,Devices_and_Connectors_not_rated_for_Al3.png,Devices_and_Connectors_not_rated_for_Al4.png Electrical equipment must be approved for use when connected to aluminum electrical conductors. This is required because aluminum conductors expand more than copper conductors and a non-conductive oxide can form on the aluminum conductor when exposed to air. Loose connections and oxidization can create more resistance to the current flow which can cause the equipment to overheat and fail. During a hazard assessment in a single family dwelling, receptacles and switches rated for copper use only were found connected to aluminum conductors. Also, non-approved wire connectors were found for connecting copper and aluminum conductors together. The use of the non-approved devices and connectors at this dwelling has the potential to create equipment damage and a fire hazard to persons and property. | 3 | Conductors Equipment is not approved for the specific use. | Devices_and_Connectors_not_rated_for_Al1.png | file://x:/photopub/docs/0000000570/bd3941ce-03bf-4024-911e-4e991a640318.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c9812dc_c5fc_4419_8357_ab16d5928365
ELIN-773285-2017 | UW-510534-2017 | 3/8/2017 12:34:03 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Devices_and_Connectors_not_rated_for_Al1.png,Devices_and_Connectors_not_rated_for_Al2.png,Devices_and_Connectors_not_rated_for_Al3.png,Devices_and_Connectors_not_rated_for_Al4.png Electrical equipment must be approved for use when connected to aluminum electrical conductors. This is required because aluminum conductors expand more than copper conductors and a non-conductive oxide can form on the aluminum conductor when exposed to air. Loose connections and oxidization can create more resistance to the current flow which can cause the equipment to overheat and fail. During a hazard assessment in a single family dwelling, receptacles and switches rated for copper use only were found connected to aluminum conductors. Also, non-approved wire connectors were found for connecting copper and aluminum conductors together. The use of the non-approved devices and connectors at this dwelling has the potential to create equipment damage and a fire hazard to persons and property. | 3 | Conductors Equipment is not approved for the specific use. | Devices_and_Connectors_not_rated_for_Al3.png | file://x:/photopub/docs/0000000570/0ec63d37-0a44-40f7-af16-21d548461399.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c9812dc_c5fc_4419_8357_ab16d5928365
BPVOP-810433-2017 | 3834043 | 5/11/2017 10:53:01 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 4 | #No_safety_relief_on_this_tank.png No safety relief device installed on this hot water storage tank per NBIC 1 4.7.3 .Every pressure retaining component of a regulated equipment must be provided with a suitable pressure relief device in order to protect the vessel from over pressurization and possible rupture. I could not locate a pressure relief device on this 500 Ltrs hot water Storage tank .Potential exists for an incident due to a missing overpressure protection device | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | No_safety_relief_on_this_tank.png | file://x:/photopub/docs/0000000599/5220dbb7-7eb8-4bec-9da3-2bf7c3511b68.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aae71643_031d_4f2c_a73c_5441503b7c86
ELHE-795444-2017 | HE-522939-2017 | 4/18/2017 12:34:11 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Subpanels1.png,Subpanels2.png Two energized 200 amp 120/240 volt electrical panels located inside an Electrical Room do not have the panel covers in place. This poses a shock hazard to personal accessing the electrical equipment and possible mechanical damage to the equipment itself. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Subpanels2.png | file://x:/photopub/docs/0000000587/bd60704a-cc2f-4075-8eba-523f585aa944.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cfd3648_2daf_4422_8aa7_047faad6247b
ELHE-795444-2017 | HE-522939-2017 | 4/18/2017 12:34:11 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Subpanels1.png,Subpanels2.png Two energized 200 amp 120/240 volt electrical panels located inside an Electrical Room do not have the panel covers in place. This poses a shock hazard to personal accessing the electrical equipment and possible mechanical damage to the equipment itself. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Subpanels1.png | file://x:/photopub/docs/0000000587/dd60b5bd-a008-4a29-9759-2bfb1a0aebed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cfd3648_2daf_4422_8aa7_047faad6247b
ELIN-813500-2017 | EL-524972-2017 | 5/10/2017 2:05:39 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound Lettrich all work performed by builder | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Work_performed1.png,Work_performed2.png,Metre_base__metre_base_back_fed_from_temporary_construction_service.png Builder has back fed from the temporary construction service to the perm infant metre base of a single-family dwelling under construction. Electrical hazards created by the builder include accidental contact of live exposed bus bar in the metre base and modification of the existing electrical installation. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Metre_base__metre_base_back_fed_from_temporary_construction_service.png | file://x:/photopub/docs/0000000599/36165410-9bfc-44e8-8df9-dc0f6832c8cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24f4f7fe_483e_4b20_baa9_6ffdf89ab3da
ELIN-813500-2017 | EL-524972-2017 | 5/10/2017 2:05:39 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound Square D 12 circuit combination load center-60 A | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Work_performed1.png,Work_performed2.png,Metre_base__metre_base_back_fed_from_temporary_construction_service.png Builder has back fed from the temporary construction service to the perm infant metre base of a single-family dwelling under construction. Electrical hazards created by the builder include accidental contact of live exposed bus bar in the metre base and modification of the existing electrical installation. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Work_performed2.png | file://x:/photopub/docs/0000000599/6f7196e6-e038-4023-93c3-66188939fe23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24f4f7fe_483e_4b20_baa9_6ffdf89ab3da
BPVIN-784189-2017 | BPV-516602-2017 | 3/28/2017 10:36:27 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | #Clearance_.png | 0 | No Created Hazard Identified | Clearance_.png | file://x:/photopub/docs/0000000577/b7a84857-d24f-4806-aa17-f42b00c78595.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5830358_7a8c_455a_9345_110c69982be8
BPVIN-733490-2017 | BPV-221544-2015 | 3/31/2017 10:46:35 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #No_lwco_flow_switch1.png,No_lwco_flow_switch2.png Each automatically fired hot water boiler shall be equipped with a low water fuel cut-off device to shut down the boiler in a low water event. I found no low water cut-off device or flow switch in lieu of a low water device on a 160psi hot water boiler. Potential exists for a low water incident due to lack safety devices. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_lwco_flow_switch1.png | file://x:/photopub/docs/0000000582/f2054e55-89e5-4503-ad61-f68f65aa01a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5dd69dfb_064a_4e63_a9d3_d05f4b843604
BPVIN-733490-2017 | BPV-221544-2015 | 3/31/2017 10:46:35 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #No_lwco_flow_switch1.png,No_lwco_flow_switch2.png Each automatically fired hot water boiler shall be equipped with a low water fuel cut-off device to shut down the boiler in a low water event. I found no low water cut-off device or flow switch in lieu of a low water device on a 160psi hot water boiler. Potential exists for a low water incident due to lack safety devices. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_lwco_flow_switch2.png | file://x:/photopub/docs/0000000582/01e7ca4b-857d-4ba5-b8ae-e6af8d558649.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5dd69dfb_064a_4e63_a9d3_d05f4b843604
GAIN-758506-2017 | GA-501976-2017 | 2/28/2017 2:31:00 PM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Combustion_air.png The as-found-condition is that the combustion air inlet for a high efficiency furnace terminates outside within 12 inches of finished grade. The potential hazard is that the combustion air inlet will be blocked by snow or other factors, causing the appliance to operate with limited or no combustion air. This could affect the combustion characteristics of the appliance and result in the production of harmful emissions such as carbon monoxide. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Combustion_air.png | file://x:/photopub/docs/0000000563/63aaeb2e-9f84-44e8-9adb-38dfeffc92ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47655b7e_7f58_482c_8314_2a03a8abc5e2
ELIN-775992-2017 | EL-464295-2016 | 3/16/2017 1:50:32 PM | ASSESS: EL: Final | png | #asFound LVT in wet location | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | #3.png LVT installed in a wet location. This is a shock hazard as the insulation will break down due to exposure to the environment. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3.png | file://x:/photopub/docs/0000000572/92bb97b1-35ea-47dd-a727-ec448470c217.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a9c2392_4cc7_4eab_8244_d1de2cfaf685
ELIN-794272-2017 | EL-521546-2017 | 4/13/2017 1:00:39 PM | ASSESS: EL: Final | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 4 | #Recessed_boxes1.png,Recessed_boxes2.png In an older mobile home, drywall has been installed over the original wall panel thereby leaving the device boxes recessed greater than the permitted 6mm without a box extender installed. This leaves a gap between the front edge of the box and the finished wall which could allow an electrical fire within the box to spread to the surrounding structure. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | Recessed_boxes1.png | file://x:/photopub/docs/0000000586/3fe64014-dfd1-4d9f-af34-cc9412f7f95c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8c063d4_7844_4522_8962_756c62374bb0
ELIN-794272-2017 | EL-521546-2017 | 4/13/2017 1:00:39 PM | ASSESS: EL: Final | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 4 | #Recessed_boxes1.png,Recessed_boxes2.png In an older mobile home, drywall has been installed over the original wall panel thereby leaving the device boxes recessed greater than the permitted 6mm without a box extender installed. This leaves a gap between the front edge of the box and the finished wall which could allow an electrical fire within the box to spread to the surrounding structure. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | Recessed_boxes2.png | file://x:/photopub/docs/0000000586/449dbaa2-aa7d-463f-994f-2b7e52f306f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8c063d4_7844_4522_8962_756c62374bb0
ELIN-813500-2017 | EL-524972-2017 | 5/10/2017 2:05:39 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound Electrical connection terminated on the load side of the main breaker | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Work_performed1.png,Work_performed2.png,Metre_base__metre_base_back_fed_from_temporary_construction_service.png Builder has back fed from the temporary construction service to the perm infant metre base of a single-family dwelling under construction. Electrical hazards created by the builder include accidental contact of live exposed bus bar in the metre base and modification of the existing electrical installation. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Work_performed1.png | file://x:/photopub/docs/0000000599/aa2e4b76-62b9-41ca-bab4-f17910b86d56.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24f4f7fe_483e_4b20_baa9_6ffdf89ab3da
ELIN-802356-2017 | EL-339591-2016 | 4/25/2017 11:33:40 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Open_slice_to_flexible_cable.png Open splice in the wall with flexible cable. Possibility for shock or fire. | 4 | Conductors, Misuse of flexible cords. | Open_slice_to_flexible_cable.png | file://x:/photopub/docs/0000000591/aca9a1bc-21d8-4b52-a969-1290b245596a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7e6edc1_b51e_4731_b9a7_820b0e1d4e64
ELIN-776509-2017 | EL-511836-2017 | 3/17/2017 12:56:55 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | #No_protection_plate_for_service_conductors_and_service_conduit_.png Protection plate is required to prevent the service conductors and service conduit from mechanical damage at the meter base location. This is an equipment damage condition. 120/240 Volt, 200 Amp. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | No_protection_plate_for_service_conductors_and_service_conduit_.png | file://x:/photopub/docs/0000000573/191e7eed-d063-4865-bb91-dac728c0f4eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54d461aa_a8c4_4d4f_97e5_9e4ceec4117c
ELIN-775903-2017 | EL-511773-2017 | 3/20/2017 11:25:03 AM | ASSESS: EL: Service Connection | png | #asFound | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 4 | 3 | #Suite_feeder_and_panel1.png,Suite_feeder_and_panel2.png Suite panel is not separately supplied from the supply authority and ready access to the main panel where the suite feeder breaker is supplied will not be available to the future suite tenant. | 4 | General Location of equipment does not allow for proper access to disconnecting means | Suite_feeder_and_panel1.png | file://x:/photopub/docs/0000000573/26a0c522-3b2a-4fac-9b6d-be8a369a0d82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0557b1b2_3384_4e95_af84_eabad5107b9e
ELHE-774842-2017 | HE-511534-2017 | 3/15/2017 9:56:39 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 3 | #Fire_damage_in_basement1.png,Fire_damage_in_basement2.png The 15 amp 120/240 volt branch circuits were damaged during a fire incident not electrically related however caused severe damage to branch wiring within the vicinity. This is a equipment damage issue | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Fire_damage_in_basement2.png | file://x:/photopub/docs/0000000572/9d45f845-aa43-4004-b93f-5188fbcd8acf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23ec51d6_f339_423e_b770_0e672f3bc7ac
BPVIN-803556-2017 | BPV-526986-2017 | 4/26/2017 12:32:37 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP014 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | 1 | 1 | #Clearances_.png,Clearances_.png | 1 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | Clearances_.png | file://x:/photopub/docs/0000000591/9a38576b-9dff-491a-bfe7-fe6a04cd782e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f61385d8_070e_4c9e_b1c0_11ac581f9d5a
ELIN-775903-2017 | EL-511773-2017 | 3/20/2017 11:25:03 AM | ASSESS: EL: Service Connection | png | #asFound | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 4 | 3 | #Suite_feeder_and_panel1.png,Suite_feeder_and_panel2.png Suite panel is not separately supplied from the supply authority and ready access to the main panel where the suite feeder breaker is supplied will not be available to the future suite tenant. | 4 | General Location of equipment does not allow for proper access to disconnecting means | Suite_feeder_and_panel2.png | file://x:/photopub/docs/0000000573/09a512ac-7cc0-442c-8192-eb7d483a22b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0557b1b2_3384_4e95_af84_eabad5107b9e
GAUP-761605-2017 | UW-503664-2017 | 2/22/2017 9:38:12 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound Gas hoses installed for appliances are undersized for the input. | GA070 | Undersized hose or appliance connector | 3 | 3 | #Gas_hose.png Gas hoses installed for appliances are undersized for the input. This may lead to incomplete combustion and the production of carbon monoxide. | 3 | Undersized hose or appliance connector | Gas_hose.png | file://x:/photopub/docs/0000000562/1b0ac87b-04b2-43ca-b8e7-a66a1cad5389.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__77bc46be_4fb7_461f_93b5_b0dfd85c7090
ELIN-645454-2016 | EL-433234-2016 | 3/17/2017 3:31:32 PM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #PVC_conduit.png No conduit supports installed conductors could be mechanically damaged | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | PVC_conduit.png | file://x:/photopub/docs/0000000573/87bf9ac5-0df1-4a38-ab22-25bc295775d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__963911d6_c085_4ec8_a484_3e49b89176e2
ELIN-780696-2017 | UW-514891-2017 | 4/7/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Open_panel.png In an existing commercial space, a 200amp 120/240volt panel was found in an energized state with no protective cover installed. This can lead to a shock hazard. Pic attached. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Open_panel.png | file://x:/photopub/docs/0000000584/63270f77-96df-4b39-8629-47c325aa1a1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff805ad6_3e74_4bb4_a487_792448f60143
ELIN-809793-2017 | EL-530446-2017 | 5/8/2017 12:12:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Need_Protection.png This assessment found GFCIs' are required for temporary receptacles during construction stage. Without this protection, a shock hazard exists. | 3 | Conductors Equipment is not approved for the specific use. | Need_Protection.png | file://x:/photopub/docs/0000000598/bf77090e-26a7-4721-86a5-732afd00305e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__084a6e82_b744_47e5_a329_c314234348d2
ELHE-774842-2017 | HE-511534-2017 | 3/15/2017 9:56:39 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 3 | #Fire_damage_in_basement1.png,Fire_damage_in_basement2.png The 15 amp 120/240 volt branch circuits were damaged during a fire incident not electrically related however caused severe damage to branch wiring within the vicinity. This is a equipment damage issue | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Fire_damage_in_basement1.png | file://x:/photopub/docs/0000000572/5f567ddb-76df-4fe0-a383-eb0fe8916afc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23ec51d6_f339_423e_b770_0e672f3bc7ac
ELIN-799596-2017 | EL-352383-2016 | 4/20/2017 3:04:10 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Main_disconnec__main_disconnect_and_a_subpanel1.png,Main_disconnec__main_disconnect_and_a_subpanel2.png Grounding conductor is not terminated at the main disconnect but is terminated at a subpanel. Potential is for fault current or step in touch potentials from a fault to not reach main supply over-current disconnects. This creates a shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Main_disconnec__main_disconnect_and_a_subpanel2.png | file://x:/photopub/docs/0000000588/f318d952-d8cb-4fc9-b388-266a4d438967.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b87054d1_fcf4_4726_ba96_5a47cebb4646
ELIN-799596-2017 | EL-352383-2016 | 4/20/2017 3:04:10 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Main_disconnec__main_disconnect_and_a_subpanel1.png,Main_disconnec__main_disconnect_and_a_subpanel2.png Grounding conductor is not terminated at the main disconnect but is terminated at a subpanel. Potential is for fault current or step in touch potentials from a fault to not reach main supply over-current disconnects. This creates a shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Main_disconnec__main_disconnect_and_a_subpanel1.png | file://x:/photopub/docs/0000000588/77fad917-18e1-44f5-a120-c3c382ebe378.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b87054d1_fcf4_4726_ba96_5a47cebb4646
GAIN-807957-2017 | GA-520451-2017 | 5/8/2017 11:56:40 AM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Fitting.png Prohibited black iron fitting installed in piping system. "Street Elbow" 90 degree fitting incorporates a internal pipe thread on one side with an external pipe thread on the other side. These fitting are prone to stress fractures cause potential gas leaks. | 3 | Non-compliant material/fittings installed | Fitting.png | file://x:/photopub/docs/0000000597/3cc60d37-4f03-4807-a46e-c4d24110e9b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84d75cb4_b982_4c62_b2c5_9bb0a702069d
ELIN-790239-2017 | EL-517912-2017 | 4/10/2017 10:27:04 AM | ASSESS: EL: Service Connection | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Distribution_.png Distribution panel installed in an area that is accessible to the public. No lockable enclosure has been provided to ensure access by authorized personnel only. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Distribution_.png | file://x:/photopub/docs/0000000584/eecb7c3b-00ba-43fb-8ffe-942bb360b4fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a85a1444_68d0_46ae_bc26_ac791ee88e85
ELIN-797522-2017 | UW-523698-2017 | 4/18/2017 1:19:06 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_outlets_switches1.png,Energized_outlets_switches2.png,Energized_outlets_switches3.png,Energized_outlets_switches4.png 120 volt 15 amp outlet and switch boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_outlets_switches1.png | file://x:/photopub/docs/0000000588/d86fda2f-ccff-41d8-a364-6de65b807852.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75f91c29_8bcf_47a0_b82f_c92da40e2eb6
ELIN-797522-2017 | UW-523698-2017 | 4/18/2017 1:19:06 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_outlets_switches1.png,Energized_outlets_switches2.png,Energized_outlets_switches3.png,Energized_outlets_switches4.png 120 volt 15 amp outlet and switch boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_outlets_switches3.png | file://x:/photopub/docs/0000000588/88398d5c-984b-43cf-aeff-eee2599eca36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75f91c29_8bcf_47a0_b82f_c92da40e2eb6
ELIN-797522-2017 | UW-523698-2017 | 4/18/2017 1:19:06 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_outlets_switches1.png,Energized_outlets_switches2.png,Energized_outlets_switches3.png,Energized_outlets_switches4.png 120 volt 15 amp outlet and switch boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_outlets_switches2.png | file://x:/photopub/docs/0000000588/16c774fd-3f00-4ea2-be3a-b21c0c713724.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75f91c29_8bcf_47a0_b82f_c92da40e2eb6
ELIN-797522-2017 | UW-523698-2017 | 4/18/2017 1:19:06 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_outlets_switches1.png,Energized_outlets_switches2.png,Energized_outlets_switches3.png,Energized_outlets_switches4.png 120 volt 15 amp outlet and switch boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_outlets_switches4.png | file://x:/photopub/docs/0000000588/e0544933-45c0-41bc-9693-a33efa7cfa18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75f91c29_8bcf_47a0_b82f_c92da40e2eb6
ELIN-762469-2017 | EL-473720-2016 | 2/27/2017 1:26:56 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | #Bedroom_Fan_Box.png The 15 amp 120 volt powered octagon outlet boxes provided for the future ceiling fans are not rated for the use and approved fan support boxes have not been supplied. This could result in a failure of the outlet boxes and possible harm to persons. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Bedroom_Fan_Box.png | file://x:/photopub/docs/0000000563/67cbd6e6-45b5-487a-8183-502a0a764e30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1413561f_c57c_461d_843c_100bf0451cc8
EDIN-791766-2017 | ED-435006-2016 | 4/7/2017 3:36:27 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Unsafe_roof_access_to_the_control_room1.png,Unsafe_roof_access_to_the_control_room2.png,Unsafe_roof_access_to_the_control_room3.png,Unsafe_roof_access_to_the_control_room4.png Guardrail are installed to prevent a fall hazard condition. During an acceptance inspection, it was found that the guardrail were not installed to give safe passage across the roof to access the elevator control room as illustrated in the attached pictures. Without the guardrail there is a serious potential for a worker to fall from the roof of the building as the unguarded area is in close proximity to the exit doorway from the stairwell. This fall will cause serious injury or death. The general contractor failed to install the guardrail on a newly constructed 8 stores residential building. | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Unsafe_roof_access_to_the_control_room4.png | file://x:/photopub/docs/0000000583/a0391cb6-5134-4dc3-936f-1d1d000d6b4c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__973aeeac_2c47_4f46_8c52_0b2952743bd2
ELIN-774612-2017 | EL-502084-2017 | 3/15/2017 9:11:54 AM | ASSESS: EL: Final | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | #Fridge_Cord.png The 120 volt 15 amp fridge has not been provided with its own dedicated circuit and receptacle and has been plugged into a kitchen counter receptacle. This poses a shock hazard to persons and possible damage to the fridge and kitchen counter receptacle as this circuit can now be overloaded. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Fridge_Cord.png | file://x:/photopub/docs/0000000572/0c74ae36-213f-47ef-a74b-44268c57c6f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af514629_7ac2_4871_b3a0_4ee71fe107c3
ELIN-764363-2017 | EL-501188-2017 | 2/28/2017 11:50:15 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #grounding_conductor_installed_in_meter_base_.png Ground conductor has been terminated to enclosure of meter base. Service ground conductors are required to terminate at Neutral or Identified conductor on AC systems. Current location of ground conductor would not allow for proper operation of overcurrent devices, and potentially lead to fire or shock in an electrical fault situation. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | grounding_conductor_installed_in_meter_base_.png | file://x:/photopub/docs/0000000563/1de8fde5-7bd1-421f-9252-1d3bb61847e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff4b0293_686d_40d1_8768_c8e8f333404a
ELIN-762694-2017 | UW-504242-2017 | 2/28/2017 3:09:26 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #overhead_service_conductors_below_acceptable_height_from_grade_and_open_spices1.png,overhead_service_conductors_below_acceptable_height_from_grade_and_open_spices2.png,overhead_service_conductors_below_acceptable_height_from_grade_and_open_spices3.png Energized Overhead service conductors are below acceptable height. Conductors are able to be reached by hand from grade. If left unattended or vandalized there is a potential of arc flash, shock and fire to persons and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | overhead_service_conductors_below_acceptable_height_from_grade_and_open_spices3.png | file://x:/photopub/docs/0000000563/44952fc7-9d05-403f-9270-4869ac84a7a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__abc420d3_ab95_47b9_93e6_3d57662af35c
ELIN-762694-2017 | UW-504242-2017 | 2/28/2017 3:09:26 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound open splices | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #overhead_service_conductors_below_acceptable_height_from_grade_and_open_spices1.png,overhead_service_conductors_below_acceptable_height_from_grade_and_open_spices2.png,overhead_service_conductors_below_acceptable_height_from_grade_and_open_spices3.png Energized Overhead service conductors are below acceptable height. Conductors are able to be reached by hand from grade. If left unattended or vandalized there is a potential of arc flash, shock and fire to persons and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | overhead_service_conductors_below_acceptable_height_from_grade_and_open_spices2.png | file://x:/photopub/docs/0000000563/de562759-a3b9-490f-88d5-e3e2f81312b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__abc420d3_ab95_47b9_93e6_3d57662af35c
ELIN-762694-2017 | UW-504242-2017 | 2/28/2017 3:09:26 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound service conductors at 1.5 meters from grade | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #overhead_service_conductors_below_acceptable_height_from_grade_and_open_spices1.png,overhead_service_conductors_below_acceptable_height_from_grade_and_open_spices2.png,overhead_service_conductors_below_acceptable_height_from_grade_and_open_spices3.png Energized Overhead service conductors are below acceptable height. Conductors are able to be reached by hand from grade. If left unattended or vandalized there is a potential of arc flash, shock and fire to persons and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | overhead_service_conductors_below_acceptable_height_from_grade_and_open_spices1.png | file://x:/photopub/docs/0000000563/9881a3de-c6ca-41f6-8867-b7101d366e66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__abc420d3_ab95_47b9_93e6_3d57662af35c
ELIN-783081-2017 | EL-514102-2017 | 3/28/2017 12:20:36 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Ash_Rd.png Equipment subject to vehicle damage, poor materials, non-approved attachment | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Ash_Rd.png | file://x:/photopub/docs/0000000577/d20d509f-84a9-4b40-8bf1-f73a117ce8b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54d5edd2_3a76_4660_b685_ab8a8ebdb025
ELIN-797654-2017 | EL-521267-2017 | 4/19/2017 1:42:10 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 2 | #B.png Plastic WSW device box is not approved for use with floor plugs. This is a shock and fire hazard. | 3 | Conductors Equipment is not approved for the specific use. | B.png | file://x:/photopub/docs/0000000588/bececb63-c15c-4697-b38e-b7c6a3b2cc91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__830c0a55_434f_447c_85d1_289bc7707174
EDIN-791766-2017 | ED-435006-2016 | 4/7/2017 3:36:27 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Unsafe_roof_access_to_the_control_room1.png,Unsafe_roof_access_to_the_control_room2.png,Unsafe_roof_access_to_the_control_room3.png,Unsafe_roof_access_to_the_control_room4.png Guardrail are installed to prevent a fall hazard condition. During an acceptance inspection, it was found that the guardrail were not installed to give safe passage across the roof to access the elevator control room as illustrated in the attached pictures. Without the guardrail there is a serious potential for a worker to fall from the roof of the building as the unguarded area is in close proximity to the exit doorway from the stairwell. This fall will cause serious injury or death. The general contractor failed to install the guardrail on a newly constructed 8 stores residential building. | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Unsafe_roof_access_to_the_control_room1.png | file://x:/photopub/docs/0000000583/f681d2d3-ecdc-479a-92a3-998f791cdb49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__973aeeac_2c47_4f46_8c52_0b2952743bd2
EDIN-791766-2017 | ED-435006-2016 | 4/7/2017 3:36:27 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Unsafe_roof_access_to_the_control_room1.png,Unsafe_roof_access_to_the_control_room2.png,Unsafe_roof_access_to_the_control_room3.png,Unsafe_roof_access_to_the_control_room4.png Guardrail are installed to prevent a fall hazard condition. During an acceptance inspection, it was found that the guardrail were not installed to give safe passage across the roof to access the elevator control room as illustrated in the attached pictures. Without the guardrail there is a serious potential for a worker to fall from the roof of the building as the unguarded area is in close proximity to the exit doorway from the stairwell. This fall will cause serious injury or death. The general contractor failed to install the guardrail on a newly constructed 8 stores residential building. | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Unsafe_roof_access_to_the_control_room2.png | file://x:/photopub/docs/0000000583/6b8bb166-0528-4287-9119-f1445e444960.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__973aeeac_2c47_4f46_8c52_0b2952743bd2
EDIN-791766-2017 | ED-435006-2016 | 4/7/2017 3:36:27 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Unsafe_roof_access_to_the_control_room1.png,Unsafe_roof_access_to_the_control_room2.png,Unsafe_roof_access_to_the_control_room3.png,Unsafe_roof_access_to_the_control_room4.png Guardrail are installed to prevent a fall hazard condition. During an acceptance inspection, it was found that the guardrail were not installed to give safe passage across the roof to access the elevator control room as illustrated in the attached pictures. Without the guardrail there is a serious potential for a worker to fall from the roof of the building as the unguarded area is in close proximity to the exit doorway from the stairwell. This fall will cause serious injury or death. The general contractor failed to install the guardrail on a newly constructed 8 stores residential building. | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Unsafe_roof_access_to_the_control_room3.png | file://x:/photopub/docs/0000000583/e542f646-fa6f-4169-9bb5-08a1c4d4c59d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__973aeeac_2c47_4f46_8c52_0b2952743bd2
ELIN-803188-2017 | EL-510112-2017 | 5/1/2017 8:36:05 AM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 2 | #Grounding_not_at_source_of_supply1.png,Grounding_not_at_source_of_supply2.png The 200 amp 120/240 volt service has been grounded however not terminated at the source of supply where the first disconnect is located at the pole service, any current flow on the identified conductor circuit will include current flow on a parallel path utilizing the bonding conductor. This could give the opportunity of a thermal hazard and the main disconnecting means may not properly operate during a fault. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Grounding_not_at_source_of_supply1.png | file://x:/photopub/docs/0000000594/8fa3e0d4-3a99-4721-a984-1c57541fb983.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c057511f_dfa4_4461_b0a9_ec41849f6caa
GAIN-766716-2017 | GA-505911-2017 | 3/20/2017 9:51:08 AM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Patio_heater.png The as found hazard was a patio heater which had been installed without the required clearance to the surrounding combustible material. This is a hazard as it creates a risk of fire. | 3 | Clearance to combustible not met | Patio_heater.png | file://x:/photopub/docs/0000000573/b6ee895c-2d34-4419-bf72-9be634efa2ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ea7d9ee_b7e7_40e9_8b87_0134361ec382
ELIN-775067-2017 | EL-472725-2016 | 3/20/2017 9:47:04 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL138 | Installation of electrical equipment General: boxes are not accessible. | 3 | 2 | #Outlet_box.png The 15 amp 120 volt receptacle box is located behind a framed pony wall for a fireplace and will become difficult to access after installation, this can become both a shock and thermal hazard | 3 | Installation of electrical equipment General: boxes are not accessible. | Outlet_box.png | file://x:/photopub/docs/0000000573/aa6debdc-6035-4669-9b28-d4ec8e3eee57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f24780f9_5ed0_42bc_89a5_8fa005c5156e
GAIN-811382-2017 | GA-487175-2017 | 5/11/2017 2:40:39 PM | ASSESS: GA: Rough-In | png | #asFound Swing joint | GA003 | Provision for expansion Incorrect swing joint | 2 | 2 | #Swing_joint.png Swing joint on riser installed improperly. If ground were to freeze and move, the piping could break and cause a leak. | 2 | Provision for expansion Incorrect swing joint | Swing_joint.png | file://x:/photopub/docs/0000000599/c393ceae-01e4-4191-9a53-34a1ebdfdebf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3665d67d_b809_4a20_af07_66ce8e77e46b
ELIN-766869-2017 | EL-480667-2016 | 3/2/2017 1:18:20 PM | ASSESS: EL: Service Connection | png | #asFound Damaged armour | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 3 | #Damaged_armour.png Jacket of armoured cable damaged during installation. Armoured cable and the connection of the cable to electrical equipment should be made without undue distortion or damage to the armour. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Damaged_armour.png | file://x:/photopub/docs/0000000565/03c10450-3638-4c12-a4cd-853ea38c9c77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__323c356e_6793_48aa_a7af_f4594c7fcf2c
ELIN-803188-2017 | EL-510112-2017 | 5/1/2017 8:36:05 AM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 2 | #Grounding_not_at_source_of_supply1.png,Grounding_not_at_source_of_supply2.png The 200 amp 120/240 volt service has been grounded however not terminated at the source of supply where the first disconnect is located at the pole service, any current flow on the identified conductor circuit will include current flow on a parallel path utilizing the bonding conductor. This could give the opportunity of a thermal hazard and the main disconnecting means may not properly operate during a fault. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Grounding_not_at_source_of_supply2.png | file://x:/photopub/docs/0000000594/294f459b-08b6-4d9a-879a-1212762912f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c057511f_dfa4_4461_b0a9_ec41849f6caa
ELIN-804363-2017 | EL-527457-2017 | 5/1/2017 2:09:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Service_equipment1.png,Service_equipment2.png,Service_equipment3.png The 200 amp 120/208 volt 3-phase 4-wire temporary service is de-energized and requested for connection. The service equipment does not provide a weather-proof or lockable enclosure and misc knock out fillers missing. The main breaker compartment has a 2" knock out missing exposing the accessibility of accidental contact with unprotected utility power on the line side of the main breaker 'once energized' plus the equipment is exposed to adverse weather conditions entering the panel. This can create a shock, thermal and equipment damage issue | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Service_equipment2.png | file://x:/photopub/docs/0000000594/686b9ee7-387f-46dd-9261-e2b4670917a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61028d4c_235c_4977_9460_10383ad773bd
ELIN-804363-2017 | EL-527457-2017 | 5/1/2017 2:09:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Service_equipment1.png,Service_equipment2.png,Service_equipment3.png The 200 amp 120/208 volt 3-phase 4-wire temporary service is de-energized and requested for connection. The service equipment does not provide a weather-proof or lockable enclosure and misc knock out fillers missing. The main breaker compartment has a 2" knock out missing exposing the accessibility of accidental contact with unprotected utility power on the line side of the main breaker 'once energized' plus the equipment is exposed to adverse weather conditions entering the panel. This can create a shock, thermal and equipment damage issue | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Service_equipment3.png | file://x:/photopub/docs/0000000594/9e9c88ff-f606-4bfd-8434-5131e8583c49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61028d4c_235c_4977_9460_10383ad773bd
ELIN-804363-2017 | EL-527457-2017 | 5/1/2017 2:09:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Service_equipment1.png,Service_equipment2.png,Service_equipment3.png The 200 amp 120/208 volt 3-phase 4-wire temporary service is de-energized and requested for connection. The service equipment does not provide a weather-proof or lockable enclosure and misc knock out fillers missing. The main breaker compartment has a 2" knock out missing exposing the accessibility of accidental contact with unprotected utility power on the line side of the main breaker 'once energized' plus the equipment is exposed to adverse weather conditions entering the panel. This can create a shock, thermal and equipment damage issue | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Service_equipment1.png | file://x:/photopub/docs/0000000594/48cb45bb-684b-4d19-b52c-afe324b3d995.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61028d4c_235c_4977_9460_10383ad773bd
GAWP-769509-2017 | GA-317157-2015 | 3/14/2017 4:52:07 PM | ASSESS: GA Work In Progress | png | #asFound No relief valve installed on Navien | GA154 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | 5 | 5 | #No_relief_valve_Navien.png Found on demand Navien water heater working without a relief valve installed. It is possible that the unit could over pressure and cause catastrophic failure, possibly resulting in injury or death. | 5 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | No_relief_valve_Navien.png | file://x:/photopub/docs/0000000571/1e53100e-0d4b-4758-ae96-3c98c901ad0d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__624b2e8d_b518_4f51_b426_c4351014e019
BPVOP-771058-2017 | 2271972 | 3/8/2017 1:32:34 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Safety_relief_valve.png Upon assessment of Hot Water Boiler with Heating surface area of 35 quare meters, Maximum Allowable Working Pressure (MAWP) of 60psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Safety_relief_valve.png | file://x:/photopub/docs/0000000568/349895f0-b745-49fa-82e6-d8eb477ec158.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6413b729_55f4_49db_b3ce_40e0b5dc48b7
BPVIN-771118-2017 | UW-509202-2017 | 3/8/2017 12:06:19 PM | ASSESS: BPV IN: Installation REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Pressure_relief_valve.png Upon assessment it is determined that machine mounted vertical air receiver (1.3m long and .80m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Pressure_relief_valve.png | file://x:/photopub/docs/0000000568/13d7785f-f2cb-48cf-99e6-fb2390c92300.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba6d1555_1634_4c40_8ff0_ed987f30d419
ELIN-813330-2017 | EL-518564-2017 | 5/11/2017 11:50:37 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #8_awg_stranded_conductor_terminated_under_wire_binding_screw.png # 8 stranded aluminum conductor is terminated under a wire binding screw. Conductors this size require solder less type compression connection. This avoids strands not being in contact with bonded metal. Inadequate bonding may result in overcurrent devices not operating to clear faults and could result in damaged equipment, shock or fire. | 3 | Continuity Bonding; method for equipment is not adequate. | 8_awg_stranded_conductor_terminated_under_wire_binding_screw.png | file://x:/photopub/docs/0000000599/629847bf-42eb-4b4c-9a9e-277796348d30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26b5349a_c803_4d6d_9662_b0b53317b21b
GAIN-792733-2017 | GA-521162-2017 | 5/9/2017 2:15:28 PM | ASSESS: GA: Final | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Oversized_vent.png Hot water heater is vented using a 6 inch vent. The vent required is a 4" vent. Possibility of spillage of flue gases out of draft hood in prime conditions due to flue gases cooling down too fast in Vent | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Oversized_vent.png | file://x:/photopub/docs/0000000598/906cfb38-41a8-4591-818a-cc991f99d7c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb0394a1_5cbe_4e2c_88d2_8eb190000c11
ELHE-814878-2017 | UW-533575-2017 | 5/12/2017 9:10:22 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound With cover removed, load side of metre base is energized. | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #modifications_made_by_owner1.png,modifications_made_by_owner2.png Building owner has installed electrical power from the temporary construction service to the permanent metre base have a single-family dwelling. Owner has made modifications to the electrical system creating a shock hazard whereby someone could accidentally touch the metre base and be electrocuted. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | modifications_made_by_owner2.png | file://x:/photopub/docs/0000000600/366d309e-1d33-4405-aed8-07ccfbab2f26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9865ba07_b5fd_452c_9afd_6f5adfb5a3f2
ELHE-814878-2017 | UW-533575-2017 | 5/12/2017 9:10:22 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Electrical modifications made by owner, feeder conductor from temporary construction service feeding permanent metre base. Load side of metre base is energized | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #modifications_made_by_owner1.png,modifications_made_by_owner2.png Building owner has installed electrical power from the temporary construction service to the permanent metre base have a single-family dwelling. Owner has made modifications to the electrical system creating a shock hazard whereby someone could accidentally touch the metre base and be electrocuted. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | modifications_made_by_owner1.png | file://x:/photopub/docs/0000000600/b6ce32d7-9ea4-49af-8dec-6db3cacfcd85.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9865ba07_b5fd_452c_9afd_6f5adfb5a3f2
ELIN-764273-2017 | EL-428876-2016 | 2/27/2017 1:26:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Unapproved_mast1.png,Unapproved_mast2.png,Unapproved_mast3.png - unapproved structure built to support overhead service conductors. - 6x6 wooden post was attached to shed like structure with minimal wood screws. Wooden post would most likely not be able to handle the stress of BC Hydro overhead conductors. if this mast were to fall the service conductors attached from utility are not fused and would lay on ground or trees energized with risk of shock or fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Unapproved_mast2.png | file://x:/photopub/docs/0000000564/7ad27259-0167-4a02-9412-bf84910c6926.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cfc22217_d99c_40ea_95b5_9d03d8f33e00
ELIN-764273-2017 | EL-428876-2016 | 2/27/2017 1:26:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Unapproved_mast1.png,Unapproved_mast2.png,Unapproved_mast3.png - unapproved structure built to support overhead service conductors. - 6x6 wooden post was attached to shed like structure with minimal wood screws. Wooden post would most likely not be able to handle the stress of BC Hydro overhead conductors. if this mast were to fall the service conductors attached from utility are not fused and would lay on ground or trees energized with risk of shock or fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Unapproved_mast1.png | file://x:/photopub/docs/0000000564/965d1ab2-5ec0-4eb0-9dab-edd6fcc77a2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cfc22217_d99c_40ea_95b5_9d03d8f33e00
ELIN-764273-2017 | EL-428876-2016 | 2/27/2017 1:26:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Unapproved_mast1.png,Unapproved_mast2.png,Unapproved_mast3.png - unapproved structure built to support overhead service conductors. - 6x6 wooden post was attached to shed like structure with minimal wood screws. Wooden post would most likely not be able to handle the stress of BC Hydro overhead conductors. if this mast were to fall the service conductors attached from utility are not fused and would lay on ground or trees energized with risk of shock or fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Unapproved_mast3.png | file://x:/photopub/docs/0000000564/3e7e7998-6a88-40e4-8b78-6cbdcd851055.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cfc22217_d99c_40ea_95b5_9d03d8f33e00
ELIN-807938-2017 | UW-529366-2017 | 5/2/2017 4:56:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use1.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use2.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use3.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use4.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use5.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use6.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use7.png Found 120/240volt 3 conductor single phase feeder from generator using flexible cord having conductors open air spliced at weather head in wet location and exposed to weather while flexible cord conductors are not approved for the use in wet locations. When electrical equipment is not used as per approved use of electrical equipment the conductors could get damaged and | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use2.png | file://x:/photopub/docs/0000000596/82ba6be6-39ef-44ce-9c40-d4cf68af6207.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c532b7af_2ceb_4797_ae98_1511ff3686b3
ELIN-807938-2017 | UW-529366-2017 | 5/2/2017 4:56:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use1.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use2.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use3.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use4.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use5.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use6.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use7.png Found 120/240volt 3 conductor single phase feeder from generator using flexible cord having conductors open air spliced at weather head in wet location and exposed to weather while flexible cord conductors are not approved for the use in wet locations. When electrical equipment is not used as per approved use of electrical equipment the conductors could get damaged and | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use5.png | file://x:/photopub/docs/0000000596/51aaf9df-c42c-4c42-8b7d-41d25c2efbad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c532b7af_2ceb_4797_ae98_1511ff3686b3
ELIN-807938-2017 | UW-529366-2017 | 5/2/2017 4:56:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use1.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use2.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use3.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use4.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use5.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use6.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use7.png Found 120/240volt 3 conductor single phase feeder from generator using flexible cord having conductors open air spliced at weather head in wet location and exposed to weather while flexible cord conductors are not approved for the use in wet locations. When electrical equipment is not used as per approved use of electrical equipment the conductors could get damaged and | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use7.png | file://x:/photopub/docs/0000000596/9c9b4b79-eafc-4499-a97f-7db4263917b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c532b7af_2ceb_4797_ae98_1511ff3686b3
ELIN-807938-2017 | UW-529366-2017 | 5/2/2017 4:56:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use1.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use2.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use3.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use4.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use5.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use6.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use7.png Found 120/240volt 3 conductor single phase feeder from generator using flexible cord having conductors open air spliced at weather head in wet location and exposed to weather while flexible cord conductors are not approved for the use in wet locations. When electrical equipment is not used as per approved use of electrical equipment the conductors could get damaged and | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use6.png | file://x:/photopub/docs/0000000596/d1bd1d1b-57d1-47d0-b3bb-19f7997c3c79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c532b7af_2ceb_4797_ae98_1511ff3686b3
ELIN-807938-2017 | UW-529366-2017 | 5/2/2017 4:56:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use1.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use2.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use3.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use4.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use5.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use6.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use7.png Found 120/240volt 3 conductor single phase feeder from generator using flexible cord having conductors open air spliced at weather head in wet location and exposed to weather while flexible cord conductors are not approved for the use in wet locations. When electrical equipment is not used as per approved use of electrical equipment the conductors could get damaged and | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use1.png | file://x:/photopub/docs/0000000596/bc2a4666-4a34-4b63-b2ac-c136e30f1520.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c532b7af_2ceb_4797_ae98_1511ff3686b3
ELIN-807938-2017 | UW-529366-2017 | 5/2/2017 4:56:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use1.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use2.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use3.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use4.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use5.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use6.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use7.png Found 120/240volt 3 conductor single phase feeder from generator using flexible cord having conductors open air spliced at weather head in wet location and exposed to weather while flexible cord conductors are not approved for the use in wet locations. When electrical equipment is not used as per approved use of electrical equipment the conductors could get damaged and | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use4.png | file://x:/photopub/docs/0000000596/cf810de2-9582-476a-aab3-7325f2be187a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c532b7af_2ceb_4797_ae98_1511ff3686b3
ELIN-807938-2017 | UW-529366-2017 | 5/2/2017 4:56:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use1.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use2.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use3.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use4.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use5.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use6.png,Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use7.png Found 120/240volt 3 conductor single phase feeder from generator using flexible cord having conductors open air spliced at weather head in wet location and exposed to weather while flexible cord conductors are not approved for the use in wet locations. When electrical equipment is not used as per approved use of electrical equipment the conductors could get damaged and | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Flexible_cord_conductor_from_generator_spliced_in_wet_location_not_approved_for_the_use3.png | file://x:/photopub/docs/0000000596/d12a32e7-0ae7-4565-9a0f-e4831b3b3b63.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c532b7af_2ceb_4797_ae98_1511ff3686b3
BPVOP-776708-2017 | 2273627 | 3/22/2017 1:50:12 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #SRV.png Upon the assessment of a Hot Water Boiler with MAWP of 100 psig, was found that the Safety Relief Valve was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SRV.png | file://x:/photopub/docs/0000000576/f03bcdd7-43e7-4515-8541-14d5ea108c0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__16f248f6_b76a_44e7_98b0_5b4d2de32e3c
BPVOP-776707-2017 | 4112067 | 3/22/2017 1:55:05 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Relief_Valve_electric.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 2009 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_electric.png | file://x:/photopub/docs/0000000576/8aff4e4e-c073-49b3-8400-629db3f6a155.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f78b2d05_9f5e_4f25_9ae1_cc38f4150411
BPVOP-776714-2017 | 4060011 | 3/22/2017 2:12:49 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Relief_Valve_.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 2009 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_.png | file://x:/photopub/docs/0000000576/7acaeb7b-af4b-4a50-9121-ae9739548d0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d36d9a5_b0d2_4ea2_bc7f_73fb29d20ed0
BPVOP-776711-2017 | 4060020 | 3/22/2017 2:20:10 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Relief_Valve_2.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_2.png | file://x:/photopub/docs/0000000576/c4cd379e-6b73-483b-b6be-0bc49ea87fe8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b77ec29_0d2b_4965_8bd3_84549b58f72c
EDMA-800743-2017 | ED-478661-2016 | 4/21/2017 9:55:02 PM | ASSESS: ED MA: Partial Acceptance | png | #asFound Machine room access across roof top | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Roof.png Fall hazard when elevator personnel requires access to the machine room at night time hours | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Roof.png | file://x:/photopub/docs/0000000589/e75e303a-ab7b-4345-aeeb-e0330a0f35b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8b839d9_29b5_459c_a756_b5b03be3250e
GAIN-779810-2017 | GA-509405-2017 | 3/22/2017 9:48:31 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Rtu.png Found roof top unit installed with vent terminated directly in front of fresh air intake of another roof top unit. This could result in the products of combustion from one unit being drawn into the fresh air intake of the next unit, and can pose a risk to the occupants of the building. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Rtu.png | file://x:/photopub/docs/0000000575/b115271a-862d-4804-9d9f-5b486b82f1eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4acdee84_d631_479e_a393_5184ea082b65
AMOP-793341-2017 | 2780139 | 4/12/2017 8:12:00 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Broken_adjustment_bolt_on_wheel.png An adjustment bolt had been broken off on a pcu wheel, wheel may not be in proper alignment to rail, possibly causing an alignment problem with the coaster. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Broken_adjustment_bolt_on_wheel.png | file://x:/photopub/docs/0000000586/113845fa-b4ed-46d1-a7a5-26e06379601b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e941587_6a83_4c3d_b746_528bfd3762c1
ELIN-803219-2017 | EL-396278-2016 | 4/28/2017 8:37:56 AM | ASSESS: EL: Service Connection | png | #asFound | EL296 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Panel_Fillers_Missing1.png,Panel_Fillers_Missing2.png This assessment found Panel fillers missing exposing live bus bars and creating a potential shock hazard. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Panel_Fillers_Missing2.png | file://x:/photopub/docs/0000000592/7916a3bf-a65d-4007-97d2-3fb808137249.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bf176c1_7724_4b3f_9ea5_dde536bccc93
ELIN-803219-2017 | EL-396278-2016 | 4/28/2017 8:37:56 AM | ASSESS: EL: Service Connection | png | #asFound | EL296 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Panel_Fillers_Missing1.png,Panel_Fillers_Missing2.png This assessment found Panel fillers missing exposing live bus bars and creating a potential shock hazard. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Panel_Fillers_Missing1.png | file://x:/photopub/docs/0000000592/52f18e8c-65fa-4493-9372-e0357498bb84.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bf176c1_7724_4b3f_9ea5_dde536bccc93
ELIN-798011-2017 | UW-523958-2017 | 4/18/2017 5:01:38 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Z.png 3 C / # 14 AWG NMWU is not installed in trench correctly. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Z.png | file://x:/photopub/docs/0000000587/c50797e6-fd5e-4eaf-a5ff-f04b2b061f87.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dea3e8c4_9276_4128_938f_ea7338248a8d
ELIN-793880-2017 | EL-413321-2016 | 4/18/2017 5:03:02 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_GFCI_protection.png 20 amp kitchen island receptacle located within 1.5M of the island sink is not GFCI protected. This is a shock hazard as an appliance could accidentally fall into standing water in the sink and electrocute an individual. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | No_GFCI_protection.png | file://x:/photopub/docs/0000000587/641e7a36-7f89-4b6e-806a-5ea1b883121d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4d20c98_4ed4_471b_9f95_466f071d65c2
ELIN-806722-2017 | EL-528604-2017 | 5/3/2017 10:07:38 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Teck_laying_on_ground.png Teck conductor left laying on the ground, final inspection requested. | 3 | Conductors Equipment is not approved for the specific use. | Teck_laying_on_ground.png | file://x:/photopub/docs/0000000595/c3d55991-ee7c-492c-8b90-45255d9105fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0bb9ff01_7a2d_4f79_901e_48ea36806218
ELIN-806722-2017 | EL-528604-2017 | 5/3/2017 10:07:38 AM | ASSESS: EL: Final | png | #asFound Teck90 feeder to hot tub left laying on the ground. | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Teck_laying_on_ground.png Teck conductor left laying on the ground, final inspection requested. | 3 | Conductors Equipment is not approved for the specific use. | Teck_laying_on_ground.png | file://x:/photopub/docs/0000000595/7d208916-75e1-466d-9273-27c3b42d3df1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0bb9ff01_7a2d_4f79_901e_48ea36806218
ELIN-786491-2017 | EL-451097-2016 | 4/6/2017 12:10:49 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Unbonded_fixtures_-_factory_installed_bond_conductor_removed1.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed2.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed3.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed4.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed5.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed6.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed7.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed8.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed9.png Electrical equipment including light fixtures are required to be bonded to the grounded system conductor. This is required to provide a low impedance path for fault current back to the source and to provide an equipotential plane to minimize the possibility of a potential difference between metal parts. This installation at a newly constructed house had light fixtures that were not bonded. The bonding conductor that was supp | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Unbonded_fixtures_-_factory_installed_bond_conductor_removed3.png | file://x:/photopub/docs/0000000583/7021179e-4829-4d6f-9742-f4f81d2c74ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07da0b50_4c9e_43b0_947a_c38d747812ae
ELIN-786491-2017 | EL-451097-2016 | 4/6/2017 12:10:49 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Unbonded_fixtures_-_factory_installed_bond_conductor_removed1.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed2.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed3.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed4.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed5.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed6.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed7.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed8.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed9.png Electrical equipment including light fixtures are required to be bonded to the grounded system conductor. This is required to provide a low impedance path for fault current back to the source and to provide an equipotential plane to minimize the possibility of a potential difference between metal parts. This installation at a newly constructed house had light fixtures that were not bonded. The bonding conductor that was supp | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Unbonded_fixtures_-_factory_installed_bond_conductor_removed8.png | file://x:/photopub/docs/0000000583/d52b4938-cf44-42e6-b2d5-33fc41cc4ed8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07da0b50_4c9e_43b0_947a_c38d747812ae
ELIN-776106-2017 | EL-353347-2016 | 4/6/2017 10:05:48 AM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Unsupported_nmd90_cable_on_a_construction_site_.png Cables are required to be properly supported where they run from, to, and between electrical equipment. This is required to prevent the cables and cable terminations from getting damaged if they are accidentally snagged and pulled on or left in locations where they are susceptible to mechanical damage. This installation has a non-metallic sheathed cable that is not properly supported. Left uncorrected this is a potential shock and fire hazard if the energized cable and the internal conductor insulation is damaged and persons or objects contact them. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Unsupported_nmd90_cable_on_a_construction_site_.png | file://x:/photopub/docs/0000000583/262193e9-78c7-4907-9b4b-8608cdc71ccf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7b7cf35_15e5_45c5_a48d_15724fdfeb78
ELIN-786491-2017 | EL-451097-2016 | 4/6/2017 12:10:49 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Unbonded_fixtures_-_factory_installed_bond_conductor_removed1.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed2.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed3.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed4.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed5.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed6.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed7.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed8.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed9.png Electrical equipment including light fixtures are required to be bonded to the grounded system conductor. This is required to provide a low impedance path for fault current back to the source and to provide an equipotential plane to minimize the possibility of a potential difference between metal parts. This installation at a newly constructed house had light fixtures that were not bonded. The bonding conductor that was supp | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Unbonded_fixtures_-_factory_installed_bond_conductor_removed4.png | file://x:/photopub/docs/0000000583/4e390a7b-b2a9-4c69-9acc-77eb5f0b8fdc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07da0b50_4c9e_43b0_947a_c38d747812ae
ELIN-808599-2017 | EL-494741-2017 | 5/4/2017 | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Exposed_to_weather_1.png,Exposed_to_weather_2.png Main electrical panel is exposed to the weather and mechanical damage during the construction phase. This could be a hazard to person(s) or property if the panel was to be damaged by water/mechanically because it could shock or fire to person(s) or property. This could be done from a short from the metal cover on the panel touching the electrical bus bar if it was mechanically damaged or from excessive water from the weather pouring into the non weather proof panel and causing electrical shock. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Exposed_to_weather_2.png | file://x:/photopub/docs/0000000597/51f229cb-84cd-4891-87bb-5fe3339552e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dbb99c00_17a0_483e_9763_0a143e873470
ELIN-808599-2017 | EL-494741-2017 | 5/4/2017 | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Exposed_to_weather_1.png,Exposed_to_weather_2.png Main electrical panel is exposed to the weather and mechanical damage during the construction phase. This could be a hazard to person(s) or property if the panel was to be damaged by water/mechanically because it could shock or fire to person(s) or property. This could be done from a short from the metal cover on the panel touching the electrical bus bar if it was mechanically damaged or from excessive water from the weather pouring into the non weather proof panel and causing electrical shock. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Exposed_to_weather_1.png | file://x:/photopub/docs/0000000597/5078b7be-eb28-4712-b258-69ca4757b8e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dbb99c00_17a0_483e_9763_0a143e873470
ELIN-804032-2017 | EL-439903-2016 | 5/8/2017 8:14:01 AM | ASSESS: EL: Final | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 4 | #6mm.png Outlet box installed in kitchen area counters exceed the minimum depths of 6mm. The reason the outlet boxes should be flush mounted is to decrease the risk of fire from damaged conductors due to rodents being able to get into the gape that exceeds 6mm. If rodents are able to get into the gap then they will damage the conductors. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 6mm.png | file://x:/photopub/docs/0000000597/8b1fa806-eead-47b0-b58e-cf51da10a28b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf2db887_9431_4cb6_a33c_d0556390f737
ELIN-772006-2017 | EL-414675-2016 | 3/9/2017 2:22:48 PM | ASSESS: EL: Service Connection | png | #asFound Service box in combination panel board after contractor corrected wrong terminations, cross connected parallel runs L1 and L2 | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Consumer_service_connections2.png The apprentice working at the site, terminated the consumer service conductors in the panel board service box incorrectly, L1 and L2 parallel runs had not been matched up. The qualified electrician onsite was not providing the apprentice with direct supervision. The qualified person did not verify the installation was correct. The FSR listed on the permit and service connection declaration did not physically inspect the work. The utility did not follow procedures and test the connection before energizing. A resulting short circuit occurred. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Consumer_service_connections2.png | file://x:/photopub/docs/0000000569/00b75fbe-3417-453b-a4e5-b01c2fdc3281.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c951ce65_8a92_44df_9c71_a5614a1e2ac5
ELIN-772006-2017 | EL-414675-2016 | 3/9/2017 2:22:48 PM | ASSESS: EL: Service Connection | png | #asFound Terminations that had been done incorrectly, since corrected | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Consumer_service_connections2.png The apprentice working at the site, terminated the consumer service conductors in the panel board service box incorrectly, L1 and L2 parallel runs had not been matched up. The qualified electrician onsite was not providing the apprentice with direct supervision. The qualified person did not verify the installation was correct. The FSR listed on the permit and service connection declaration did not physically inspect the work. The utility did not follow procedures and test the connection before energizing. A resulting short circuit occurred. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Consumer_service_connections2.png | file://x:/photopub/docs/0000000569/d68bfa56-997c-4780-9b5f-65f9b47fe885.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c951ce65_8a92_44df_9c71_a5614a1e2ac5
ELIN-772006-2017 | EL-414675-2016 | 3/9/2017 2:22:48 PM | ASSESS: EL: Service Connection | png | #asFound Corrected connection at the service box | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Consumer_service_connections2.png The apprentice working at the site, terminated the consumer service conductors in the panel board service box incorrectly, L1 and L2 parallel runs had not been matched up. The qualified electrician onsite was not providing the apprentice with direct supervision. The qualified person did not verify the installation was correct. The FSR listed on the permit and service connection declaration did not physically inspect the work. The utility did not follow procedures and test the connection before energizing. A resulting short circuit occurred. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Consumer_service_connections2.png | file://x:/photopub/docs/0000000569/75beaffe-f7ba-42f3-a33e-6ca97f0d49e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c951ce65_8a92_44df_9c71_a5614a1e2ac5
ELIN-769842-2017 | EL-506744-2017 | 3/9/2017 2:55:58 PM | ASSESS: EL: Service Connection | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Exposed_and_energized_.png Energized receptacles did not have cover plates on them. This condition could lead to accidental contact resulting in an electrical shock. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Exposed_and_energized_.png | file://x:/photopub/docs/0000000569/b61349ce-858d-4032-93a1-1d477abf6f66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b3cc3d3_0c34_4bfb_bf03_318f2263e7d4
GAIN-812318-2017 | GA-530314-2017 | 5/12/2017 11:02:03 AM | ASSESS: GA: Rough-In | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Pinched_electrical_supply.png Electrical supply conductors pinched between fireplace case and wood framing. This could lead to an electrical short and possible fire. | 3 | Appliance not installed according to installation instructions | Pinched_electrical_supply.png | file://x:/photopub/docs/0000000600/41154425-db6a-433e-a60f-eb08a14bb1c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00e9f148_07de_4905_8a95_ec57a7b7b4ab
ELIN-780744-2017 | EL-508400-2017 | 3/23/2017 10:54:34 AM | ASSESS: EL: Service Connection | png | #asFound Plate electrode has not been buried. | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | #Plate_not_buried.png Service connection for new single family dwelling. Grounding electrode has not been properly installed and is laying on the earth instead of being buried. Shock hazard when connected if a fault occurs. Also overcurrent devices may not be able to trip in a fault. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Plate_not_buried.png | file://x:/photopub/docs/0000000575/4885f75d-1dc0-472d-9e20-95bec195705b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b67d32ca_03f2_42bb_a058_f7da97277880
BPVOP-771295-2017 | 2263442 | 3/2/2017 4:32:31 PM | ASSESS: BPV OP: Re-Certification Boiler | pdf | #asFound See photo of boiler nameplate and SRV nameplate. | BP121 | 3.0.1 Safeties will not function - Pressure Relief Device Set Pressure over required minimum to provide over pressure protection and would lead to over pressure occurrence | 5 | 5 | #HW62472_Pictures.pdf This assessed 1969 boiler MAWP (maximum allowable working pressure) is 30 psig as per the nameplate. The Safety Relief Valve found installed is set at 45 psig which exceeds the MAWP. In case of an upset condition this pressure relief would not protect the pressure components of this boiler and a rupture could result. | 5 | 3.0.1 Safeties will not function - Pressure Relief Device Set Pressure over required minimum to provide over pressure protection and would lead to over pressure occurrence | HW62472_Pictures.pdf | file://x:/photopub/docs/0000000568/cc147a60-b92c-4882-aa3f-7b0fa2a15aaf.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ded3879d_8f2d_4498_af5f_05acc4c9142d
EDMA-813480-2017 | ED-506422-2017 | 5/10/2017 12:54:42 PM | ASSESS: ED MA: Partial Acceptance | png | #asFound | ED052 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 2 | 2 | #Pit.png Pit ladder was not installed | 2 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | Pit.png | file://x:/photopub/docs/0000000599/1935b598-4fe9-42df-adc7-991e1e9e2d72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__231d50a2_9ba0_4c41_888c_9ecfed98a4d5
ELIN-786491-2017 | EL-451097-2016 | 4/6/2017 12:10:49 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Unbonded_fixtures_-_factory_installed_bond_conductor_removed1.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed2.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed3.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed4.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed5.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed6.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed7.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed8.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed9.png Electrical equipment including light fixtures are required to be bonded to the grounded system conductor. This is required to provide a low impedance path for fault current back to the source and to provide an equipotential plane to minimize the possibility of a potential difference between metal parts. This installation at a newly constructed house had light fixtures that were not bonded. The bonding conductor that was supp | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Unbonded_fixtures_-_factory_installed_bond_conductor_removed6.png | file://x:/photopub/docs/0000000583/4e5f7a33-a3d2-4a1e-8a1a-1c62ef373de6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07da0b50_4c9e_43b0_947a_c38d747812ae
ELIN-802651-2017 | EL-518546-2017 | 5/2/2017 8:15:44 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Raceway_is_needed.png This assessment found a raceway not installed for the non-heating Leeds of in-floor heat, which has a potential for fire or shock if cable is damaged. | 3 | Conductors Equipment is not approved for the specific use. | Raceway_is_needed.png | file://x:/photopub/docs/0000000594/d860ecf5-5550-4743-a706-83b97328e957.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5f48b05_b41e_4323_859e_2dfb2df41686
GAIN-791518-2017 | GA-520535-2017 | 4/12/2017 2:26:00 PM | ASSESS: GA: Final | png | #asFound Venting | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Venting.png As per directive D-G5 071030 states that when venting category 1 appliances to use the smallest practical size vent, the common vent used is not the smallest size for the combined load of the hot water tanks. This could cause a spillage situation or unnecessary condensation of the venting system. | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Venting.png | file://x:/photopub/docs/0000000586/883b75ab-fd69-4b54-b7b5-c607253658b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27cbc080_d115_46ec_9c39_af67578c1c7b
GAHE-771411-2017 | HE-509420-2017 | 3/9/2017 7:43:59 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound Salmon arm 1 st street | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Vent_connector.png,261_.png At time of inspection venting of water heater was oversized, this inadequate venting of flue gases could causing carbon monoxide poisoning | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Vent_connector.png | file://x:/photopub/docs/0000000568/d7f6b6df-013a-462a-b436-ba5987c310d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__694e1c44_4948_4577_926f_fe2092ed1041
ELIN-800261-2017 | EL-524698-2017 | 5/2/2017 3:25:25 PM | ASSESS: EL: Final | png | #asFound | EL151 | Installation of electrical equipment Entrance to dwelling does not have light. | 3 | 3 | #No_Exterior_fixtures.png Each entrance to a residential occupancy requires illumination that is controlled by a switch near the door inside the building. This is required to prevent trips and falls from inadequate illumination and to provide illumination for security. During an assessment for a silver label inspection of a modular home, the safety officer found that two of the entrances into the home did not have exterior light fixtures. The lack of illumination at these entrances could create a potential physical hazard to persons from trips or fall and reduces security at this dwelling. | 1 | Installation of electrical equipment Entrance to dwelling does not have light. | No_Exterior_fixtures.png | file://x:/photopub/docs/0000000594/743fa5d9-7b71-4bc9-bed7-1bb12e49778d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__258904cb_9624_4670_995f_a464d60b9c6a
ELOP-653569-2016 | EL-118469-2014 | 3/29/2017 12:33:52 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | #Primary_lines_over_mobile_home.png Various locations where mobile homes are below overhead primary conductors. Exterior sheathing of mobile homes is metal. Primary lines create induced voltages over space, acceptable clearances have to be maintained to avoid a potential for shock and arc flash to persons and property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Primary_lines_over_mobile_home.png | file://x:/photopub/docs/0000000578/b3b60e00-546d-4aaa-9d9e-aab42360edac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42364CAF_DA91_41BC_A113_72BD556D3541
GAIN-811720-2017 | GA-531372-2017 | 5/10/2017 2:32:40 PM | ASSESS: GA: Final | png | #asFound Existing combustion air removed due to new boilers being direct vented. However no ventilation air inside mechanical room | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Air_requirements1.png,Air_requirements2.png Combustion Air and Ventilation air installed in boiler has been blocked due to new boiler install being direct vented. (Separate combustion air and flue per boiler). Ventilation air is still required in boiler room because of the amount of heat produced from combustion. Boiler room is above a workable temperature, possibly causing fatigue for technicians working in boiler room, also the electrical components could start malfunctioning causing control issues to heating system and safeties of equipment | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Air_requirements2.png | file://x:/photopub/docs/0000000599/f9d3ce78-a22f-4216-8aa5-574712fabbfe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c05f9ab_5292_4479_b46e_a354226ab6a7
GAIN-811720-2017 | GA-531372-2017 | 5/10/2017 2:32:40 PM | ASSESS: GA: Final | png | #asFound No comb Air for HWT | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Air_requirements1.png,Air_requirements2.png Combustion Air and Ventilation air installed in boiler has been blocked due to new boiler install being direct vented. (Separate combustion air and flue per boiler). Ventilation air is still required in boiler room because of the amount of heat produced from combustion. Boiler room is above a workable temperature, possibly causing fatigue for technicians working in boiler room, also the electrical components could start malfunctioning causing control issues to heating system and safeties of equipment | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Air_requirements1.png | file://x:/photopub/docs/0000000599/334b69c3-4fe1-470a-be8f-ad66e5d2c2c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c05f9ab_5292_4479_b46e_a354226ab6a7
ELIN-786491-2017 | EL-451097-2016 | 4/6/2017 12:10:49 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Unbonded_fixtures_-_factory_installed_bond_conductor_removed1.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed2.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed3.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed4.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed5.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed6.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed7.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed8.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed9.png Electrical equipment including light fixtures are required to be bonded to the grounded system conductor. This is required to provide a low impedance path for fault current back to the source and to provide an equipotential plane to minimize the possibility of a potential difference between metal parts. This installation at a newly constructed house had light fixtures that were not bonded. The bonding conductor that was supp | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Unbonded_fixtures_-_factory_installed_bond_conductor_removed9.png | file://x:/photopub/docs/0000000583/c2d04ac3-311c-4435-bd46-e86efc078582.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07da0b50_4c9e_43b0_947a_c38d747812ae
ELIN-786491-2017 | EL-451097-2016 | 4/6/2017 12:10:49 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Unbonded_fixtures_-_factory_installed_bond_conductor_removed1.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed2.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed3.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed4.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed5.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed6.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed7.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed8.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed9.png Electrical equipment including light fixtures are required to be bonded to the grounded system conductor. This is required to provide a low impedance path for fault current back to the source and to provide an equipotential plane to minimize the possibility of a potential difference between metal parts. This installation at a newly constructed house had light fixtures that were not bonded. The bonding conductor that was supp | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Unbonded_fixtures_-_factory_installed_bond_conductor_removed2.png | file://x:/photopub/docs/0000000583/91705f49-b3f7-4e35-b0d5-f9093faed8b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07da0b50_4c9e_43b0_947a_c38d747812ae
ELIN-786491-2017 | EL-451097-2016 | 4/6/2017 12:10:49 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Unbonded_fixtures_-_factory_installed_bond_conductor_removed1.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed2.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed3.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed4.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed5.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed6.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed7.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed8.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed9.png Electrical equipment including light fixtures are required to be bonded to the grounded system conductor. This is required to provide a low impedance path for fault current back to the source and to provide an equipotential plane to minimize the possibility of a potential difference between metal parts. This installation at a newly constructed house had light fixtures that were not bonded. The bonding conductor that was supp | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Unbonded_fixtures_-_factory_installed_bond_conductor_removed5.png | file://x:/photopub/docs/0000000583/55febe1a-8934-4fe2-9bf7-40f86ef257ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07da0b50_4c9e_43b0_947a_c38d747812ae